## Sheet1
DATA DATE/TIME | 2019-10-07 | 36494.5869
WORK ORDERS WHERE LEAD WAS IDENTIFIED 8/28/2017 - 8/28/2019
W/O_NO | WO_DATE | MATERIAL | ADD | STREET | CROSS STREET | PROBLEM_ | PROBLEM_DETAILS | COMP_DATE | ACTION_TAKEN
201605185201 | 2016-08-17 | LEAD | 2285 | SERE | MANDEVILLE | WILK | WM - LEAK IN THE STREET (DIRECTLY UNDER STREET LIGHT) CHANGED FROM 2200BLK SERE WATER VALVE LEAKNG IN STREET BY POLE ***VALVE#350-V009 8/18/17 LEAK GETTING WORSE NOW CAUSING A HOLE NEXT TO VALVE, NEED 1 BARREL ON SITE (AJR) /** 1) MN: A302407 SN: 0100526, *TAP: SIZE: A LOC: 314 FEET FROM P LINE AT MARIGNY, *MB: CODE: ADKO LOC: ON SERE, 314' FROM P.L. MARIGNY, 6' OUTSIDE P.L. ****/ | 2017-09-03 | EXCAVATED IN ASPHALT STREET. EXAMINED FOUND LEAK ON 3/4 TAIL PIECE. MADE REPAIRS BACKFILLED WITH RIVER SAND AND COLD MILL. CLEANED UP JOB AREA. JOB COMPLETE. --------------------------8X8 APHLAT STREET----------------------
201605398802 | 2017-08-17 | LEAD | 4612 | ORLEANS AV | S OLYMPIA | WILK | EXAMINE THE JOB AND FOUND THAT THE COCK IS DAMEGED BUT I NEED BREAKER TO CUT CONCRETE DRIVEWAY TO DRIVEWAY TO REPAIR IT /** 1) MN: A328674 SN: 0079705, *TAP: SIZE: A LOC: 93 FEET FROM P LINE AT OLYMPIA S, *MB: CODE: CDI2 LOC: 93FT FROM PL OLYMPIA REAR ST METER ON ST PETER ****/ | 2017-09-24 | EXCAVATED IN DRIVEWAY ON INLET LEAK MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVER SAND AND COLD MILL 4 X 4 ST LJF
201605441102 | 2017-05-11 | LEAD | 2101 | SONIAT | S LIBERTY | WILK | ML (RESIDENTIAL) METER LEAK METER # B-040367 ACCT # 041422,04,9 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: B032053 SN: 0041846, *TAP: SIZE: B LOC: 43 FEET FROM P LINE AT SONIAT, *MB: CODE: BDH LOC: SIDE ST ON S LIBERTY 43' P.L. SONIAT ****/ (TRUCK 250)EXAMINED FOR LEAK FOUND LEAK ON CURB COCK BUT WAS UNABLE TO EXCAVATE DUE TO IRON FLOWER HOLDERS /** 1) MN: B032053 SN: 0041846, *TAP: SIZE: B LOC: 43 FEET FROM P LINE AT SONIAT, *MB: CODE: BDH LOC: SIDE ST ON S LIBERTY 43' P.L. SONIAT ****/ DOTTIE READY 10-26-17 EXP 11-15-17 | 2017-11-11 | REPLACED 3/4 INCH WASHERS TO STOP LEAK
201605561504 | 2017-08-25 | LEAD | 3734 | TULANE AV | S CORTEZ | WMTLK | ACCT#096608026 METER#E004509 BAD METER LEAK EXCAVATING IN SW OVER 2" SERVICE TO MAKE REPAIRS IN SAME ( JOB CONTINUED) /** 1) MN: E004509 SN: 0083529, *TAP: SIZE: E LOC: 70 FEET FROM P LINE AT GRAVIER, *MB: CODE: BEHP LOC: ON S CORTEZ 105' FRM PL GRAVIER IN MH 7FT OUTSIDE ** 2) MN: G001331 SN: 0083529, *TAP: SIZE: G LOC: 85 FEET FROM P LINE AT CORTEZ SO, *MB: CODE: __ LOC: ON TULANE 82FT FROM S CORTEZ THERE IS 1 MORE NOT LISTED. ****/ DOTTIE READY 9-8-17 EXP 9-28-17 | 2017-09-22 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 2" METER COCK LEAKING. REPLACED COCK AND 6FT OF 2" TUBING TIED INTO LEAD. ( JOB CONTINUED NEED TO BACKFILL)
201605573101 | 2016-10-19 | LEAD | 4633 | DART | VENDOME PL | WMEX | UNABLE TO REMOVE. CONCRETE IN BOX. PLEASE REPAIR AND REMOVE METER B035507 ACCT 099176053 /** 1) MN: B024004 SN: 0095318, *TAP: SIZE: B LOC: 216 FEET FROM P LINE AT VENDOME PL, *MB: CODE: BD25 LOC: ON DART, 217' FROM P.L. VENDOME PL.,9' OUTSIDE ****/ DOTTIE READY 8-29-17 EXP 9-18-17 | 2017-09-02 | EXPOSED AND RAISED METER BOX TO GRADE AND MARKED LEFT METER ON BY REQUEST FROM MRS. PAULINE. CREW FOUND B041911 AT ABOVE LOCATION
201605573901 | 2016-10-19 | LEAD/PLASTIC | 3517 | LIVE OAK | EDINBURGH | WILK | MI- SIDEWALK LEAK CHANGED FROM 3500 LIVE OAK INLET SERVICE LEAK @ CURB /** 1) MN: B027825 SN: 0114495, *TAP: SIZE: C LOC: 37 FEET FROM P LINE AT EDINBURGH, *MB: CODE: BDK LOC: ON LIVE OAK 37FT FROM PL OF EDINBURGH 7FT OUTSIDE ** 2) MN: SN: 0000000, *TAP: SIZE: __ LOC: 0 FEET FROM LINE AT , *MB: CODE: __ LOC: HYDRANT IS LOCATED ON THE CORNER OF EDINBURGH AND ****/ | 2017-12-11 | EXCAVATED A 5 X 10 CUT IN CONCRETE SIDEWALK OVER A 1" INLET SERVICE LEAK LEAD ON INLET & OUTLET CHANGED THE COCK RAISED METER BOX UP TO GRADE & REPLACED 1" OUTLET WITH 12 OF 1" PVC FROM METER BOX TO PROPERTY BACKFILLED WITH RIVER SAND & COLD MILL 5' X10' CUT C/SW JOB COMPLETE
201605724001 | 2016-11-16 | LEAD | 1126 | WASHINGTON AV | CAMP | WMTLK | ML- METER LEAK ACCT# 102955-539885 METER# B037629 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER BOX UNDER WATER IN TREE ROOTS /** 1) MN: B027743 SN: 0005549, *TAP: SIZE: B LOC: 86 FEET FROM P LINE AT CAMP URPL, *MB: CODE: DL1 LOC: 86' FROM URPL CAMP ****/ DOTTIE READY9-22-17 EXP 10-12-17 | 2017-10-12 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 3/4 CURB COCK LEAKING IN TREE ROOTS UNABLE TO REMOVE LEAD DUE TO CAR PARKED ON JOB. REPLACED CURB COCK TO STOP LEAK. LEAD NEED TO REMOVED.
201605730501 | 2016-11-17 | LEAD | 3208 | DRYADES | HARMONY | WILK | 0 ML- METER LEAK MTR.# A-414735 INLET SERVICE LEAK BAD BLEEDER VALVE /** 1) MN: SN: 0062105, *TAP: SIZE: A LOC: 78 FEET FROM P LINE AT HARMONY, *MB: CODE: BD LOC: AT 3210 80' P.L. HARMONY ****/ DOTTIE READY9-12-17 EXP10-2-17 | 2017-09-18 | ARRIVED ON SITE EXAMINED METER BOX FOUND BAD BLEEDER VALVE ON 5/8 CURB COCK EXCAVATED IN MUDPLOT ,REPLACED WITH NEW COCK BACKFILLED AND DRESSED 4 FT. X 4 FT. MUDCUT.
201605745304 | 2017-11-15 | LEAD/PLASTIC | 4908 | MAGAZINE | UPPERLINE | WILK | REPAIR INLET SERVICE CAUSING CAVE IN STREET /** 1) MN: A275930 SN: 0025820, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT UPPERLINE, *MB: CODE: CDLM LOC: ON MAGAZINE 73.5FT FROM UPPERLINE ****/ | 2017-12-27 | REPLACED 15FT. OF 3/4 TUBING FROM STREET TO PROPERTY LINE.
201605770604 | 2018-12-03 | LEAD | 5516 | URQUHART | CAFFIN AV | WMTLK | WATER LEAK CONTINUES AROUND METER AFTER PREVIOUS REPAIR. CONTRACTOR NEEDS THIS REPAIRED BEFORE THEY CAN COMPLETE RESTORATION. ***DO NOT CREATE RESTORATION WORK ORDER AFTER REPAIR.RESTORATION IS ALREADY ASSIGNED TO THE CONTRACTOR.**** /** 1) MN: A323370 SN: 0041219, *TAP: SIZE: B LOC: 112 FEET FROM P LINE AT FLOOD, *MB: CODE: BDK LOC: ON URQUHART 112'FRM PL FLOOD ****/ | 2018-12-09 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201605811401 | 2016-12-05 | LEAD | 1927 | ST ROCH AV | N PRIEUR | WMRE | UNABLE TO LOCATE METER BOX BY ADDRESS POSSIBLE EMPTY LOT WAS UNABLE TO LOCATE BOX THERE AS WELL PLEASE LOCATOE AND SET A 5/8 METER LOCATION #300505 /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-10-10 | FOUND METER IN MANHOLE SUPPLYING WATER TO BUILDING
201605862001 | 2016-12-16 | LEAD | 5007 | COLISEUM | ARABELLA | WILK | WM - LEAK ON THE SIDEWALK JOB TAKEN 12/13/16 BY BAL @ 3:04 PM (KLL) SYSTEM DOWN INLET SERVICE LEAK ON SIDEWALK /** 1) MN: A250914 SN: 0036582, *TAP: SIZE: A LOC: 59 FEET FROM P LINE AT ROBERT, *MB: CODE: AF6 LOC: 60' P.L. ROBERT ****/ DOTTIE READY 8-29-17 EXP 9-18-17 | 2017-09-02 | REPLACED 5/8 CURB COCK.CREW FOUND METER A399742 AT ABOVE LOCATION
201605862701 | 2016-12-13 | LEAD | 2123-25 | GEN PERSHING | LASALLE | WMTLK | ML - METER LEAK JOB TAKEN 12/13/16 BY T.JOHN @ 1:02 PM (KLL) SYSTEM DOWN EXAMINE INLET & OUTLET SERVICE FOR A LEAK MUD PLOT & SIDEWALK FLOODED 3/16/17 LEAK GETTING MUCH WORSE PER SR#12798468 (AJR) 7/21/17 ALSO LOCATE AND SET 5/8 METER PER SR#12809861 07/26/17 LEAK HAS GOTTEN WORSE CAUSING AREA TO FLOOD PER S/R# 12810440 /** AT 2123: 1) MN: A218698 SN: 0022096, *TAP: SIZE: A LOC: 93 FEET FROM P LINE AT LA SALLE, *MB: CODE: CFM LOC: ON GEN PERSHING 123.5FT FROM LA SALLE ** AT 2125: 2) MN: A279083 SN: 0022096, *TAP: SIZE: A LOC: 93 FEET FROM P LINE AT LA SALLE, *MB: CODE: CFM LOC: ON GEN PERSHING 123FT FROM LA SALLE ****/ DOTTIE READ 9-6-17 EXP 9-26-17 | 2017-09-06 | ARRIVED AT THE ABOVE LOCATION MADE 3 X3 SIDEWALK CUT OVER THE METER BOX MADE REPAIR ON 3/4 LEAD LINE AND ALSO SET ANOTHER METER,THEN BACKFILLED AND CLEANED THE AREA. NEED PAVING. (SOC 3FT. X 3 FT. S/W) ***********OLD METER INFO*************8 MTR:A218698 FAC:29317272 MAKE:ROCKWELL READ:5320
201605903101 | 2016-12-23 | LEAD | 5305 | ANNUNCIATION | VALMONT | WILK | ML-- METER LEAK METER # A224055 ACCT # 126605566572 INLET SERVICE LEAK BEHIND CURB COCK 5/26/17 LEAK GETTING WORSE AND FLOODING AREA PER SR#12805381 (AJR) /** 1) MN: A224055 SN: 0049892, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT VALMONT, *MB: CODE: CDLM LOC: ON ANNUNCIATION,46' FROM U.S.P.L. VALMONT ****/ DOTTIE READY 8-15-17 EXP 9-4-17 | 2017-08-31 | REPLACED 5/8 CURB COCK TIED INTO LEAD
201605905101 | 2016-12-24 | LEAD | 3316 | PRYTANIA | LOUISIANA AV | WILK | MI METER BOX LEAK METER REMOVED 5/27/14 EXAMINE INLET SERVICE AT SIDEWALK FOR LEAK /** 1) MN: A212108 SN: 0052984, *TAP: SIZE: A LOC: 161 FEET FROM P LINE AT LOUISIANA AVE, *MB: CODE: BDK LOC: 161' P.L. LOUISIANA AV ** 2) MN: A215081 SN: 0052984, *TAP: SIZE: B LOC: 161 FEET FROM P LINE AT TOLEDANO, *MB: CODE: OOO LOC: ON PRYTANIA ST 162' FROM URPL TOLEDANO ****/ DOTTIE READY 10-25-17 EXP11-14-17 | 2017-11-11 | EXCAVATED 3 X 3 MUD PLOT REPLACED 5/8 INCH COCK AND WASHERS BACKFILLED AND CLEANED THE AREA
201605938701 | 2016-12-31 | LEAD | 604 | SONIAT | LAUREL | WILK | MI: LEAK ON THE SIDEWALK EXAMINE INLET SERVICE AT SIDEWALK FOR LEAK /** 1) MN: A276844 SN: 0018670, *TAP: SIZE: B LOC: 190 FEET FROM P LINE AT LAUREL, *MB: CODE: CE LOC: ON SONIAT 189' FROM URPL LAUREL ****/ DOTTIE READY 8-29-17 EXP 9-18-17 | 2017-09-02 | REPLACED 5/8 CURB COCK,,,CREW FOUND METER A276844 AT ABOVE LOCATION
201700000601 | 2017-01-03 | LEAD | 5314 | ANNUNCIATION | VALMONT | WILK | ML-METER LEAK ACCT#165065566723 METER#A146681 BAD BLEEDER VALVE /** 1) MN: A146681 SN: 0104621, *TAP: SIZE: A LOC: 108 FEET FROM P LINE AT VALMONT, *MB: CODE: BDLM LOC: 107FT FROM PL VALMONT 7' OUTSIDE PL 3' INSIDE CURB ****/ DOTTIE READY 11-7-17 EXP 11-27-17 | 2017-11-11 | EXCAVATED 3 X 3 MUD PLOT REPLACED 5/8 INCH COCK AND WASHERS TO STOP LEAK BACKFILL AND CLEANED THE AREA
201700014601 | 2017-01-05 | LEAD | 4311 | S ROMAN | GEN PERSHING | WILK | ML- METER LEAK ACCT 133144-544609 MTR# A224382 BAD BLEEDER VALVE 3/16/17 LEAK GETTING WORSE PER SR#12798469 /** 1) MN: A224382 SN: 0064014, *TAP: SIZE: A LOC: 88 FEET FROM P LINE AT GEN PERSHING, *MB: CODE: BDK2 LOC: ON SO. ROMAN,86.5' FROM U.S.P.L. GEN. PERSHING ****/ DOTTIE READY 11-7-17 EXP 11-27-17 | 2017-11-11 | REPLACED 5/8 INCH WASHERS CUSTOMER HAS CUSTOMED MADE DRIVEWAY
201700014701 | 2017-01-05 | LEAD | 1310 | MARENGO | PERRIER | WILK | ML METER LEAK METER # A308534 ACCOUNT # 153807-555989 INLET SERVICE LEAK BEHIND CURB COCK 1ST METER NEAR PERRIER 03/06/17 LEAK HAS GOTTEN WORSE (KSW) 4/10/17 LEAK GETTING WORSE PER SR#12800989 (AJR) /** 1) MN: A325872 SN: 0003536, *TAP: SIZE: B LOC: 70 FEET FROM P LINE AT PERRIER, *MB: CODE: ADM5 LOC: SECOND METER ON MARENGO 68FT FROM PL OF PERRIER ** 2) MN: A308534 SN: 0003536, *TAP: SIZE: B LOC: 66 FEET FROM P LINE AT PERRIER, *MB: CODE: ADM5 LOC: ON MARENGO 67' FROM PL PERRIER 11' OUTSIDE PL 6' I ****/ DOTTIE READY 11-7-17 EXP 11-27-17 | 2017-11-11 | EXAM FOUND NO LEAK
201700081501 | 2017-01-16 | LEAD/PLASTIC | 316 | AUDUBON BL | FONTAINEBLEAU DR | WILK | ML METER LEAK ACCT# 164724-575529 METER# C023029 INLET SERVICE LEAK AT CURB 03/24/17 LEAK HAS GOTTEN WORSE NOW FLOODING AREA (KSW) /** 1) MN: C023029 SN: 0069614, *TAP: SIZE: C LOC: 334 FEET FROM P LINE AT FONTAINBLEAU DR, *MB: CODE: ADMP LOC: ON AUDUBON BLVD., 334' FROM P.L. FONTAINBLEAU DR., ****/ DOTTIE READY 9-28-17 EXP 10-18-17 | 2017-10-21 | ARRIVED ON JOB EXCABVATED IN STREET AND MUD PLOT FOUND TWO 1"WATER SERVICE LEAKING MADE REPAIRS AND BACKFILLED JOB COMPLETE. (SOC 5 FT. X 6 FT. STREET F/D ASPHALT) CREW FOUND METER C023029 AT ABOVE LOCATION
201700086101 | 2017-01-17 | LEAD | 3111 | CONSTANCE | 8TH | WILK | ML METER LEAK METER# A337093 ACCT# 199345-538963 INLET SERVICE LEAK BEHIND CUBR COCK FLOODING GUTTER BOTTOM /** 1) MN: A323418 SN: 0032154, *TAP: SIZE: A LOC: 74 FEET FROM P LINE AT EIGHTH, *MB: CODE: BEK1 LOC: ON CONSTANCE 73FT FROM PL OF EIGHTH ****/ DOTTIE READY 8-17-17 EXP 9-6-17 | 2017-08-31 | REPLACED 5/8 CURB COCK TIED INTO LEAD...OLD METER A337093 FACTORY 57288947 MAKE SENSUS READ 5173
201700132603 | 2018-07-03 | LEAD | 5201 | FRANCE RD |  | WILK | 2 INCH COCK LEAKING FROM BLEEDER /** 1) MN: E006894 SN: 0115615, *TAP: SIZE: E LOC: 76 FEET FROM P LINE AT HYDT #8, *MB: CODE: BFK2 LOC: ON FRANCE RD., 76' FROM HYDT. #8, 5' OUTSIDE P.L. ****/ | 2018-07-09 | BROKEN UP MANHOLE AND REPAIRED LEAK ON 2INCH LED INLET SERVICE. REPAIRED MANHOLE BACKFILL CLEANED UP JOB AREA.
201700159002 | 2017-02-03 | LEAD/PLASTIC | 4194 | ORLEANS AV | N SOLOMON | WILK | EXCAVATED JOB UNABLE TO COMPLETE BY METER IN DRIVEWAY NEED A MACHINE 08/04/17 CUST STATES METER IS STILL LEAKING CAUSING AREA TO FLOOD & CREATING ALGAE (KSW) /** 1) MN: A242208 SN: 0067490, *TAP: SIZE: A LOC: 15 FEET FROM P LINE AT SOLOMON N, *MB: CODE: CDN2 LOC: ON ST. PETER, 14' FROM P.L. NO. SOLOMON ****/ | 2017-12-04 | MADE A 4 X 10 SIDEWALK CUT EXCAVATED AND MADE REPAIRS ON A 3/4 INLET LEAK FROM THE CURB TO THE METER LEAD IS ON THE INLET IN THE STREET RAISED THE GRADE AND RENEWED THE OUTLET REFER THAT CUT TO PAVING. JOB COMPLETE
201700165102 | 2017-02-07 | LEAD/PLASTIC | 1316 | LOWERLINE | PLUM | WOLK | EXCAVATED IN MUDPLOT OVER A 5/8 INLET SERVICE LEAK BUT LARGE TREE ROOTS IS SURROUNDING THE METERBOX NEED MACHINE /** 1) MN: A340023 SN: 0064236, *TAP: SIZE: A LOC: 80 FEET FROM P LINE AT PLUM, *MB: CODE: AFM LOC: ON LOWERLINE,80' FROM U.S.P.L. PLUM ****/ | 2018-06-04 | EXCAVATED IN TREE ROOTS AND MADEREPAIS BY REROTING A5/8 METER FROM OUT THE TREE. OUTLRT HAS PLASTIC ON IT. INLET LEAD ITS ACANAL RIGHT BY THE WATER MAIN. [JOB COMPLETE ]
201700185701 | 2017-02-03 | LEAD/PLASTIC | 2320 | JOSEPH |  | WILK | ML-METER LEAK ACCT#136078-568111 METER #A322327 INLET SERVICE LEAK IN MUDPLOT NEAR CURB /** 1) MN: A322327 SN: 0066805, *TAP: SIZE: B LOC: 182 FEET FROM P LINE AT ROBERTSON S, *MB: CODE: BDN LOC: ON JOSEPH ST 182' FROM PL S ROBERTSON ST ****/ | 2017-10-26 | ARRIVED AT THE ABOVE LOCATION MADE A MUDPLOT CUT OVER THE METER BOX MADE REPAIR ON 5/8 LEAD LINE AND ALSO CHANGED BROKEN HAND WHEEL AND BACKFILLED AND CLEANED THE AREA.
201700187801 | 2017-02-04 | LEAD | 817 | ANTONINE | ANNUNCIATION | WILK | METER LEAK METER# A 317326 ACCT# 115222 558064 INLET LEAK IN THE MUDPLOT /** 1) MN: A317326 SN: 0021173, *TAP: SIZE: A LOC: 137 FEET FROM P LINE AT LAUREL, *MB: CODE: CFLM LOC: ON ANTONINE, 136' FROM P.L. LAUREL ** 2) MN: 000000 SN: 0021172, *TAP: SIZE: A LOC: 145 FEET FROM P LINE AT ANNUNCIATION, *MB: CODE: CFLM LOC: ON ANTONINE, 143' FROM P.L. ANNUNCIATION ****/ DOTTIE READY 8-29-17 EXP 9-18-17 | 2017-09-02 | REPLACED 5/8 CURB COCK. (SOC 3 FT. X 3 FT. MUDCUT.)
201700188902 | 2018-02-25 | LEAD/PLASTIC | 2831 | KENT DR | GEN MEYER AV | WILK | JOB STILL LEAKING /** 1) MN: A339700 SN: 0150774, *TAP: SIZE: B LOC: 178 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: BD12 LOC: ON KENT 179FT FROM GEN MEYER 10FT OUTSIDE ****/ | 2018-02-25 | EXCAVATED THROUGHT TREE ROOTS ON THE INLET AND OUTLET SERVICE AND REPAIR LEAK AND WE RAISE THE METER BOX TO GRADE THEN WEBACKFILL AND CLEAN UP JOB SITE
201700205101 | 2017-02-08 | LEAD/PLASTIC | 810 | JEFFERSON AV | MAGAZINE | WILK | ML METER LEAK METER# A 271886 ACCT# 112148-564466 INLET SERVICE LEAK BEHIND CURB COCK FLOODING GRASSY AREA 5/10/17 LEAK GETTING WORSE PER SR#12803910 (AJR) /** 1) MN: A286820 SN: 0039496, *TAP: SIZE: A LOC: 71 FEET FROM P LINE AT CONSTANCE, *MB: CODE: CDLM LOC: 20FT FROM LPL CURB 73' P.L. CONSTANCE ****/ DOTTIE READY 10-3-17 EXP 10-2317 | 2017-10-11 | ARRIVED ON JOB SITE FOR INLET SERVICE AND ALSO A BAD OUTLET SERVICE LEAK ON LEAD LINE.EXCAVATED IN MUDPLOT BY CURB AND MADE REPAIRS ON THE INLET AND OUTLET.
201700230101 | 2017-02-13 | LEAD | 5030 | ANNUNCIATION | SONIAT | WILK | ACCT #038655042 (NEW LOCATION #121334) A SMALL LEAK WAS FOUND AT THE WHEEL SIDE OF THE METER. /** 1) MN: A213990 SN: 0042173, *TAP: SIZE: A LOC: 442 FEET FROM P LINE AT ANNUNCIATION, *MB: CODE: BFL1 LOC: ON SONIAT,44' FROM R.P.L. ANNUNCIATION ****/ DOTTIE NREADY 10-3-17 EXP 10-23-17 | 2017-10-11 | ARRIVED ON JOB SITE FOR INLET SERVICE LEAK EXAMINE JOB AND FOUND THAT THE COCK WAS LEAKING ,EXCAVATED IN MUDPLOT AND MADE REPAIRS AND CHANGED COCK.
201700285601 | 2017-02-22 | LEAD/PLASTIC | 5754 | PASTEUR BL | BURBANK DR | WSNR | REMOVE ALL LEAD (PB) FROM SERVICE CONNECTION. REPLACE SERVICE FROM MAIN TO PROPERTY LINE. /** 1) MN: A315233 SN: 0096983, *TAP: SIZE: B LOC: 664 FEET FROM P LINE AT PRENTISS AVE, *MB: CODE: BD LOC: 664' PL PRENTISS 7FT OUTSD 10FT INSIDE ****/ | 2017-11-06 | EXCAVATED A 35 X 8 MUDPLOT CUT TO RENEW INLET SERVICE ON A 1'' CONTROLLER LINE FROM THE CURB TO THE METER BOX AND RAISE METER BOX TO GRADE. ALSO RENEWED OUTLET SERVICE FROM METER BOX TO P.L. JOB CONTINUED BECAUSE CONTROLLER LINE HAS TO BE RENEWED FROM CURB TO WATER MAIN. JOB CONTINUED JEG
201700316301 | 2017-03-01 | LEAD/PLASTIC | 1818 | BROADWAY | HICKORY | WILK | ML: METER LEAK ACCT# 132333-581524 METER # B030489 PLEASE REPAIR ASAP INLET SERVICE LEAK ON SIDEWALK /** 1) MN: B030658 SN: 0063482, *TAP: SIZE: B LOC: 160 FEET FROM P LINE AT HICKORY, *MB: CODE: AD LOC: ON BROADWAY 159.5' FROM USPL HICKORY ****/ | 2017-11-29 | EXCAVATED AND MADE REPAIRS ON A 3/4 INLET SERVICE LEAK LEAD LINE. ALSO RENEWED THE OUTLET AND RAISED THE METER TO GRADE JOB COMPLETE. JEG
201700334801 | 2017-03-06 | LEAD | 428 | S SCOTT | BANKS | WILK | ML - METER LEAK MTR# A 405178 ACCT# 128081-300579 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A335601 SN: 0055470, *TAP: SIZE: A LOC: 85 FEET FROM P LINE AT BAUDIN, *MB: CODE: BDO2 LOC: ON SO. SCOTT,79' FROM L.R.P.L. BAUDIN ****/ | 2017-11-03 | REPLACED 5/8 CURB COCK TIED INTO LEAD
201700334802 | 2017-11-06 | LEAD/PLASTIC | 428 | S SCOTT | BANKS | WSNR | WSNR-REMOVE ALL LEAD FROM MAIN TO PROPERTY /** 1) MN: A335601 SN: 0055470, *TAP: SIZE: A LOC: 85 FEET FROM P LINE AT BAUDIN, *MB: CODE: BDO2 LOC: ON SO. SCOTT,79' FROM L.R.P.L. BAUDIN ****/ DOTTIE READY 11-30-17 EXP 12-20-17 | 2017-12-02 | ARRIVED ON JOB EXCAVATED IN STREET NO WATER SERVICE FOUND WITH TAP MEASUREMENT GIVEN FOUND WATER SERVICE IN SIDEWALK UNDER DRIVEWAY,CUSTOMER REFUE TO LET DRIVEWAY BE CUT. (SOC 5 FT. X 20 FT. ASPHALT F/D )
201700342901 | 2017-03-07 | LEAD/PLASTIC | 201 | CAMBRIDGE CT | WESTCHESTER PL | WILK | MI- LEAK IN STREET. MARK BY DATE 6/29/17***EXPIRATION DATE 7/19/17**** INLET SERVCE LEAK IN ASPAHLT STREET /** 1) MN: A319925 SN: 0125588, *TAP: SIZE: A LOC: 29 FEET FROM P LINE AT WESTCHESTER, *MB: CODE: BLM2 LOC: 29FT FROM PL WESTCHESTER 2' OUTSIDE PL 11' INSIDE ****/ | 2017-12-12 | EXCAVATED METER BY HAND REMOVED LEAD FROM OUTLET CHANGED COCK ON INLET SIDE AND RAISED BOX TO GRADE
201700369801 | 2017-03-12 | LEAD/PLASTIC | 1233 | FERN | PLUM | WILK | ML: METER LEAK METER # A412309 ACCOUNT# 114105-583084 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A240528 SN: 0018659, *TAP: SIZE: A LOC: 68 FEET FROM P LINE AT PLUM, *MB: CODE: CFN1 LOC: 68FT FROM RPL PLUM IN GARDEN ON FERN ST ****/ | 2017-12-13 | EXCAVATED IN MUDPLOT OVER A 5/8" INLET SERVICE LEAK PLASTIC OUTLET CHANGE THE COCK SEALED BACKFILLED AND DRESS UP
201700402601 | 2017-03-18 | LEAD | 1103 | LOWERLINE | ZIMPEL | WILK | ML - METER LEAK MTR# A 406200 ACCT# 131448-583245 EXAMINE INLET & OUTLET FOR A LEAK IN TREE ROOTS 6/23/17 CUSTOMER STATES HAS POOR PRESSURE INSIDE HOME NOW PER SR#12807546 (AJR) /** 1) MN: A278035 SN: 0062160, *TAP: SIZE: A LOC: 46 FEET FROM P LINE AT LOWERLINE, *MB: CODE: ADHL LOC: ON ZIMPEL,45' FROM L.P.L. LOWERLINE ****/ | 2017-10-11 | ARRIVED AT JOB HAD TO GET CARS REMOVED FROM COLLEGE STUDENTS IN CLASS. HAD TO CHANGE BAD METER BOX COCK. COULD NOT REMOVE LEAD FROM INLET OR OUTLET. NEED CARS TO BE REMOVE. MAYBE ON A SUNDAY WHEN CLASS IS OUT. JEG
201700407202 | 2017-04-27 | LEAD | 2626 | CAMBRONNE | APPLE | WMEX | EXAMINED AND FOUND LEAK ON METER BOX BUT UNABLE TO EXCAVATED DUE TO METER IN ROCKS AND GRAVEL REF TO CREW WITH MACHINE TO MAKE REPAIRS /** 1) MN: A325328 SN: 0072359, *TAP: SIZE: B LOC: 197 FEET FROM P LINE AT APPLE, *MB: CODE: CDN LOC: 197FT FROM PL APPLE ****/ | 2017-09-30 | EXCAVATED IN MUDPLOT ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVER SAND LJF
201700410301 | 2017-03-20 | LEAD | 7026 | WALMSLEY AV | AUDUBON BL | WMTLK | LOCATIONID#172631-596125 METER#B022840 METERBOX OVERFLOWING 06/28/17 CUSTOMER STATES LEAK AT THE METER HAS GOTTEN WORSE (KSW) /** 1) MN: B022840 SN: 0103513, *TAP: SIZE: B LOC: 105 FEET FROM P LINE AT AUDUBON BLVD, *MB: CODE: ADK2 LOC: 105FT PL AUDUBON BL 8' OUTSIDE 4' INSIDE CURB ****/ DOTTIE READY 10-27-17 EXP 11-16-17 | 2017-11-03 | REPLACED 3/4 CURB COCK TIED INTO LEAD
201700442001 | 2017-03-24 | LEAD/PLASTIC | 2561 | CHELSEA DR | DURBRIDGE DR | WILK | MI- CHECK FOR LEAK AT PROPERTY LINE INLET SERVICE LEAK @ CURB /** 1) MN: C008156 SN: 0142276, *TAP: SIZE: C LOC: 37 FEET FROM P LINE AT DURBRIDGE DR, *MB: CODE: AD2M LOC: ON CHELSEA 37' FROM DPL DURBRIDGE DR 1' NEAR DRIVE ****/ | 2017-09-04 | EXCAVATED METER BOX AND FOUND LEAK ON INLET SERVICE CHANGED COCK IN BOX AND BACKFILLED WITH COLD MILL AND SAND
201700453001 | 2017-03-28 | LEAD/PLASTIC | 5701 | CARLISLE CT | RUE COLETTE | WILK | ML- METER LEAK ACCT.# 232665-416998 MTR.# A 136558 INLET SERVICE LEAK /** 1) MN: A136558 SN: 0146755, *TAP: SIZE: B LOC: 106 FEET FROM P LINE AT COLLETTE RUE, *MB: CODE: ADKL LOC: ON CARLISLE CT., 104' FROM P.L. RUE COLETTE, 5' ****/ | 2017-11-16 | EXCAVATED METER BOX AND CHOPPED TREE ROOTS TO EXPOSE LEAK BY HAND FOUND LEAK ON INLET SERVICE REPAIRED SERVICE AND INSTALLED NEW BOX COCK AND WHEEL
201700461001 | 2017-03-29 | LEAD | 3900 | MAGAZINE | GEN TAYLOR | WMTLK | NEW ACCT# 119528-557215 OLD ACCT# 035645 07 0 METER# A181692 EXCESSIVE CONSUMPTION ** POSS METER LEAK /** 1) MN: A181692 SN: 0172253, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT MAGAZINE, *MB: CODE: AG LOC: ON GEN. TAYLOR,94.3' FROM R.P.L. MAGAZINE ****/ DOTTIE READY 2-15-18 EXP 3-7-18 | 2018-03-06 | ARRIVED ON JOB EXCAVATED IN MUDPLOT FOUND 5/8 METER BOX COCK LEAKING MADE REPAIRS AND BACKFILLED. JOB COMPLETE TIED INTO LEAD
201700493801 | 2017-04-05 | LEAD | 1706 | NAPOLEON AV | CARONDELET | WMTLK | LOCATIONID#138144-572156 METER#B033506 METERBOX OVERFLOWING /** 1) MN: B019691 SN: 0010954, *TAP: SIZE: B LOC: 12 FEET FROM P LINE AT NAPOLEON AVE, *MB: CODE: AFHK LOC: ON CARONDELET 27FT FROM NAPOLEON AVE. ****/ DOTTIE READY 2-1-18 EXP 2-21-18 | 2018-02-05 | EXAMINE JOB AND CLEANED OUT METER BOX AND FOUND BAD METER COCK.EXCAVATED IN MUPLT AND MADE REPAIRS ON METER COCK AND BACKFILL JOB WITH RIVERSAND AND TIED COCK BACK ONTO LEAD LINE.
201700496701 | 2017-04-05 | LEAD | 4225 | DRYADES | MILAN | WILK | ML- METER LEAK METER # A121597 INLET SERVICE LEAK BAD BLEEDER VALVE /** 1) MN: A121597 SN: 0035236, *TAP: SIZE: B LOC: 136 FEET FROM P LINE AT MILAN, *MB: CODE: CDLM LOC: ON DRYADES 135..6FT FROM MILAN ****/ DOTTIE READY 10-26-17 EXP 11-15-17 | 2017-11-11 | EXCAVATED 3 X 3 MUD PLOT THROUGH TREE ROOTS REPLACED 5/8 INCH METER COCK TO STOP LEAK BACKFILL AND CLEANED THE AREA
201700497101 | 2017-04-05 | LEAD | 4013 | EVE | S BROAD | WILK | **********PICK UP********** INLET SERVICE LEAK IN AN ASPHALT STREET FLOODING STREET & GUTTER 10/24/17 LEAK HAS GOTTEN WORSE NOW FLOODING AREA PER SR#12818766 (AJR) /** 1) MN: A283933 SN: 0073892, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT BROAD S, *MB: CODE: DL LOC: ON EVE 110FT FROM LSPL BROAD ****/ | 2017-11-11 | EXCAVATED 12 X 8 STREET CUT MADE REPAIRS ON INLET SERVICE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201700502601 | 2017-04-06 | LEAD | 2809 | MILAN | WILLOW | WILK | ML- METER LEAK IN EMPTY METER BOX INLET SERVICE LEAK @ DRIVEWAY /** 1) MN: A261839 SN: 0016590, *TAP: SIZE: A LOC: 212 FEET FROM P LINE AT WILLOW, *MB: CODE: AFK2 LOC: ON MILAN 212FT FROM WILLOW ****/ DOTTIE READY 10-26-17 EXP 11-15-17 | 2017-11-11 | EXCAVATED 3 X 2 MUD PLOT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201700529001 | 2017-04-11 | LEAD/PLASTIC | 1176 | MAGAZINE | ERATO | WILK | ML-- METER LEAK METER # A372876 ACCT# 119623537145 INLET SERVICE LEAK INSIDE METER BOX ON SIDEWALK /** 1) MN: A277141 SN: 0033937, *TAP: SIZE: A LOC: 101 FEET FROM P LINE AT MAGAZINE, *MB: CODE: BEHK LOC: SIDE 2ND METER ON ERATO 101.5' FROM LRPL MAGAZINE ** 2) MN: A279081 SN: 0033937, *TAP: SIZE: A LOC: 97 FEET FROM P LINE AT MAGAZINE, *MB: CODE: OOO LOC: ON ERATO 97' FROM PL MAGAZINE 4' OUTSIDE PL 6' INS ****/ | 2017-09-18 | BROKE THE SIDEWALK AND EXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE PUT A BARREL ON THE JOB SITE TO COMEBACK AND BACKFILL THEN WE CLEAN UP JOB SITE
201700536601 | 2017-04-12 | LEAD | 5237 | CAMP | BELLECASTLE | WILK | ML METER LEAK METER # A314782 ACCOUNT # 104182-559392 INLET SERVICE LEAK ON SIDEWALK /** 1) MN: A314782 SN: 0006385, *TAP: SIZE: B LOC: 33 FEET FROM P LINE AT BELLECASTLE, *MB: CODE: CE LOC: ON CAMP 32FT FROM LSPL OF BELLECASTLE ****/ DOTTIE READY 10-26-17 EXP 11-15-17 | 2017-11-06 | REPLACED 5/8 CURB COCK TIED INTO LEAD UNABLE TO REMOVE LEAD DUE TO CAR PARKED ON JOB. *******OLD METER INFO********* METER:A4314782 FACTORY:530722665 MAKE:HERSEY READ:9172
201700537501 | 2017-04-13 | LEAD/PLASTIC | 8306 | OLEANDER | DANTE | WMTLK | ACCT#141590 MET#A295531 PLEASE REPAIR LEAK @ CURB COCK /** 1) MN: A295531 SN: 0072894, *TAP: SIZE: B LOC: 51 FEET FROM P LINE AT DANTE, *MB: CODE: ADL2 LOC: ON OLEANDER, 52' FROM P.L. DANTE ****/ | 2017-10-03 | EXCAVATED A 4 X 7 CUT IN CONCRETE DRIVEWAY/ SIDEWALK OVER A 5/8 INLET SERVICE LEAK. LEAD ON INLET & CHANGED OUTLET CHANGED COCK RAISE METERBOX UP TO GRADE AND REPLACED THE OUTLET FROM METERBOX TO PROPERTY BACKFILLED AND DRESSED UP WITH RIVERSAND AND COLDMILL. JEG
201700549402 | 2017-05-17 | LEAD/PLASTIC | 638 | CAMP | CAPDEVILLE | WILK | NEED TO CUT THE STREET TO MAKE REPAIRS PUMP DOWN MANHOLE TO EXAMINED METER FOR LEAK FOUND INSIDE MANHOLE ON A 1 1/2 WATER COMING OUT TOP FOR MANHOLE FLOODING SIDEWALK /** 1) MN: D006719 SN: 0000981, *TAP: SIZE: D LOC: 62 FEET FROM P LINE AT CAPDEVILLE, *MB: CODE: CDM3 LOC: ON CAMP 62' FROM PL CAPDEVILLE 9' OUTSIDE PL 3' IN ****/ | 2017-12-11 | ARRIVED ON JOB SITE EXAMINED METER IN MANHOLE FOUND LEAK STREET SIDE OF THE COCK HAD TO CUT OUT STREET TO REPAIR
201700549405 | 2017-12-12 | LEAD/PLASTIC | 638 | CAMP | CAPDEVILLE | WILK | /** 1) MN: D006719 SN: 0000981, *TAP: SIZE: D LOC: 62 FEET FROM P LINE AT CAPDEVILLE, *MB: CODE: CDM3 LOC: ON CAMP 62' FROM PL CAPDEVILLE 9' OUTSIDE PL 3' IN ****/ | 2017-12-12 | EXPOSED LINE IN STREET REMOVED LEAKING LINE REPAIRED 2" LINE BARRICADED WHOLE IN STREET NEED DRESSED WITH SAND AND COAL MILL
201700564301 | 2017-04-19 | LEAD/PLASTIC | 4000 | UTAH | DONNA DR | WILK | MI: LEAK IN THE STRRET INLET SERVICE LEAK IN GUTTER BOTTOM NEXT TO MAIL BOX 4/21/17 ALSO RAISE METER TO GRADE 5/30/17 UPGRADE TO B PER INSPC C PLAINS (AJR) /** 1) MN: A280081 SN: 0158541, *TAP: SIZE: C LOC: 246 FEET FROM P LINE AT DONNA DR, *MB: CODE: BDKM LOC: 361'FRM PL DONNER 2'FRM CORNER PL RIO GRANDE ****/ | 2017-11-07 | EXAMINED LEAK LEAK COMING FROM MAIN CAUTION OF AREA WHERE LEAK COMING FROM MAAY BE DANGEROUS UNABLE TO LOCATE METER BOX FOR METER READING NEED MACHINE TO COMPLETE JOB
201700566401 | 2017-04-20 | LEAD/PLASTIC | 5811 | ABBEY DR | ALBANY CT | WILK | ML - METER LEAK MTR# A 145256 ACCT# 231640-418057 INLET SERVICE LEAK /** 1) MN: A210133 SN: 0142085, *TAP: SIZE: B LOC: 256 FEET FROM P LINE AT DURBRIDGE DR, *MB: CODE: BD36 LOC: RES. 256FT FROM PL DURBRIDGE ****/ | 2017-10-03 | BROKE THE STREET AND EXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOB SITE.
201700566801 | 2017-04-20 | LEAD/PLASTIC | 1824 | BODENGER BL | MAGELLAN | WILK | LOCATIONID#225362-701537 METER#A405618 BLEEDER LEAK /** 1) MN: A325802 SN: 0076147, *TAP: SIZE: B LOC: 921 FEET FROM P LINE AT BOLBOA BLVD, *MB: CODE: AD LOC: ON BODENGER BLVD 943' FROM PL BOLBOA BLVD ****/ | 2017-09-04 | EXCAVATED ON THE INLET AND OUTLET SERVICE AND REPAIR LEAK AND RENEW THE OUTLET SERVICE AND RAISE THE METERBOX TO GRADE THEN WE BACKFILLED
201700585701 | 2017-04-24 | LEAD/PLASTIC | 505 | S GENOIS | BAUDIN | WILK | ML- METER LEAK METER# A398608 ACCT# 135817-533464 INLET SERVICE LEAK /** 1) MN: A308335 SN: 0066556, *TAP: SIZE: A LOC: 52 FEET FROM P LINE AT BAUDIN, *MB: CODE: CDL7 LOC: ON S GENOIS 53FT FROM PL OF BAUDIN ****/ DOTTIE READY 10-26-17 EXP 11-15-17 | 2017-10-26 | ARRIVED AT THE ABOVE LOCATION MADE REPAIRS ON THE LEAD AND THEN BACKFILLED AND CLEANED THE AREA
201700597202 | 2017-05-03 | LEAD/PLASTIC | 8830 | STROELITZ | GEN OGDEN | WILK | EXCAVATED IN AROUND AROUND 5/8" MEETR BOX , FOUND LEAK DEEP UNDER METER BOX , REFE TO CREW WITH MACHINE FOR INLET SERVICE LEAK . CLEANED AND DRESS UP AREA FOUND LEAD ON INLET /** 1) MN: A241428 SN: 0103334, *TAP: SIZE: A LOC: 44 FEET FROM P LINE AT STROELITZ, *MB: CODE: BDL5 LOC: ON GEN OGDEN, 44' FROM P.L. STROELITZ, 6' OUTSIDE ****/ | 2018-05-30 | EXCAVATED AND MADE REPAIRS ON A 5/8" INLET SERVICE LEAK , ALSO RENEWED THE OUTLET FROM THE METER BOX TO PROPERTY LEAD ON INLET PLASTIC ON THE OUTLET JOB COMPLETE
201700597203 | 2018-05-31 | LEAD | 8830 | STROELITZ | GEN OGDEN | WSNR | REPLACE WATER SERVICE FROM WATER MAIN TO METER BOX 180239040 EXP 6/5/18 /** 1) MN: A241428 SN: 0103334, *TAP: SIZE: A LOC: 44 FEET FROM P LINE AT STROELITZ, *MB: CODE: BDL5 LOC: ON GEN OGDEN, 44' FROM P.L. STROELITZ, 6' OUTSIDE ****/ | 2018-11-06 | JOB WILL BE RE-SCHEDULE AT A LATER DATE DO TO PAVEMENT BACK LOG
201700611901 | 2017-04-28 | LEAD/PLASTIC | 4909 | WILLOW | UPPERLINE | WILK | MI LEAK IN SIDEWALK INLET SERVICE LEAK /** 1) MN: A269743 SN: 0066577, *TAP: SIZE: B LOC: 54 FEET FROM P LINE AT UPPERLINE, *MB: CODE: CEL1 LOC: ON WILLOW 56.3FT FROM UPPERLINE ****/ DOTTIE READY 8-18-17 EXP 9-7-17 | 2017-08-30 | ARRIVED AT THE ABOVE LOCATION MADE A 3X3 SIDEWALK CUT OVER THE METERBOX, MADE REPAIRS THEN BACKFILLED AND CLEANED THE AREA
201700612405 | 2017-09-18 | LEAD/PLASTIC | 4926 | BERKLEY DR | HERALD | WILK | LEAK CONTINUES. -WATER INLET LEAK ***DO NOT CREATE RESTORATION WORK ORDER. DPW ALREADY HAS RESTORATION WORK ORDER SEE WO#201700612404*** /** 1) MN: A228173 SN: 0129796, *TAP: SIZE: B LOC: 432 FEET FROM P LINE AT HUNTLEE DR, *MB: CODE: ADLM LOC: ON BERKLEY DR 433' FROM PL HUNTLEE DR 6' OUTSIDE P ****/ | 2017-11-28 | EXCAVATED METER BOX AND FOUND LEAK ON OUTLET RAN NEW LINE FROM METER BOX TO PROPERTY
201700623701 | 2017-05-02 | LEAD | 4219 | LOYOLA AV | MILAN | WILK | MI- LEAK AT THE SIDEWALK EXAMINE INLET SERVICE AT SIDEWALK FOR A LEAK /** 1) MN: A280069 SN: 0003457, *TAP: SIZE: A LOC: 0 FEET FROM LINE AT LOYOLA AVE, *MB: CODE: CFN1 LOC: ****/ DOTTIE READY 10-26-17 EXP 11-15-17 | 2017-11-11 | MADE REPAIR ON INLET SERVICE LINE NO METER FOUND
201700638101 | 2017-05-05 | LEAD/PLASTIC | 2027 | ST NICK | COPERNICUS | WMTLK | ML- METER LEAK METER#A298585 ACCT#231310-409964 MARK BY DATE 5/17/17*** EXPIRATION DATE 6/6/17****** EXAMINE INLET AND OUTLET SERVICE AT SIDEWALK FOR A LEAK, SIDEWALK FLOODED, LEFT 2 (TWO) CONES FOR PROTECTION /** 1) MN: A138258 SN: 0141292, *TAP: SIZE: B LOC: 2 FEET FROM P LINE AT COPERNICUS, *MB: CODE: A LOC: ON ST NICK 2' FROM DPL COPERNICUS 3' INSIDE CURB ****/ | 2017-09-19 | ARRIVED ON JOB SITE FOUND METER TO HIGH FOR GRADE EXCVAATED BY HAND LOWERED METER BOX
201700642701 | 2017-05-08 | LEAD/PLASTIC | 1240 | MAGAZINE | THALIA | WMTLK | *LOCATIONID#126624-569610 METER#A276829 METERBOX FILLED WITH WATER,METER LEAK /** 1) MN: A295619 SN: 0050966, *TAP: SIZE: A LOC: 65 FEET FROM P LINE AT THALIA, *MB: CODE: CDV LOC: ON MAGAZINE,64' FROM L.R.P.L. THALIA ****/ | 2017-12-19 | BROKE THE SIDEWALK AND EXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE LEFT A BARREL ON JOB SITE AFTER BACKFILL BECAUSE COLDMILL WAS WET
201700643901 | 2017-05-08 | LEAD | 5210 | MAGAZINE | DUFOSSAT | WMTLK | LOCATIONID#114953-559593 METER#A133920 LEAK INSIDE METERBOX 07/18/17 LEAK AT SIDEWALK FLOODING GUTTER BOTTOM GETTING OFF INTO DRAIN CATCH BASIN PER INSP B BOURNES UPGRADED TO PRIORITY -C- (FCP) /** 1) MN: A133920 SN: 0017923, *TAP: SIZE: A LOC: 103 FEET FROM P LINE AT DUFOSSAT, *MB: CODE: CDL1 LOC: ON MAGAZINE 104.5FT FROM PL OF DUFOSSAT ****/ DOTTIE READY2-15-18 EXP 3-7-18 | 2018-03-06 | ARRIVED ON JOB EXCAVATED IN SIDEWALK FOUND 5/8 METER BOX COCK LEAKING MADE REPAIRS AND BACKFILLED JOB COMPLETE TIED INTO LEAD.
201700644501 | 2017-05-08 | LEAD | 2719 | MARENGO | MAGNOLIA | WMTLK | LOCATIONID#117512-552939 METER#A153021 LEAK INSIDE METERBOX /** 1) MN: A153021 SN: 0025485, *TAP: SIZE: A LOC: 159 FEET FROM P LINE AT MAGNOLIA, *MB: CODE: CFT1 LOC: METER ON REAR STREET. ****/ DOTTIE READY 1-10-18 EXP 1-30-18 | 2018-01-25 | EXAMINE JOB PUMP METER BOX OUT AND FOUND METER COCK LEAKING EXCAAVTED ON 4 X 4 MUDPLOT AND MADE REPAIRS TO METER COCK.BACKFILLED JOB WITH RIVERSAND IN MUDPLOT TIED INTO LEAD.
201700644503 | 2018-05-30 | LEAD | 2719 | MARENGO | MAGNOLIA | WSNR | WSNR WATER - SERVICE -NEEDS REPAIR (TRUCK 577 REPLACED CURB COCK BUT LEAD SREVICE NEEDS TO BE REMOVED) /** 1) MN: A153021 SN: 0025485, *TAP: SIZE: A LOC: 159 FEET FROM P LINE AT MAGNOLIA, *MB: CODE: CFT1 LOC: METER ON REAR STREET. ****/ /** 1) MN: A153021 SN: 0025485, *TAP: SIZE: A LOC: 159 FEET FROM P LINE AT MAGNOLIA, *MB: CODE: CFT1 LOC: METER ON REAR STREET. ****/ | 2019-04-09 | REFERRED TO CONTRACTOR
201700648402 | 2017-06-26 | LEAD/PLASTIC | 35 | CHATHAM DR | CHASE | WMRE | EXAMINED AND FOUND METERBOX COVERED UP REFER TO CREW TO UNCOVER METER BOX ALSO RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY /** 1) MN: B020853 SN: 0118116, *TAP: SIZE: B LOC: 399 FEET FROM P LINE AT CHASE, *MB: CODE: CDL LOC: ON CHATHAM DR., 400' FROM P.L. CHASE, 7' OUTSIDE ****/ | 2017-09-01 | EXCAVATED A 4 X 8 TRENCH THROUGH TREE ROOT UTILLITESOVER A 3/4' SERVICE THAT WAS RAISED UP TO GRADE AND REPLACED OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILLED AND DRSSS UP WITH RIVER SAND LASTIC INLET LEAD OUTLET,,,,JOB COMPLETE
201700667601 | 2017-05-11 | LEAD/PLASTIC | 453 | AUDUBON BL | FONTAINEBLEAU DR | WMTLK | LOCATIONID#136609 METER#A224807 METERBOX OVERFLOWING /** 1) MN: A224807 SN: 0066954, *TAP: SIZE: B LOC: 385 FEET FROM P LINE AT FONTAINBLEAU DR, *MB: CODE: CDLM LOC: ON AUDUBON 454' FROM PL OF TONTAINBLEAU DR ****/ DOTTIE READY 8-24-17 EXP 9-13-17 | 2017-09-15 | EXCAVATE IN TREE ROOTS OVER 5/8 OUTLET SERVICE. REPLACE 5/8 HANDWHEEL TIED LINE BACK INTO LEAD. RAISE METER TO GRADE AND CLEAN JOB SITE.
201700668001 | 2017-05-11 | LEAD/PLASTIC | 6940 | HAYNE BL | TARPON | WMTLK | LOCATIONID#179563-461716 METER#B036882 METERBOX OVERFLOWING 12/27/17 LEAK HAS GOTTEN WORST & AFFECTING BILL REFER TO (KSW) MARK BY 05/30/17 EXPIRE 06/19/17 /** 1) MN: B022823 SN: 0135336, *TAP: SIZE: B LOC: 84 FEET FROM P LINE AT HAYNES BLVD, *MB: CODE: AFHO LOC: ON REDFISH, 84' FROM P.L. HAYNES BLVD., 4' OUTSIDE ****/ | 2018-08-02 | EXCAVATED IN A 4X4 MUD PLOT BY HAND FOUND LEAD ON INLET, WITH 3/4 CRUB COCK RAIS METER BOX TO GRADE BACK FILL AND DRESS JOB CONTINUED
201700671801 | 2017-05-11 | LEAD/PLASTIC | 3710 | RUE RENEE | BRUNSWICK CT | WILK | ML-METER LEAK ACCT#233859-417181 METER#C018343 INLET SERVICE LEAK /** 1) MN: C018343 SN: 0151771, *TAP: SIZE: C LOC: 15 FEET FROM P LINE AT BRUNSWICK CT., *MB: CODE: ADM1 LOC: ON RUE RENEE, 14.5' FROM D.P.L. BRUNSWICK CT., 3' ****/ | 2017-11-29 | EXCAVATED METER BOX TO EXPOSED LEAK FOUND LEAK ON BOX COCK REPLACED WITH NEW COCK AND BACKFILLED
201700685301 | 2017-05-15 | LEAD/PLASTIC | 6409 | PEONY | SULLEN PL | WILK | METER LEAK A-395277 ACCT # 234988-419443 INLET SERVICE LAK IN GRASS /** 1) MN: A316240 SN: 0158339, *TAP: SIZE: A LOC: 149 FEET FROM P LINE AT SULLEN, *MB: CODE: ADM4 LOC: ON PEONY 149FT FROM SULLEN 10FT OUTSIDE ****/ | 2017-08-31 | ARRIVED ON JOB EXAMINED METER EXCAVATED BY HAND FOUND LEAK INLET AND REPAIRED
201700688901 | 2017-05-15 | LEAD | 3420 | BIENVILLE |  | WMTLK | MI- LEAK AT THE SIDEWALK EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: A301228 SN: 0023123, *TAP: SIZE: A LOC: 138 FEET FROM P LINE AT N JEFF DAVIS PKWY, *MB: CODE: CFL5 LOC: INSIDE 138' P.L. N JEFF DAVIS PKWY ****/ DOTTIE READY 1-10-18 EXP 1-30-18 | 2018-01-25 | EXAMINE JOB PUMP WATER OUT METER BOX AND FOUND THAT BOTH METER COCK WAS LEAKING.MADE REPAIRS TO BOTH COCKS,NO METER WAS NOT IN METER BOX .EXCAVATED ON 4 X 4 MUDPLOT AND BACKFILLED WITH RIVERSAND WITH RIVERSAND .TIED ONTO LEAD.
201700710001 | 2017-05-19 | LEAD/PLASTIC | 1721 | UPPERLINE | BARONNE | WMTLK | **********PICK UP********** EXAMINE INLET & OUTLET SERVICE FOR A LEAK BOTH METERS UNDER WATER 6/9/17 LEAK GETTING WORSE PER SR#12806384 (AJR) 9/14/17 LEAK HAS GOTTEN WORSE PER SR#12814856 (AJR) /** 1) MN: A117120 SN: 0002443, *TAP: SIZE: A LOC: 11 FEET FROM P LINE AT BARONNE, *MB: CODE: CD3 LOC: 2ND IN FRONT ****/ DOTTIE READY 9-6-17 EXP 9-26-17 | 2017-09-18 | ARRIVED ON SITE EXCAVATED IN MUDPLOT FOUND LEAK ON LEAD INLET SERVICE ,REPLACED 3 FT. OF LEAD WITH 3 FT OF PLASTIC TUBING BACKFILLED DRESSED 4 FT. X 4FT. MUDCUT.
201700731501 | 2017-05-24 | LEAD | 2203 | REV JOHN RAPHAEL JR WAY |  | WMTLK | LOCATIONID#119033-547509 METER#A422302 METERBOX OVERFLOWING /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-01-29 | REPLACED 5/8 CURB COCK TIED INTO LEAD
201700766401 | 2017-06-02 | LEAD/PLASTIC | 1931 | RIVER OAKS DR | GEN MEYER AV | WILK | WM LEAK IN THE GRASS BUBBLING UP INLET SERVICE LEAK NEAR SIDEWALK FLOODING AREA, FOUND FLAGS AND BARRELS UPON ARRIVAL /** 1) MN: A225835 SN: 0121460, *TAP: SIZE: B LOC: 69 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: ADM1 LOC: ON RIVER OAKS DR., 69' FROM P.L. GEN. MEYER AVE., ****/ | 2017-10-23 | ARRIVED ON JOB SITE EXAMINED METER EXCAVATED BY HAND FOUND LEAK ON INLET FOUND PLASTIC ON INLET AND REPAIRED
201700774501 | 2017-06-05 | LEAD/PLASTIC | 1209 | L B LANDRY AV | DE ARMAS | WILK | WM - LEAK IN THE STREET ACROSS FROM SCHOOL, CLOSER TO CORNER OF DE ARMAS INLET SERVICE LEAK AT MAIN IN ASPHALT STREET FLOODING AREA **CHANGED FROM 1221 L B LANDRY AV** 6/10/17 LEAK GETTING WORSE NOE FLOODING AREA PER SR#12806493 (AJR) /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-11-14 | ARRIVED ON JOB SITE HAD TO METER FOUND METER EXAMINED METER EXCAVTED BY HAND FOUND LEAK ON INLET AND REMOVED LEAD FROM OUTLET TO PROPERTY AND REPAIRED LEFT A WHIP FOR PROPERTY TO TIE IN FOUND NO METER RAISED METER BOX TO GRADE
201700781101 | 2017-06-06 | LEAD/PLASTIC | 802 | PINE | MAPLE | WMRE | MI LOCATE AND RAISE METER METER # A-422585 ACCT # 152989-584625 LOCATE/RAISE METER TO GRADE /** 1) MN: A286165 SN: 0002529, *TAP: SIZE: A LOC: 15 FEET FROM P LINE AT MAPLE, *MB: CODE: AD4 LOC: ON PINE 15FT FROM U.S.P.L. OF MAPLE ****/ | 2017-12-25 | MADE A 4 X 4 SIDEWALK CUT . EXCAVATED IN TREE ROOTS AND MADE REPAIRS FROM THE METER TO PROPERTY. LOCATED AND RAISED THE METER TO GRADE. INLET LEAD OUTLET PLASTIC. REFER CUT TO PAVING. JOB COMPLETE. JEG
201700787301 | 2017-06-07 | LEAD | 2908 | PALMER AV | N PETERS | WMTLK | WM-LEAK IN THE SIDEWALK EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A262359 SN: 0068155, *TAP: SIZE: B LOC: 76 FEET FROM P LINE AT JEFFERSON AVE, *MB: CODE: CDM1 LOC: ON PALMER AVE 76.5FT FROM PL OF JEFFERSON AVE ****/ | 2018-04-04 | REPLACED 5/8 CURB COCK TIED INTO LEAD.
201700814001 | 2017-06-13 | LEAD/PLASTIC | 10 | VIVIAN CT | HUNTLEE DR | WILK | ML METER LEAK ACCT# 227067-415958 METER# A258629 INLET SERVICE LEAK IN MUDPLOT FLOODING SIDEWALK 7/28/17 LEAK GETTING WORSE PER SR#12810643 (AJR) 9/8/17 LEAK GETTING WORSE AND RUNNING INTO STREET PER SR#12814316 (AJR) /** 1) MN: A258629 SN: 0123451, *TAP: SIZE: A LOC: 177 FEET FROM P LINE AT HUNTLEE DR, *MB: CODE: BFK LOC: ON VIVIAN CT., 177' FROM P.L. HUNTLEE DR., 4' ****/ | 2017-09-09 | EXCAVATED ON THE INLET AND OUTLET SERVICE AND REPAIR LEAK AND RENEW THE OUTLET FROM PROPERTY THEN WE BACKFILL AND CLEAN UP JOB SITE
201700818702 | 2017-07-06 | LEAD/PLASTIC | 2427 | LEONIDAS |  | WILK | METER LEAK INLET SERVICE LEAK NO METER IN BOX CURB COCK IN OFF POSITION WATER PASSING THROUGH. LEAKALSO FLOODINIG SIDEWALK & GUTTER BOTTOM /** 1) MN: A303133 SN: 0083758, *TAP: SIZE: A LOC: 230 FEET FROM P LINE AT CLAIBORNE AVE S, *MB: CODE: ADL7 LOC: ON LEONIDAS 215 FT FROM PL S CLAIBORNE AVE ****/ NEED MACHINE METERBOX IN SIDEWALK /** 1) MN: A303133 SN: 0083758, *TAP: SIZE: A LOC: 230 FEET FROM P LINE AT CLAIBORNE AVE S, *MB: CODE: ADL7 LOC: ON LEONIDAS 215 FT FROM PL S CLAIBORNE AVE ****/ | 2017-10-14 | MADE A 4 X 4 SIDEWALK CUT EXCAVATED AND MADE REPAIRS ON A 5/8 INLET LEAK. ALSO RAISED THE METER TO GRADE AND RENEWED THE OUTLET LEAD IN THE INLET JEG
201700840201 | 2017-06-19 | LEAD/PLASTIC | 1854 | GEN COLLINS AV | WALL BL | WILK | ML METER LEAK METER#C024578 ACCT#231000-408799 INLET SERVICE LEAK IN MUDPLOT 08/24/17 LEAK GETTING WORSE (NLD) /** 1) MN: C024578 SN: 0139872, *TAP: SIZE: C LOC: 224 FEET FROM P LINE AT WALL, *MB: CODE: CDKO LOC: 219FT FROM P.L. WALL ****/ | 2017-09-04 | EXCAVATED METER BOX AND FOUND LEAK ON OUTLET SERVICE REPLACE SERVICE LINE FROM METER BOX TO PROPERTY INSTALLED METER BOX COMPLETE
201700843803 | 2017-09-18 | LEAD | 1109 | PHILIP | MAGNOLIA | WMTBG | ARRIVED AT THE ABOVE LOCATION MADE 5X5 MUDPLOT WAS UNABLE TO FIND THE METER, MEASURE THE LOCATION AND THE METER ELL UNDER THE SIDEWALK RETURN FIRST AM TO CUT OUT DRIVEWAY ARRIVED ON JOB CONTRACTOR ASKED TO WAIT UNTIL THEY FINISH WHAT THEY DOING TO COMPLETE JOB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ DOTTIE READY 1-2-18 EXP 1-22-18 | 2018-01-29 | EXAMINE JOB AND LOCATED METER UNDER SIDEWALK AND MADE A 5FT X 9 FT CUT IN DRIVEWAY,EXCAVATED IN DRIVEWAY AND MADE REPAIRS ON A 1" METER COCK ONTO LEAD AND BACKFILLED WITH RIVERSAND AND COLDMILL.
201700851201 | 2017-06-22 | LEAD/PLASTIC | 2355 | HOLIDAY DR | FIESTA | WILK | WM-LEAK IN THE SIDEWALK INLET SERVICE LEAK IN GRASS @ CURB /** 1) MN: A285420 SN: 0145239, *TAP: SIZE: C LOC: 200 FEET FROM P LINE AT FIESTA DR, *MB: CODE: BDK LOC: 187FT FROM P.L. FIESTA ****/ | 2017-11-03 | EXCAVATED METER OBSERVED LEAK ON INLET SERICE COCK REPAIRED BACKFILLED HOLE
201700868301 | 2017-06-27 | LEAD | 7903 | FRERET | FERN | WMTLK | *******PICKUP JOB******* EXAMINE INLET AND OUTLET SERVICE INSIDE METER BOX FOR A LEAK /** 1) MN: A144162 SN: 0011932, *TAP: SIZE: B LOC: 54 FEET FROM P LINE AT FERN LSPL, *MB: CODE: ADK LOC: 54'FROM LSPL FERN ****/ | 2017-10-10 | EXCAVATED IN MUD PLOT TO REPAIR BAD BOX COCK . FOUND LEAD ON INLET AND OUTLET NEED REROUT OUTLET JOB CONT-- REPLACE LEAD SERVICE FROM WATER MAIN TO PROPERY LINE 170443743 9/26/-10/16/17 CB
201700876301 | 2017-06-28 | LEAD/PLASTIC | 3015 | CHERRY | FIG | WMTLK | ML- METER LEAK METER#A355290 ACCT6#182566-705614 EXAMINE INLET AND OUT SERVICE FOR LEAK, METER BOX UNDER WATER AREA FLOODED 10/20/17 CUSTOMER STATES LEAK IS WORSE AND HAD TO SET PAVERS FOR TENANTS TO WALK ON (NLD) /** 1) MN: A336864 SN: 0082438, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT FIG, *MB: CODE: CDN1 LOC: ON CHERRY, 133' FROM P.L. FIG, 6' OUTSIDE,6' IN- ****/ | 2018-01-29 | EXCAVATED A 9 X 8 MUDPLOT UT TO REPAIR INLET SERVICE LEAK, REPLACED LEAD PIPE FROM CURB TO METER BOX AND RAISED METER BOX TO GRADE , BACKFILLED AND DRESSED JOB SITE JOB CONT - TO REPLACE LEAD FROM MAIN TO CURB
201700879701 | 2017-06-29 | LEAD | 910 | AUDUBON | BURTHE | WILK | ML METER LEAK ACCOUNT #151742703450 METER # A397993 INLET SERVICE LEAK BEHIND CURB COCK /** 1) MN: A224836 SN: 0086766, *TAP: SIZE: B LOC: 99 FEET FROM P LINE AT BURTHE, *MB: CODE: CD LOC: FIRST METER CURB ON AUDUBON 99FT FROM PL BURTHE ****/ DOTTIE CALLED : 9/19/17; READY 9/22/17; EXP. 10/12/17 | 2017-10-11 | ARRIVED ON JOB SITE FOR INLET SERVICE LEAK.EXAMINE JOB AND FOUND THE COCK WAS LEAKING,EXCAVATED IN MUDPLOT AND CHANGED METER COCK.
201700881601 | 2017-06-29 | LEAD | 6311 | MAGAZINE | CALHOUN | WILK | ML- METER LEAK METER#A251838 ACCT#119407-563182 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A289378 SN: 0032122, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT CALHOUN, *MB: CODE: CDLM LOC: ON MAGAZINE 78FT FROM CALHOUN ****/ DOTTIE READY 8-31-17 EXP 9-20-17 | 2017-09-13 | ARRIVED ON SITE FOUND LEAK ON 5/8 CURB COCK AND BROKEN HANDWHEEL REPLACED WITH NEW CURB COCK AND HAND WHEEL AFTER EXCAVATING IN MUDPLOT FOUND LEAD ON INLET SIDE AND PLASTIC ON OUTLET BACKFILLED 4 X 4 FT. MUDCUT.
201700887201 | 2017-07-01 | LEAD/PLASTIC | 4632 | PALMYRA |  | WILK | ML- METER LEAK METER#A239147 ACCT# 133460-536176 INLET SERVICE LEAK INSIDE METER BOX 11/10/17 CUSTOMER STATES LEAK GETTING WORSE (NLD) 2/1/18 LEAK HAS GOTTEN WORSE. PER S/R # 12830553 (PET) /** 1) MN: A239147 SN: 0064356, *TAP: SIZE: A LOC: 246 FEET FROM P LINE AT OLYMPIA N, *MB: CODE: AGKT LOC: ON PALMYRA 246FT FROM OLYMPIA ****/ | 2018-03-18 | EXCAVATED AND MADE REPAIRS ON A OUTLET SERVICE LEAK RENEWED THE OUTLET FROM THE METER BOX TO PROPERTY . LEAD ON THE INLET. JOB COMPLETE. JEG
201700890601 | 2017-09-08 | LEAD | 1035 | ARABELLA | COLISEUM | WILK | ML - METER LEAK MTR# A 424868 ACCT# 122041-564125 INLET SERVICE LEAK BEHIND CURB COCK 8/15/17 LEAK GETTING WORSE PER SR#12812065 (AJR) /** 1) MN: A292887 SN: 0039878, *TAP: SIZE: A LOC: 51 FEET FROM P LINE AT COLISEUM, *MB: CODE: CEL LOC: ON ARABELLA ST 51.3' FROM RPL COLISEUM ST 2' FROM ****/ DOTTIE READY 9-7-17 EXP 9-27-17 | 2017-09-07 | ARRIVED AT THE ABOVE LOCATION MADE A SIDEWALK CUT 3X2 OVER THE METER BOX & MADE REPAIR ON THE INLET LEAD LINE. THEN BACKFILLED AND CLEANED THE AREA. (NEED PAVING)...OLD METER A424868 FACTORY: 15511150 MAKE: HERSEY READ: 736
201700892904 | 2018-12-03 | LEAD | 2129 | GORDON | N MIRO | WOLK | LEAK CONTINUES AFTER PREVIOUS REPAIR. CONTRACTOR NEEDS THIS SITE REPAIRED TO COMPLETE RESTORATION. ***DO NOT CREATE RESTORATION WORK ORDER AFTER REPAIR.*** /** 1) MN: A327579 SN: 0128584, *TAP: SIZE: A LOC: 211 FEET FROM P LINE AT NO. GALVEZ, *MB: CODE: CDMN LOC: ON GORDON, 211' FROM P.L. NO. GALVEZ, 8' OUTSIDE ****/ | 2018-12-08 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIRS ON INLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201700906301 | 2017-07-06 | LEAD/PLASTIC | 509 | PARK BL | NUNEZ | WILK | WM - LEAK IN THE STREEET LOCATED BEHIND THE HOUSE ON LAWRENCE ST BY WALKING TRAIL INLET SERVICE LEAK IN GRASS BY DRIVEWAY ON LAWRENCE /** 1) MN: A186619 SN: 0078079, *TAP: SIZE: A LOC: 98 FEET FROM P LINE AT NUNEZ, *MB: CODE: CD LOC: RES ON LAWRENCE 97.5' FROM PL NUNEZ ****/ | 2017-10-26 | EXCAVATED METER BOX AND FOUND LEAK ON CURB COCK INSTALLED METER BOX COMPLETE
201700940801 | 2017-07-14 | LEAD | 3610 | TULANE AV | S GENOIS | WILK | MI LEAK IN THE STREET EXAMINE INLET SERVICE FOR LEAK @ SIDEWALK 08/22/17 LEAK GETTING WORSE (NLD) /** 1) MN: D003268 SN: 0020968, *TAP: SIZE: D LOC: 75 FEET FROM P LINE AT GENOIS S, *MB: CODE: CEKP LOC: ON TULANE 68FT PL S.GENOIS 5' INSIDE CURB ****/ DOTTIE READY 8-24-17 EXP 9-13-17 | 2017-09-14 | REPLACED 1 1/2 CURB COCK TIED INTO LEAD .
201700941004 | 2017-11-29 | LEAD | 2712 | MAGAZINE | WASHINGTON AV | WILK | REPAIR INLET SERIVCE /** 1) MN: A252847 SN: 0009502, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT FOURTH, *MB: CODE: ADLK LOC: 100' FROM URPL FOURTH ****/ | 2017-11-30 | REPLACED 24 FT. OF 1" TUBING TIED INTO LEAD INTO LEAD IN STREET AND 1" TUBING AT SIDEWALK. (SOC 8 FT. X 20 FT. ST.)UNABLE TO GET READING
201700949901 | 2017-07-17 | LEAD/PLASTIC | 253 | PINE | PRYTANIA | WILK | ML - METER LEAK MTR# A 012305 ACCT# 162427-586123 INLET SERVICE LEAK BEHIND CUCB COCK /** 1) MN: A012305 SN: 0101887, *TAP: SIZE: A LOC: 58 FEET FROM P LINE AT PRYTANIA, *MB: CODE: BD LOC: ON PINE, 56' FROM P.L. PRYTANIA, 7' OUTSIDE P.L. ****/ | 2017-09-11 | EXCAVATED A 4 X 4 CUT IN CONCRETE SIDEWALK THROUGH TREEROOTS OVER A 5/8 OUTLET SERVICE LEAK CHANGED THE HANDWHEEL AND REPLACED OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILLED AND DRESSUP WITH RIVERSAND AND COLDMILL LEAD ON INLET
201700955601 | 2017-07-18 | LEAD/PLASTIC | 1752 | SHIRLEY DR | COPERNICUS | WILK | ML- METER LEAK MN:A403167 ACCT#226184-405294 INLET SERVICE LEAK ON SIDEWALK IN DRIVEWAY /** 1) MN: A305928 SN: 0134007, *TAP: SIZE: C LOC: 357 FEET FROM P LINE AT COPERNICUS, *MB: CODE: AD25 LOC: ON SHIRLEY D 383.5' FROM PL COPERNICUS 6' OUTSIDE ****/ | 2017-11-21 | EXAMINED METER BOX PUMP DOWN WATER OBSERVED LEAK COMING FROM HANDWHEEL REPAIRED HANDWHEEL OBSERVED LEAKING STOPPED
201700960001 | 2017-07-18 | LEAD/PLASTIC | 6529 | GEN DIAZ | LANE | WILK | MI- LEAK IN STREET INLET SERVICE LEAK IN ASPHALT STREET 08/21/17 LEAK GETTING WORSE (NLD) 08/31/17 *****CUSTOMER OUT OF WATER****** 8PSI ON OUTSIDE FAUCET PER INSP. C KENT (NLD) /** 1) MN: B013835 SN: 0110245, *TAP: SIZE: B LOC: 217 FEET FROM P LINE AT LANE, *MB: CODE: BDLM LOC: 217FT FROM PL LANE 9' OUTSIDE PL 8' INSIDE CURB ****/ | 2017-08-31 | PUMPED WATER DOWN IN HOLE DUG BY EXCAVATOR AND EXPOSED LEAD LINE REMOVED LEAD LINE AND REPAIR LEAK ALSO PROPERLY BACK FILLED HOLE. CUSTOMER WATER WENT BACK TO NORMAL PRESSURE
201700960002 | 2017-08-31 | LEAD/PLASTIC | 6529 | GEN DIAZ | LANE | WILK | REFER TO THE ZONE TO REMOVE LEAD LINE FROM MAIN TO PROPERTY /** 1) MN: B013835 SN: 0110245, *TAP: SIZE: B LOC: 217 FEET FROM P LINE AT LANE, *MB: CODE: BDLM LOC: 217FT FROM PL LANE 9' OUTSIDE PL 8' INSIDE CURB ****/ | 2017-09-14 | EXCAVATED A 3 X 13 STREET CUT TO REMOVE LEAD INLET SERVICE JOB CONTINUED
201700963301 | 2017-07-19 | LEAD | 3728 | S GALVEZ | GEN TAYLOR | WMTLK | ML-- METER LEAK METR # A 391496 ACCT# 128915-572372 EXAMINE INLET AND OUTLET SERVICE FOR LEAK FOUND METER OFF LEFT OFF /** 1) MN: A186552 SN: 0069775, *TAP: SIZE: C LOC: 85 FEET FROM P LINE AT S GALVEZ ST, *MB: CODE: AGL LOC: ON S GALVEZ ST 52' FROM LRPL GENL TAYLOR ****/ DOTTIE READY 2-1-18 EXP EXP 2-21-18 | 2018-02-06 | EXAMINEE JOB AND PUMP WATER OUT OF METER BOX AND FOUND BAD METER COCK AND EXCAVATED IN 4 X4 MUDPLOT AND MADE REPAIRS ON BAD METER COCK AND TIED BACK ONTO LEAD LINE .BACKFILL JOB WITH RIVERSAND AND LEAD LINE AND ALSO THERE WAS NO METER IN BOX.
201700965801 | 2017-07-19 | LEAD | 1219 | ST FERDINAND | MARAIS | WILK | ML -- METER BOX LEAK INLET SERVICE LEAK IN STREET @ CURB GETTING OFF IN DCB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-09-11 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA (NO METER)
201700967301 | 2017-07-20 | LEAD/PLASTIC | 1872 | FARRAGUT | SHEPARD CT | WMBK | LOCATIONID#235031-404953 METER#A294923 METER CASING MISSING,PLEASE REPLACE /** 1) MN: A294923 SN: 0160919, *TAP: SIZE: B LOC: 44 FEET FROM P LINE AT SHEPARD, *MB: CODE: ADL3 LOC: ON FARRAGUT, 100' FROM P.L. SHEPARD, 6' OUTSIDE, ****/ | 2017-10-17 | EXAMINED AREA LOCATED METER CLEANED EXCAVATED METER AREA REPALCED METER TOP AND UPPER CASE
201700972101 | 2017-07-20 | LEAD | 4601 | CHEF MENTEUR HW | LOUISA | WMTLK | ML-- METER LEAK METER# E005729 ACCT# 176111-601978 *** CALL UPON ARRIVAL ****** EXAMINE INLET/OUTLET SERVICE FOR A LEAK ( CUSTOMER COMPLAINING OF HIGH WATER BILL) 01/12/18 PER S/R 12827073 METER LEAK (KSW) /** 1) MN: G002309 SN: 0999999, *TAP: SIZE: G LOC: 169 FEET FROM P LINE AT LOUISA, *MB: CODE: CD LOC: ON STEPHEN GIRARD SERVITUDE 169FT FROM LOUISA ** 2) MN: E005729 SN: 0119308, *TAP: SIZE: E LOC: 254 FEET FROM P LINE AT LOUISA, *MB: CODE: OOO LOC: IN SERVICE ALLEY BEHIND 4601 CHEF SERVES DOMESTIC THERE ARE 2 MORE NOT LISTED. ****/ | 2019-03-03 | MADE A 11X16 CUT ASPHALT PARKING LOT.EXCAVATED DOWN ON 6 INCH WATER MAIN AT 2 INCH TAP. FOUND LEAK COMING FROM COCK IN MANHOLE ALSO SERVICE WAS LEAD. MADE REPAIRS REPLACING COCK NIPPLE UNION AND SERVICE FROM MAIN TO METER. HAD TO EXCAVTED BY HAND BECAUSE OF UTILITIES.BACKFILLED.
201700977101 | 2017-07-21 | LEAD | 2710 | LASALLE | 4TH | WILK | MI- STREET LEAK INLET SERVICE LEAK IN ASPHALT STREET FLOODING STREET AND GUTTER BOTTOM 08/25/17 LEAK HAS GOTTEN WORSE. FLOODING AREA. (KSW) /** 1) MN: A323896 SN: 0000941, *TAP: SIZE: B LOC: 80 FEET FROM P LINE AT FOURTH UPL, *MB: CODE: CDL LOC: 80' FROM UPL FOURTH ****/ DOTTIE READY 9-6-17 EXP 9-26-17 | 2017-09-08 | EXCAVATED IN STREET FOUND INLET LEAD SERVICE LEAKING. MADE REPAIR ON SERVICE AND TIED BACK INTO LEAD SERVICE, 5/8 SERVICE...NO METER
201700978006 | 2018-05-20 | LEAD/PLASTIC | 630 | HUNTLEE DR | MACARTHUR BL | WILK | LEAK CONTINUES AFTER PREVIOUS REPAIR. WATER LEAK -INLET SERVICE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. ***RESTORATION WORK ORDER NOT NEEDED. DPW ALREADY HAS RESTORATION.*** /** 1) MN: A123730 SN: 0115276, *TAP: SIZE: A LOC: 183 FEET FROM P LINE AT MAC ARTHUR BLVD, *MB: CODE: CFL LOC: ON HUNTLEE 183' FRO M PL MAC ARTHUR BLVD 6'OUTSIDE ****/ | 2018-07-05 | ARRIVED ON JOB SITE EXAMAINE LEAK IN SIDEWALK BROKE CONCRETE EXCVATED IN MUD PLOT BY HAND MADE REPAIRS ON SERVICE SERVICE WAS AT HOUSE 629 HUNLEE DR BACKFILLED DRESS UP WORK SITE HOUSE HAD NO METER (JOB COMPLETE)
201700992001 | 2017-07-25 | LEAD | 4863 | MONTEGUT | STEPHEN GIRARD AV | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK IN MUD PLOT ALSO CHANGE 5/8 METER DEFECTIVE, NO REGISTRATION /** 1) MN: A264712 SN: 0112161, *TAP: SIZE: A LOC: 1143 FEET FROM P LINE AT STEPHEN GIRARD AVE, *MB: CODE: BFL LOC: 143FT FROM PL STEPHEN GIRARD 6' OUTSIDE PL 7' INSI ****/ | 2017-09-01 | EXAMINE LOCATION FOUND INLET SERVICE LEAKING OUTSIDE OF METER BOX. EXCAVATED DOWN ON INLET AND AOUTLET SERVICES. FOUND PLASTIC TUBING ON OUTLET & LEAD ON INLET. MADE REPAIRS BY REPLACEING COCK , WASHERS & 2FT OF INLET SERIVCE ALSO WATER METER. BACKFILLED DRESS UP OLD METER A408806 FACTORY 14114568 MAKE HERSEY READ 59
201700998604 | 2018-02-07 | LEAD/PLASTIC | 1121 | L B LANDRY AV | DIANA | WMTLK | METER LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-02-07 | EXAMINED METER FOUND LEAK ON INLET REPLACED WASHER ON METER STOPPED WATER FROM LEAKING
201701001901 | 2017-07-26 | LEAD/PLASTIC | 1417 | SOCRATES | LEBOUEF | WILK | MI-LEAK IN GRASSY AREA INLET SERVICE LEAK IN GRASS FLOODING CURB AND STREET /** 1) MN: A253237 SN: 0091053, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT LEBOEUF, *MB: CODE: BDKL LOC: ON SOCRATES 110' FROM PLLEBOEUF ****/ | 2017-11-21 | EXCAVATED METER BOX EXPOSED INLET AND OUTLET OBSERVED LEAK ON BOX COCK REPAIRED AND REPLACED BROKEN HANDWHEEL OBSERVED LEAK ON PLASTIC INLET SERVICE LINE BACKFILLED DRESS UP WITH SAND NEEDED
201701003901 | 2017-07-26 | LEAD/PLASTIC | 1353 | CRESCENT DR | CARTIER AV | WILK | ML METER LEAK ACCT#172909-578687 METER# C034579 INLET SERVICE LEAK I NMUDPLOT 09/07/11 LEAK HAS GOTTEN WORSE CAUSING AREA TO FLOOD PER SERVICE REQUEST #12814214 (FCP) /** 1) MN: C007152 SN: 0116161, *TAP: SIZE: C LOC: 122 FEET FROM P LINE AT CARTIER AVE, *MB: CODE: ADLM LOC: ON CRESCENT 122FT PL CARTIER AV 8' OUTSIDE 10' ****/ | 2017-10-22 | EXCAVATED AND MADE REPAIRS ON A 1 INCH INLET SERVICE LEAK LEAD ON THE INLET PLASTIC ON THE OUTLET JOB COMPLETE JEG
201701004503 | 2017-11-03 | LEAD/PLASTIC | 818 | BROOKLYN | SLIDELL | WMBK | EXCAVATED AND WASN,T ABLE TO LOCATE METER HABE TO COMEBACK AND FINISH WE BACKFILL AND CLEAN UP JOB SITE /** 1) MN: A313961 SN: 0033920, *TAP: SIZE: A LOC: 138 FEET FROM P LINE AT SLIDELL, *MB: CODE: AFN LOC: ON BROOKLYN AVE., 138' FROM L.P.L. SLIDELL ****/ | 2017-11-29 | EXCAVATED AND LOCATED WATER METER BOX THEN WE BACKFILL AND CLEAN UP JOB SITE
201701015301 | 2017-07-28 | LEAD/PLASTIC | 4418 | FIESTA | COMET | WILK | WM - LEAK AT THE CURB INLET SERVICE LEAK BETWEEN CURB AND STREET /** 1) MN: A291668 SN: 0133614, *TAP: SIZE: B LOC: 193 FEET FROM P LINE AT COMET, *MB: CODE: BDK LOC: ON FIESTA DR., 193' FROM P.L. COMET, 7' OUTSIDE, ****/ | 2017-11-06 | BROKE THE STREET AND EXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOB SITE
201701016501 | 2017-07-28 | LEAD/PLASTIC | 601 | CONRAD |  | WMTLK | MI- LEAK AT THE SIDEWALK EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: C026797 SN: 0115851, *TAP: SIZE: C LOC: 15 FEET FROM P LINE AT CONRAD, *MB: CODE: BDH5 LOC: ON LOUIS 14TH 15' FROM PL CONRAD 10' OUTSIDE PL 6' ****/ | 2018-07-05 | EXCAVATED IN MUDPLOT LOCATED LEAK ON 1' ABANDON SERVICE MADE REPAIRS ON 1' INLET SERVICE INLET HAS LEAD BACK FILLED DRESSED JOB WITH RIVERSAND NO METER.
201701032001 | 2017-08-01 | LEAD | 3810 | GENTILLY BL | BACCICH | WILK | ML - METER LEAK MTR # A278956 ACCT # 133084 - 478838 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A278956 SN: 0086058, *TAP: SIZE: A LOC: 159 FEET FROM P LINE AT LOTUS, *MB: CODE: AFR2 LOC: ON GETNILLY 174FT FROM PL LOTUS 12FT OUTSD PL ****/ | 2017-12-18 | FOUND LINK ON LEAD LINE OUTSIDE MADE REPAIRS ON OUTLET AND RESTORE WATER LJF
201701032401 | 2017-08-01 | LEAD/PLASTIC | 2245 | BECK | PRANCER | WILK | WM - LEAK IN THE STREET EXAMINE LEAK ON MAIN IN CONCRETE STREET **CHANGED FROM 2200BLK BECK** /** 1) MN: A308680 SN: 0136401, *TAP: SIZE: B LOC: 106 FEET FROM P LINE AT PRANCER, *MB: CODE: CD LOC: ON BECK 106' FROM PL PRANCER 7' OUTSIDE PL 3' INSI ****/ | 2018-04-30 | ARRIVED ON JOB SITE FOUND LEAK IN THE STREET USE MACHINE WITH BREAKER TO BRAEK UP STREET EXCAVATED WITH MACHINE FOUND LEAK ON SERVICE LINE INLET PLASTIC AND REPAIRED AND BACKFILLED WITH RIVER SAND AND COAL MILL
201701033001 | 2017-08-02 | LEAD | 5204 | ANNUNCIATION | DUFOSSAT | WMTLK | LOCATIONID#119305-560030 METER#A210473 METERBOX OVERFLOWING 08/25/17 CUSTOMER STATES WATER LEAK FROM METER IS CAUSING DAMAGE TO FOUNDATION OF HOME. (KSW) /** 1) MN: A210473 SN: 0030992, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT ANNUNCIATION, *MB: CODE: AFH LOC: METER ON DUFFOSAT THIRD METER BOX FROM ANNUNCIAT- ****/ DOTTIE READY 8-25-17 EXP 9-14-17 | 2017-08-31 | REPLACED 5/8 CURB COCK TIED INTO LEAD
201701034801 | 2017-08-02 | LEAD | 4737 | NIGHTHART | PRENTISS AV | WILK | ML- METER LEAK AT METER# A322334 ACCT# 175503-499727 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A309886 SN: 0119511, *TAP: SIZE: C LOC: 319 FEET FROM P LINE AT PRENTISS AVE, *MB: CODE: ADK2 LOC: ON NIGHTHART, 311' FROM P.L. PRENTISS AVE., 9' OUT ****/ | 2017-09-19 | EXCAVATED IN A 4X4 MUD PLOT CUT OVER 5/8 METER BOX. FOUND INLET SERVICE LEAD LINE LEAKING AND BOX BROKEN. RENEW WITH 5/8 STOP COCK WITH 4 FT OF WATER TUBING WITH A METER BOX COMPLETE. RAISE METER BOX TO GRADE, BACKFILL AND DRESS. JOB COMPLETE.
201701037201 | 2017-08-02 | LEAD | 1902 | FORSTALL | N PRIEUR | WMRE | **********PICK UP********** LOCATE & CLOSE SERVICE INLET SERVICE LEAK INTERFERING WITH CONTRACTORS WORK METER LOCATED ON N PRIEUR IN 5000BLK OF N PRIEUR /** 1) MN: A334046 SN: 0132512, *TAP: SIZE: A LOC: 36 FEET FROM P LINE AT FORSTALL, *MB: CODE: ADH LOC: ON NO. PRIEUR, 36' FROM P.L. FORSTALL, 7' OUTSIDE ****/ | 2017-08-31 | EXCAVATED 4 X 6 MUD PLOT FOPUND LEAK ON 3/4 INCH ABANDON INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201701043401 | 2017-08-03 | LEAD/PLASTIC | 102 | CAMBRIDGE CT | WOODLAND HW | WILK | ML- METER LEAK MTR # A-389099 INLET SERVICE LEAK CAUSING METER BOX TO OVERFLOW /** 1) MN: A319933 SN: 0124613, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT WOODLAND HWY, *MB: CODE: CGM2 LOC: ON CAMBRIDGE CT 134' FROM PL WOODLAND HWY 2' OUTSI ****/ | 2017-09-04 | EXCAVATED INLET AND OUTLET FOUND LEAD ON OUTLET AND LEAK ON BOX COCK SO WE REPLACED LEAD WITH PLASTIC AND INSTALLED A METER BOX COMPLETE BACKFILLED WITH RIVER SAND
201701052401 | 2017-08-07 | LEAD/PLASTIC | 2224 | ST THOMAS | JACKSON AV | WOLK | WM LEAK ON THE SIDEWALK OUTLET SERVICE LEAK BEHIND HANDWHEEL /** 1) MN: A295740 SN: 0052791, *TAP: SIZE: A LOC: 217 FEET FROM P LINE AT JACKSON AVE, *MB: CODE: BDLM LOC: ON ST. THOMAS, 217'FROM P.L. JACKSON AVE.,7' OUT- ****/ | 2017-10-09 | BROKE SIDEWALK WITH SLEDGE HAMMER AND EXCAVATED WATER CHANGED BOX COCK TO REPAIR LEAK LEAD INLET
201701056201 | 2017-08-07 | LEAD | 1730 | BIENVILLE | N DERBIGNY | WILK | ML- METER LEAK METER#A376084 ACCT#221362-522640 INLET SERVICE LEAK IN MUDPLOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-01-07 | REPLACED 5/8 INCH HANDWHEEL + GUTS AT ABOVE LOCATION
201701060601 | 2017-08-08 | LEAD/PLASTIC | 6123 | CARLISLE CT | WESTCHESTER PL | WMRE | MI- PLEASE RAISE AND LOCATE METER MTR.# B-034785 ACCT # 228024-418321 /** 1) MN: B020798 SN: 0119131, *TAP: SIZE: B LOC: 643 FEET FROM P LINE AT WESTCHESTER, *MB: CODE: CDLM LOC: ON CARLISLE 46FT FROM DIV P/L WOODLAND ****/ | 2017-09-04 | EXCAVATED IN TREE ROOTS AND RAISE METER BOX TO GRADE RENEW 5/8 OUTLET SERVICE CHANGED LEAD LINE MADE 4X4 AND 2X4 MUD CUT **************OLD METER INFO********** MTR:B034785 FAC:70698464 MAKE:SENSUS READ:50483
201701070801 | 2017-08-09 | LEAD | 1135 | HENRY CLAY AV | COLISEUM | WILK | ML- METER LEAK METER# A306668 ACCT# 102283-563000 EXAMINE INLET SERVICE FOR LEAK 08/21/17 ****1ST AM**** PER BOURNES LEAK HAS GOTTEN WORSE ALSO CUSTOMER HEAR NOISE IN PIPES /** 1) MN: A306668 SN: 0001390, *TAP: SIZE: B LOC: 33 FEET FROM P LINE AT HENRY CLAY AVE LRPL, *MB: CODE: AGHT LOC: 33'FROM LRPL HENRY CLAY AVE. ****/ DOTTIE READY 9-21-17 EXP 10-11-17 | 2017-09-20 | REPLACED 5/8 CURB COCK TIED INTO LEAD.....CREW FOUND METER AT #A306668 AT ABOVE LOCATION
201701074601 | 2017-08-10 | LEAD/PLASTIC | 615 | GEN TAYLOR | ANNUNCIATION | WILK | WM SIDEWALK LEAK **********1ST AM********** CHANGE FROM 619 GEN TAYLOR INLET SRV LEAK IN S/W BUBBLING UP A LITTLE, FLDG IN FRONT OF BOTH ADDRESSES 615-19 GEN TAYLOR 08/20/17 LEAK GETTING WORSE IN S/W PRE S/R# 12811754 (NLD) 08/27/17 LK IN S/W GETTING WORSE PER S/ R #12813297 (FCP) 10/31/17 PER INSP L HEBERT UPGRD TO *****( B 1ST AM )***** INLET SERVICE LEAK ON S/W FLDING AREA BLOCKING ACCESS TO CUSTOMER HOUSE (KSW) /** 1) MN: A261149 SN: 0004323, *TAP: SIZE: B LOC: 111 FEET FROM P LINE AT ANNUNCIATION, *MB: CODE: BFLO LOC: ON GEN TAYLOR,111' FROM U.S.P.L. ANNUNCIATION ****/ | 2017-11-01 | ARRIVED ON JOB EXCAVATED IN SIDEWALK FOUND LEAD SERVICE LEAKING MADE REPAIRS AND BACKFILLED JOB COMPLETE. SOC 5 FT. X 3 FT. S/W
201701074901 | 2017-08-10 | LEAD/PLASTIC | 1137 | L B LANDRY AV | DIANA | WMTLK | ML-METER LEAK ACCT#225467-403746 METER#A352898 EXAMINE INLET AND OUTLET SERVICE FOR LEAK, METER BOX OVERFLOWING FLOODING CURB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-09-07 | EXCAVATED METER BOX AND FOUND THAT THE METER BOX BOTTOM WAS BROKEN REPLACED WITH METER BOX COMPLETE
201701077001 | 2017-08-11 | LEAD | 1133 | DECATUR | GOV NICHOLLS | WMTLK | LOCATIONID#106889-483348 METER#A333600 METERBOX OVERFLOWING /** 1) MN: A333600 SN: 0024052, *TAP: SIZE: A LOC: 60 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: CEN1 LOC: 60FT FROM USPL GOV NICHOLLS ****/ | 2017-08-28 | EXCAVATED IN BRICK SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201701078201 | 2017-08-11 | LEAD | 1015 | ESPLANADE AV | N RAMPART | WILK | MI- LEAK AT THE SIDEWALK INLET SERVICE LEAK IN MUDPLOT NEAR METER /** 1) MN: B025781 SN: 0056467, *TAP: SIZE: B LOC: 126 FEET FROM P LINE AT BURGUNDY, *MB: CODE: ADT LOC: 126FT FROM LSPL BURGUNDY ****/ | 2017-08-30 | EXCAVATED 3 X 2 BRICK SIDEWALK MADE REPAIR ON INLET SERVICE TO STOP LEAK BACKFILLED AND CLEANED THE AREA LEFT BRICK STACKED UP AGAINT BUILDING
201701079301 | 2017-08-11 | LEAD/PLASTIC | 6230 | STRATFORD PL |  | WILK | ML- METER LEAK ACCT#228958-705200 METER#B041807 INLET SERVICE LEAK ON SIDEWALK FLOODING TREEROOTS /** 1) MN: B014403 SN: 0125342, *TAP: SIZE: B LOC: 227 FEET FROM P LINE AT AURORA DR, *MB: CODE: CD LOC: ON STRATFORD PL., 228' FROM P.L. AURORA DR., 7' ****/ | 2017-11-29 | CHOPPED TREE ROOTS AND EXCAVATED BY HAND FOUND LEAK ON BOX COCK REPLACED COCK AND BACKFILL
201701081301 | 2017-08-11 | LEAD | 1710-12 | AUBRY | OLD PRIEUR | WMTLK | MI-LEAK BETWEEN CURB AND SIDEWALK. EXAMINE INLET/OUTLET SERVICE FOR LEAK METER UNDER WATER /** AT 1710: 1) MN: A316792 SN: 0080704, *TAP: SIZE: B LOC: 130 FEET FROM P LINE AT OLD ROMAN, *MB: CODE: CDL1 LOC: 130FT FROM PL OLD ROMAN ****/ | 2017-09-01 | EXCAVATED IN GUTTER BOTTOM AND MADE REPAIR ON 3/4 INLET SERVICE REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA
201701089101 | 2017-08-14 | LEAD | 5012 | LOUISA DR | DREUX AV | WILK | *******PICKUP JOB******** INLET SERVICE LEAK AT CURB /** 1) MN: A266067 SN: 0112404, *TAP: SIZE: A LOC: 759 FEET FROM P LINE AT MIRABEAU AVE, *MB: CODE: CDLM LOC: 759FT FROM MIRABEAU AVE 7' OUTSIDE PL 5' INSIDE CU ****/ | 2017-08-31 | EXAMINE LOCATION FOUND COCK LEAKING & UPPER CASING WAS MISSING. EXCAVATED DOWN ON INLET SERVICE. FOUND LEAD ON SERVICE. MADE REPAIRS BY REPLACING WASHER'S, COCK, UPPER CASING. BACKFILLED DRESS UP.
201701090401 | 2017-08-15 | LEAD/PLASTIC | 1414 | NUMA |  | WOLK | INLET IS A 5/8 AND OUTLET IS A 3/4. REPAIR AND SET A 3/4 METER LOCATION 226310 OUTLET NEED TO BE REDUCE TO A 5/8, NO METER IN BOX *****RENOVATED PROPERTY***** /** 1) MN: B031299 SN: 0125166, *TAP: SIZE: B LOC: 79 FEET FROM P LINE AT SOCRATES, *MB: CODE: BDM1 LOC: ON NUMA 79' FROM PL SOCRATES 5' OUTSIDE PL ****/ | 2017-09-28 | REPLACED 3/4 METER BOX WITH 5/8 METER BOX AND INSTALLED NEW METER
201701091201 | 2017-08-15 | LEAD/PLASTIC | 1024 | LEONIDAS | ZIMPEL | WILK | ML - METER LEAK MTR# A 269855 ACCT# 153009-587664 BAD BLEEDER VALVE /** 1) MN: A269855 SN: 0079592, *TAP: SIZE: A LOC: 172 FEET FROM P LINE AT FRERET, *MB: CODE: BDLN LOC: 193FT FROM PL FRERET 12FT FROM LPL CURB ****/ | 2017-10-15 | EXCAVATED IN TREE ROOTS AND MADE REPAIRS ON A 5/8 INLET SERVICE LEAK. LEAD LINE. OUTLET PLASTIC. JOB COMPLETE JEG
201701094601 | 2017-08-16 | LEAD | 120 | S JEFFERSON DAVIS PK | EUPHROSINE | WMTLK | LOCATIONID#110506-533667 METER#A140136 LEAK INSIDE METERBOX, /** 1) MN: A140136 SN: 0011627, *TAP: SIZE: A LOC: 139 FEET FROM P LINE AT CLEVELAND AVE, *MB: CODE: CF LOC: CLEVELAND 139FT FROM IRPL ****/ | 2017-08-31 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 CURB COCK BACKFILLED + DRESSED UP AREA
201701094701 | 2017-08-16 | LEAD/PLASTIC | 1080 | FARRAGUT | DE ARMAS | WMTLK | LOCATIONID#225429-404614 METER#A394479 AREA FLOODED METERBOX OVERFLOWING /** 1) MN: A312787 SN: 0135103, *TAP: SIZE: B LOC: 122 FEET FROM P LINE AT DE ARMAS, *MB: CODE: ADK2 LOC: ON FARRAGUT, 122' FROM P.L. DE ARMAS, 6' OUTSIDE ****/ | 2017-09-06 | HAD TO LOCATE METER TO EXAMINE FOUND BOX IN MUD PLOT CHECKED METER AND IT WAS LOOSE
201701095101 | 2017-08-16 | LEAD/PLASTIC | 1800 | NUMA | MAGELLAN | WMTLK | LOCATIONID#238622-702175 METER#A345913 LEAK INSIDE METERBOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-09-15 | EXCAVATED ON THE INLET AND OUTLET SERVICE AND RAISE METERBOX TO GRADE THEN WE BACKFILL AND CLEAN UP JOB SITE
201701095201 | 2017-08-16 | LEAD/PLASTIC | 1520 | SHIRLEY DR | LAWRENCE ST | WMTLK | LOCATIONID#226110-402136 METER#A423932 LEAK INSIDE METERBOX /** 1) MN: A329735 SN: 0129793, *TAP: SIZE: B LOC: 209 FEET FROM P LINE AT LAWRENCE, *MB: CODE: AE25 LOC: 22FT FROM P.L. LAWRENCE ****/ | 2017-10-06 | ARRIVED ON JOB SITE EXAMINED METER BROKE UP DRIVE WAY AROUND METER BOX EXCAVATED BY HAND FOUND LEAK ON INLET AND REPAIRED
201701096701 | 2017-08-16 | LEAD/PLASTIC | 2001 | BODENGER BL | MAGELLAN | WILK | MI- METER LEAK ACCOUNT #226472 METER #A355842 INLET SERVICE LEAK CAUSING METER BOX TO OVERFLOW /** 1) MN: A307004 SN: 0101854, *TAP: SIZE: A LOC: 387 FEET FROM P LINE AT MAGELLAN, *MB: CODE: AF LOC: ON BODENGER BLVD., 387' FROM P.L. MAGELLAN, 5.5' ****/ | 2017-11-06 | EXCAVATED METER OBSERVED LEAK ON METER COMING FROM INLET SERVICE BOX COCK REPLACED THEN RAISED METER TO GRADE
201701096802 | 2017-10-24 | LEAD/PLASTIC | 1104-06 | SUMNER | DIANA | WILK | /** AT 1104: 1) MN: A197750 SN: 0089455, *TAP: SIZE: A LOC: 53 FEET FROM P LINE AT DIANA, *MB: CODE: CD LOC: ON SUMNER 52FT FROM DIANA ****/ | 2017-10-24 | REPAIR JOB HAVE TO COMBACK AND CLEAN UP AND BACKFILL JOB SITE SO WE LEFT BARRELS AROUND JOB SITE....JOB CONTINUED
201701100601 | 2017-08-17 | LEAD | 4994 | MONTEGUT | MIRABEAU AV | WOLK | ML- METER LEAK ACCT# 169123-468897 METER# A273487 OUTLET SERVICE LEAK @ SIDEWALK FLOODING SIDEWALK CON REG /** 1) MN: A273487 SN: 0111399, *TAP: SIZE: A LOC: 707 FEET FROM P LINE AT MIRABEAU AVE, *MB: CODE: CDL LOC: 707FT PL MIRABEAU AV 6' OUTSIDE 7' INSIDE CURB ****/ | 2017-09-08 | EXAMINED FOUND OUTLET LEAKING. METER BOX BOTTOM WAS BROKEN. EXCAVATED ON INLET AND OUTLET SERVICE, FOUND LEAD, MADE REPAIRS BY REPLACING COCK, WASHERS, HANDWHEEL AND OUTLET FOR METER TO PROPERTY. REPLACED BOTTOM. BACKFILLED DRESSED UP.
201701101001 | 2017-08-17 | LEAD/PLASTIC | 1134 | MELPOMENE |  | WMEX | LOCATIONID#119694-537045 METER#A422093 LEAK INSIDE METERBOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-11-17 | BROKE CONCRETE AND EXCAVATED ON METER BOX FOUND LEAK INSIDE THE BOX MADE REPAIR NEED RETURN TO BACKFILLED ALSO HAD TO CHANGE METER,,,JOB CONTINUED OLD METER: A392880 FACT:749798 MAKE:SENSUS READ:11549
201701103401 | 2017-08-17 | LEAD/PLASTIC | 8201 | JEANNETTE | DUBLIN | WMTLK | ML - METER LEAK MTR# A 211437 ACCT# 123278-589369 METER LOCATED ON DUBLIN EXAMINE INLET AND OUTLET SERVICE FOR LEAK METR BOX UNDER WATER GRASSY AREA FLOODED /** 1) MN: A211437 SN: 0042764, *TAP: SIZE: A LOC: 40 FEET FROM P LINE AT JEANNETTE, *MB: CODE: CDHL LOC: SIDE GUTTER ON DUBLIN 42' P.L. JEABBETTE ****/ | 2017-11-14 | EXCAVATED IN TREE ROOTS AND MADE REPAIRS ON A 5/8 INLET SERVICE LEAK. LEAD LINE ALSO RENEWED THE OUTLET AND RAISED THE METER TO GRADE. PLASTIC ON THE OUTLET JOB COMPLETE JEG
201701104104 | 2017-10-30 | LEAD | 4233 | ST CLAUDE AV | LESSEPS | PSCO | S/W CON 5 X4 S/W CON 2 X4 /** 1) MN: SN: 0105738, *TAP: SIZE: B LOC: 48 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: BEH LOC: ON LESSEPS 48FT PL ST CLAUDE AV 8' OUTSIDE ****/ | 2017-11-15 | EXCAVATED IN EXPOSED SIDEWALK RAISED METER BOX TO GRADE.
201701106901 | 2017-08-18 | LEAD/PLASTIC | 2061 | LAURADALE DR |  | WMTBG | METER BELOW GRADE, PLEASE SET 5/8 METER LOCATION 229650 METER BELOW GRADE, ALSO SET 5/8 METER /** 1) MN: A133490 SN: 0131151, *TAP: SIZE: B LOC: 21 FEET FROM P LINE AT LAURADALE DR, *MB: CODE: BDH LOC: ON RUCK, 21' FROM P.L. LAURADALE DR., 7' OUTSIDE, ****/ | 2017-09-15 | RAISED METER BOX TO GRADE AND MADE SURE NOTHING WAS LEAKING SET NEW METER
201701107801 | 2017-08-18 | LEAD/PLASTIC | 1120 | SOUTHLAWN BL | DIANA | WMTLK | LOCATIONID#227241-406161 METER#A149000 METERBOX OVERFLOWING /** 1) MN: A149000 SN: 0122278, *TAP: SIZE: A LOC: 461 FEET FROM P LINE AT DIANA, *MB: CODE: CD LOC: ON SOUTHLAWN BLVD 461' FROM PL DIANA 6' OUTSIDE PL ****/ | 2017-10-09 | EXCAVATED METER BOX AND FOUND LEAK ON INLET SERVICE REPLACED BOX COCK AND CHANGED WASHERS ALL PLASTIC
201701109401 | 2017-08-18 | LEAD/PLASTIC | 8827 | FIG |  | WOLK | ML METER LEAK ACCOUNT #157403593261 METER #A398323 OUTLET SERVICE LEAK BEHIND HANDWHEEL FLOODING GRASSY AREA 10/27/17 LEAK GETTING WORSE PER SR#12819174 (AJR) /** 1) MN: A308801 SN: 0094771, *TAP: SIZE: A LOC: 24 FEET FROM P LINE AT FIG, *MB: CODE: BFHK LOC: ON GEN OGDEN 23FT FROM PL FIG 2' OUTSIDE PL 8' IN ****/ | 2017-12-21 | EXCAVATED A 4 X 4 CUT CONCRETE SIDEWALK OVER A 5/8 INLET SERVICE LEAK LEAD INLET AND PLASTIC OUTLET CHANGED THE COCK AND REPLACED 10 FT OF LEAD WITH 3/4 PVC PIPE FROM THE CURB TO THE METER BOX AND RAISE UP TO GRADE BACKFILLED WITH RIVERSAND AND COLD MILL. JOB COMPLETED JEG
201701109602 | 2017-09-01 | LEAD | 1936 | LAPEYROUSE |  | WILK | EXCAVATED IN MUD PLOT AT MERSURE GIVEN AND FOUND DRY INLET SET METER CASING AND BOTTOM LEFT 3/4 PLASTIC WHIP TO PROPERTY JOB REFER BACK TO ZONE 4 TO RUN FROM MAIN BACKFILLED AREA DUMPSTER ON SITE 874-3771 /** 1) MN: 000000 SN: 0045388, *TAP: SIZE: B LOC: 51 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: BE LOC: 1ST METER SIDE ST ON N JOHNSON 50' P.L. LAPEYROUSE ****/ | 2017-09-12 | EXCAVATED IN GUTTER BOTTOM AT ABOVE LOCATION FOUND INLET WITH WATER ON IT RAN NEW INLET FROM GUTTER BOTTOM TO METER RESTORED WATER TO ABOVE LOCATION BACKFILLED + DRESSED UP AREA
201701109801 | 2017-08-18 | LEAD | 5407 | DAUPHINE | ANDRY | WILK | MI LEAK IN EMPTY METER BOX FOR SPRINKLER SYSTEM 1" CONNECTION NOT HOUSE METER CALL UPON ARRIVEL 908-5637 G METER PASSING WATER IN THE OFF POSITION. CUSTOMER STATED METER WAS TO BE REMOVED ALSO METER LOCATED ON DAUPHINE, *****HOUSE UNDER RENOVATIONS***** /** 1) MN: A259122 SN: 0048571, *TAP: SIZE: D LOC: 84 FEET FROM P LINE AT ANDRY, *MB: CODE: AEI LOC: ON BURGUNDY,84' FROM P.L. ANDRY ** 2) MN: C007833 SN: 0048571, *TAP: SIZE: G LOC: 133 FEET FROM P LINE AT ANDRY, *MB: CODE: BEQ LOC: ON DAUPHINE 126.6' FROM PL ANDRY 4' OUTSIDE PL 5.5 ****/ | 2017-08-28 | EXCAVATED IN EXISTING 2 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK WITH NEW ONE BACK FILLED AREA
201701110501 | 2017-08-18 | LEAD | 1225 | INDEPENDENCE | URQUHART | WMTLK | ML- METER LEAK ACCT. 112984 -486254 METER # A217088 EXAMINE INLET & OUTLET SERVICE FOR A LEAK AREA FLOODED /** 1) MN: A217088 SN: 0015962, *TAP: SIZE: B LOC: 205 FEET FROM P LINE AT MARAIS, *MB: CODE: ADLM LOC: ON INDEPENDENCE 135' FROM PL URQUHART ****/ | 2017-09-20 | REPLACED 5/8 HANDWHEEL + GUTS IN METER BOX
201701110901 | 2017-08-18 | LEAD/PLASTIC | 6001 | MILNE BL | POLK | WILK | WM - LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET **CHANGED FROM 6000BLK MILNE BL** /** 1) MN: A224106 SN: 0087142, *TAP: SIZE: B LOC: 26 FEET FROM P LINE AT POLK AVE, *MB: CODE: AEK LOC: ON MILNE 25.5 FT FROM PL POLK AVE ****/ | 2017-10-04 | EXCAVATED A 10 X 10 ASPHALT CUT IN THE STREET TO REPAIR INLET SERVICE LEAK. BACKFILLED AND CLEANED UP JOBSITE REPAIRED CONTROLLING LINE IN THE STREET FOUND PVC/LEAD PIPE ON INLET SERVICE. JEG
201701115301 | 2017-08-21 | LEAD | 2715 | N RAMPART | PORT | WILK | MI-METER BOX LEAKING INLET SERVICE LEAK IN BOX /** 1) MN: A293795 SN: 0049971, *TAP: SIZE: A LOC: 89 FEET FROM P LINE AT PORT, *MB: CODE: AE LOC: ON N RAMPART 88FT FORM PL OF PORT ****/ | 2017-09-07 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201701115501 | 2017-08-21 | LEAD | 949 | WILSON DR | DELGADO DR | WILK | ML - METER LEAK MTR# A 296643 ACCT# 141395-514246 INLE SERVICE LEAK IN MUDPLOT NEAR METER BOX IN LARGE TREE ROOTS /** 1) MN: A296643 SN: 0072292, *TAP: SIZE: B LOC: 380 FEET FROM P LINE AT DUMAINE, *MB: CODE: BDK7 LOC: ON WILSON 380FT FROM DUMAINE ****/ | 2017-09-08 | EXCAVATED IN TREE ROOTS AND MUD PLOT AND MADE REPAIR ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201701116901 | 2017-08-21 | LEAD | 2519 | ELDER | CLEMATIS | WMTLK | ML - METER LEAK MTR# A 314036 ACCT# 151587-476033 EXAMINE INLET & OUTLET SERVICE FOR A LEAK FLOODING SIDEWALK & DRIVEWAY METER BOX UNDER WATER /** 1) MN: A215952 SN: 0085886, *TAP: SIZE: B LOC: 137 FEET FROM P LINE AT CLEMATIS, *MB: CODE: ADM LOC: OPP 2516 ON ELDER 137FT FROM PL CLEMATIS ****/ | 2017-09-23 | DUG IN MUDPLOT BY SHOVEL ABOUT 5FT UNTIL WE DISCOVERED LEAK ON LEAD LINE. WE THE REMOVED LEAD AND REPAIRED LINE AND BACKFILLED BY BACKHOE. LJF
201701117101 | 2017-08-21 | LEAD | 4105 | JUMONVILLE | SENATE | WOLK | MI LEAK IN STREET CHANGED FROM 4101 JUMONVILLE OUTLET SERVICE LEAK WITH CONSTANT REGISTRATION FLOODING SIDEWALK /** 1) MN: A253085 SN: 0127986, *TAP: SIZE: B LOC: 38 FEET FROM P LINE AT SENATE, *MB: CODE: BDK2 LOC: ON JUMONVILLE 38FT FROM PL SENATE 7' OUTSIDE PL ****/ | 2017-09-29 | EXCAVATED IN MUDPLOT BEHIND 5/8 METERBOX MADE REPAIRS ON OUTLET SERVICE. CLEANED AND DRESSED UP AREA, FOUND LEAD ON OUTLET SERVICE. JEG
201701117402 | 2017-09-05 | LEAD | N/A | N DERBIGNY | LOUISA | WMLK | EXCAVATED IN ASPHALT STREET OVER 12 INCH WATER MAIN FOUND JOINT LEAKING ON WATER MAIN UNABLE TO COMPLETE REFER BACK TO ZONE 4 FOR REPAIR LEFT JOB SAFE WITH BOARDS + BARRELLS /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-09-06 | EXCAVATED AND MADE ADDITIONAL 2 X 2STREET CUT AND CORKED A JOINT ON 12 INCH WATER MAIN BACKFILLED AREA
201701118401 | 2017-08-21 | LEAD | 940 | CANAL | BURGUNDY | WILK | ML METER LEAK ACCOUNT #163259711239 METER #C036157 INLET SERVICE LEAKING FROM BLEEDER VALVE FOUND OFF LEFT OFF /** 1) MN: C024608 SN: 0002188, *TAP: SIZE: C LOC: 20 FEET FROM P LINE AT CANAL, *MB: CODE: BDH3 LOC: ON UNIVERSITY PLACE 21' FROM PL CANAL 10' OUTSIDE ** 2) MN: D005342 SN: 0002188, *TAP: SIZE: D LOC: 59 FEET FROM P LINE AT CANAL, *MB: CODE: BHR6 LOC: ON UNIVERSITY PL 59FT FR PL CANAL ****/ | 2017-08-28 | EXCAVATED IN BRICK SIDEWALK REPLACED 1 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201701118501 | 2017-08-21 | LEAD | 1620 | PORT | N CLAIBORNE AV | WMLK | MI-LEAK IN THE STREET (WATER BUBBLING UP FROM HOLE) LEAK ON THE MAIN /** 1) MN: A345402 SN: 0072980, *TAP: SIZE: A LOC: 175 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: AEL2 LOC: ON PORT,176.6' FROM U.S.P.L. NO. CLAIBORNE AVE. ****/ | 2017-08-28 | MADE 6 X 6 CUT IN BLACK TOP STREET AND MADE REPAIR ON 3/4 INCH INLET ABANDON SERVICE BACKFILLED AREA
201701119501 | 2017-08-21 | LEAD | 2808 | UPPERLINE | FRERET | WILK | PLEASE REPAIR UNDER GROUND LEAK CURBCOCK JUST SITTING IN HOLE PLEASE INSTALL A CASING BOX AND 5/8 METER AREA IS FLOODING LOC.NUMBER IS 302645 DOTTIE READY 8-25-17 EXP 9-14-17 BAD CURB COCK, CUSTOMER OUT OF WATER AND SET 5/8 METER, HOUSE UNDER RENOVATION /** 1) MN: SN: 0061803, *TAP: SIZE: A LOC: 79 FEET FROM P LINE AT CLARA, *MB: CODE: CDLM LOC: ON UPPERLINE 79FT FROM USPL CLARA ****/ | 2017-08-30 | REPLACED 5FT OF 3/4 TUBING & SET 5/8 WATER METER TIED INTO LEAD
201701119901 | 2017-08-21 | LEAD | 2121-23 | PINE | PANOLA | WILK | MI- LEAK IN THE SIDE WALK INLET SERVICE LEAK AT METER /** AT 2121: 1) MN: A305887 SN: 0066908, *TAP: SIZE: B LOC: 218 FEET FROM P LINE AT PANOLA, *MB: CODE: CDMN LOC: 218' P.L. PANOLA ** AT 2123: 2) MN: A242032 SN: 0066908, *TAP: SIZE: A LOC: 218 FEET FROM P LINE AT PANOLA, *MB: CODE: CDMN LOC: 219' P.L. PANOLA ****/ | 2017-11-28 | EXAMINED AND FOUND LEAK ON CURB COCK. EXCAVATED BY HAND, REPLACED CURB COCK AND BACKFILLED WITH RIVER SAND . JOB COMPLETE LJF
201701122701 | 2017-08-22 | LEAD/PLASTIC | 3117 | COPERNICUS | MURL | WILK | MI- CUST READY FOR TIE IN METER# C036455 ACCT# 301742-407014 INLET SERVICE LEAK ALSO METER BOX BOTTOM BROKEN, CUSTOMER OUT OF WATER, NO ONE LOVING @ LOCATION ***CUSTOMER NOT READY FOR TIE IN*** /** 1) MN: C024286 SN: 0141791, *TAP: SIZE: C LOC: 120 FEET FROM P LINE AT MURL, *MB: CODE: BDM1 LOC: ON COPERNICUS, 117' FROM P.L. MURL, 7' OUTSIDE, ****/ | 2017-09-05 | TRIED TO TIE IN AND NOTICED THE METER BOX BOTTOM WAS BROKEN EXCAVATED METER BOX AND REPLACED WITH METER BOX COMPLETE NO LEAK WAS FOUND
201701124301 | 2017-08-22 | LEAD/PLASTIC | 1123 | MICHAEL | DE ARMAS | WILK | MI--SIDEWALK LEAK INLET SERVICE LEAK NEAR DRIVEWAY 01/10/18 CUSTOMER NEEDS BACKFILL (NLD) /** 1) MN: B029661 SN: 0122814, *TAP: SIZE: B LOC: 534 FEET FROM P LINE AT PATTERSON RD, *MB: CODE: CD LOC: 534FT FROM PL PATTERSON MTR ON MICHAEL 3FT INSIDE ****/ | 2017-10-23 | ARRIVED ON JOB SITE EXAMINED METER EXCAVATED BY HAND FOUBND LEAK ON INLET AND OUTLET FOUND PLASTIC ON INLET AND LEAD ON OUTLET REMOVED LEAD REPLACED WITH PLASTIC AND REPAIRED
201701124601 | 2017-08-22 | LEAD | 1505-07 | N PRIEUR | COLUMBUS | WILK | WM - LEAK BETWEEN THE SIDEWALK AND CURB INLET SERVICE LEAK IN MUDPLOT /** AT 1505: 1) MN: A307143 SN: 0041600, *TAP: SIZE: A LOC: 26 FEET FROM P LINE AT COLUMBUS, *MB: CODE: ADK LOC: 25FT FROM PL COLUMBUS ** AT 1507: 2) MN: A144667 SN: 0041600, *TAP: SIZE: A LOC: 24 FEET FROM P LINE AT COLUMBUS, *MB: CODE: __ LOC: ON NO. PRIEUR, 25' FROM P.L. COLUMBUS, 8' OUTSIDE, ****/ | 2017-09-01 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201701126701 | 2017-08-22 | LEAD | 9567 | PALM | CECIL | WMTLK | METER LEAK ACCT #148978-596157 METER # A-359498 EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN BOX /** 1) MN: A316063 SN: 0096392, *TAP: SIZE: C LOC: 510 FEET FROM P LINE AT LIVINGSTON, *MB: CODE: CD LOC: 508FT FROM PL LIVINGSTON 8' OUTSIDE PL 2' INSIDE ****/ | 2017-11-21 | EXCAVATED IN MUD PLOT ON 1 1/2 LEAD LINE LEAKING MADE ALL REPAIR TO STOP LEAK COROTROLLING LINE BACK FILL WITH RIVER SAND
201701127101 | 2017-08-22 | LEAD/PLASTIC | 3726 | PITTARI PL |  | WILK | ML METER LEAK ACCOUNT #228375541596 METER #A423353 INLET SERVICE LEAK IN MUDPLOT FLOODING CURB /** 1) MN: A218914 SN: 0120786, *TAP: SIZE: B LOC: 192 FEET FROM P LINE AT TULLIS DR, *MB: CODE: AD LOC: ON PITTARI PL 192' FROM PL TULLIS DR 8' OUTSIDE PL ****/ | 2017-11-20 | EXCAVATED METER OBSERVED LEAK ON SERVICE COCK EXCAVATED TO PROPERTY REMOVED LEAD AND REPLACED WITH PLASTIC REPLACED DID METER BOX WITH NEW METER BOX CASING AND RAISED TO GRADE BACKFILLED AND DRESSED UP WITH SAND
201701131001 | 2017-08-23 | LEAD | 1508 | SAUVAGE | GRAND RTE ST JOHN | WMTLK | LOCATIONID#148239-491453 METER#A157428 METERBOX OVERFLOWING /** 1) MN: A292757 SN: 0057317, *TAP: SIZE: B LOC: 64 FEET FROM P LINE AT GRAND RTE ST JOHN, *MB: CODE: CDL1 LOC: 63FT FROM PL GRAND ROUTE ST JOHN METER ON SAUVAGE ****/ | 2017-09-01 | REPLCAED 5/8 INCH WASHERS TO STOP LEAK
201701131301 | 2017-08-23 | LEAD | 2431 | NEW ORLEANS | N ROCHEBLAVE | WMTLK | LOCATIONID#146138-495489 METER#A419742 LEAK INSIDE METERBOX /** 1) MN: A143542 SN: 0084811, *TAP: SIZE: A LOC: 231 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BE LOC: ON NEW ORLEANS 231FT FROM ROCHEBLAVE ****/ | 2017-09-07 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201701131901 | 2017-08-23 | LEAD/PLASTIC | 516 | MAGELLAN |  | WILK | MI LEAK IN THE STREET INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A158312 SN: 0094324, *TAP: SIZE: B LOC: 144 FEET FROM P LINE AT NUNEZ, *MB: CODE: CD LOC: RES ON MAGELLAN 143' FROM PL NUNEZ 9.5' OUTSIDE L ****/ | 2017-11-30 | EXCAVATED METER BOX AND FOUND LEAK IN BOX CHANGED WASHERS AND RAISED METER BOX TO GRADE
201701132901 | 2017-08-23 | LEAD | 1829-31 | MARIGNY | N PRIEUR | WILK | MI-LEAK AT CURB EXAMINE INLET SERVICE FORLEAK NEAR GUTTER /** AT 1831: 1) MN: A278330 SN: 0082380, *TAP: SIZE: B LOC: 244 FEET FROM P LINE AT ROMAN N, *MB: CODE: CDN3 LOC: 245' P.L. N ROMAN ****/ | 2017-09-01 | EXCAVATED IN MUD PLOT + REPACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA (NO METER)
201701133001 | 2017-08-23 | LEAD | 1220 | FORSTALL | MARAIS | WILK | *****************PICKUP*************** INET SERVICE LEAK @ THE MAIN /** 1) MN: A280405 SN: 0082799, *TAP: SIZE: A LOC: 195 FEET FROM P LINE AT MARAIS, *MB: CODE: CDK LOC: RES ON FORSTALL 194FT FROM PL MARAIS ****/ | 2017-09-13 | EXCAVATED IN ASPHALT STREET OVER WATER MAIN + FOUND 2 LEAK REPLACED 1 1/2 INCH BEND ADAPTER ON WATER MAIN ALSO REPLACED 3/4 INCH BEND ADAPTER ON WATER MAQIN FOR SEPRATE SERVICE LINE COMPACTED BACKFILLED + DRESSED UP AREA
201701135301 | 2017-08-23 | LEAD | 3165 | DAUPHINE | LOUISA | WILK | BAD BLEEDER VALVE LEAK. CUSTOMER IS WAITING FOR WATER. LOC ID 115041 METER A360788 INLET SERVIC LEAK CUSTOMER HAS WATER NO ONE @ LOCATION /** 1) MN: A255250 SN: 0018447, *TAP: SIZE: A LOC: 46 FEET FROM P LINE AT LOUISA, *MB: CODE: AEN LOC: 43FT FROM UPL LOUISA METER ON DAUPHINE ****/ | 2017-09-11 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201701137101 | 2017-08-23 | LEAD/PLASTIC | 1532 | ELIZARDI BL |  | WILK | ML - METER LEAK MTR # A388556 ACCT # 225666-406033 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A277115 SN: 0122502, *TAP: SIZE: A LOC: 85 FEET FROM P LINE AT LAWRENCE, *MB: CODE: ADLO LOC: ON ELIZARD BLVD., 84.5' FROM P.L. LAWRENCE, 15.5' ****/ | 2017-10-04 | EXCAVATED ON THE INLET AND OUTLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOB SITE HAVE TO COMEBACK AND FINISH
201701138301 | 2017-08-24 | LEAD | 1844 | PAULINE | ANNETTE | WILK | ML- METER LEAK ACCT# 202586-432744 METER# A410196 INLET SERVICE LEAK NEXT TO ABOVE ADDRESS, NO METER IN BOX /** 1) MN: A307145 SN: 0092725, *TAP: SIZE: A LOC: 41 FEET FROM P LINE AT NO. PRIEUR, *MB: CODE: CDL LOC: ON PAULINE, 42' FROM P.L. NO. PRIEUR, 8' OUTSIDE, ****/ | 2017-09-08 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON ABANDON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND/COLDMILL
201701138601 | 2017-08-24 | LEAD | 927 | FRANCE | BURGUNDY | WILK | ML- METER LEAK METER# # A-407244 ACCT# 213937-707289 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A334116 SN: 0065710, *TAP: SIZE: A LOC: 19 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CD LOC: ON FRANCE 19FT FROM BURGUNDY 5FT OUTSIDE ** 2) MN: B032019 SN: 0065710, *TAP: SIZE: B LOC: 175 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CE LOC: ON FRANCE 175FT FROM PL BURGUNDY ****/ | 2017-09-08 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND / COLDMILL
201701138901 | 2017-08-24 | LEAD/PLASTIC | 6320-22 | PAINTERS | MEXICO | WMTLK | ML-- METER LEAK METER # A357632 ACCT# 176776-473653 EXAMINE INLET & OUTLET SERVICE FOR A LEAK IN GUTTER BOTTOM FLOODING GUTTER BOTTOM, METER UNDER WATER /** AT 6320: 1) MN: A134746 SN: 0145885, *TAP: SIZE: B LOC: 186 FEET FROM P LINE AT MEXICO, *MB: CODE: ADK5 LOC: 188FT FROM PL MEXICO 7' OUTSIDE PL ** AT 6322: 2) MN: A309089 SN: 0145885, *TAP: SIZE: B LOC: 186 FEET FROM P LINE AT MEXICO, *MB: CODE: ADN5 LOC: 186FT PL MEXICO 5' OUTSIDE 4'6" INSIDE CURB ****/ | 2017-10-18 | EXCAVATED IN GUTTER BOTTOM TO REPAIR INLET SERVICE AND RAISE METER BOX TO GRADE AND RENEW OUTLET FROM BOX TO PROPERTY FOUND LEAD ON INLET BOBCAT WAS AT THE SHOP
201701139701 | 2017-08-24 | LEAD | 1718 1/2 | N ROBERTSON | ST ANTHONY | WMTLK | ML METER LEAK METRER# A362607 ACCT# 123770-486732 EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A138635 SN: 0059589, *TAP: SIZE: B LOC: 134 FEET FROM P LINE AT ANNETTE, *MB: CODE: BD LOC: ON N ROBERTSON 132' FROM LRPL ANNETTE ****/ | 2017-09-08 | EXCAVATED IN GUTTER BOTTOM + REPLACED 5/8 CURB COCK + RAISED 5/8 INCH METER BOX BOTTOM TO GRADE BACKFILLED + DRESSED UP AREA ALSO REPLACED 5/8 INCH METER *************OLD METER INFO************** MTR:A362607 FAC:70890316 MAKE:SENSUS READ:90421
201701143501 | 2017-08-24 | LEAD/PLASTIC | 3600 | HUNTLEE DR | GEN DE GAULLE DR | WLPR | PP-- POOR PRESSURE METER # A367720 ACCT# 230920415187 EXAMINE INLET FOR POOR PRESSURE /** 1) MN: A339774 SN: 0139204, *TAP: SIZE: B LOC: 385 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: BDR5 LOC: 387'FORM P L BERKLEY ****/ | 2017-11-21 | EXCAVATED INLET AND CHANGED COCK
201701144201 | 2017-08-25 | LEAD | 908 | JOURDAN AV |  | WMTLK | INLET AND OUTLET SERVICES NOT LINING UP. PLEASE REPAIR METER A431701 LOC ID 185940 INLET AND OUTLET OT LINNING UP, UNABLE TO SET METER PROPERLY HOUSE UNDER RENOVATION /** 1) MN: A275868 SN: 0140193, *TAP: SIZE: B LOC: 77 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CDL6 LOC: 75FT FROM PL BURGUNDY 15' OUTSIDE PL ****/ | 2017-09-06 | EXCAVATED 3 X 2 MUD PLOT REPLACED 5/8 METER BOX COCK TO ALIGN WITH HANDWHEEL BACK FILL AND CLEANED THE AREA
201701144602 | 2017-10-10 | LEAD/PLASTIC | 3831 | TALL PINES DR | POST OAK AV | WOLK | /** 1) MN: A232369 SN: 0150996, *TAP: SIZE: A LOC: 117 FEET FROM P LINE AT POST OAK AVE, *MB: CODE: BDM LOC: RES. 117FT FROM PL POST OAK AVE 10' OUTSIDE PL 2' ****/ | 2017-10-10 | BROKE THE SIDWALK AND EXCAVATED THROUGH TREE ROOTS ONNTHE OUTLET SERVICE AND REPAIR LEAK THEN WE LEFT BARRELS AROUND JOB SITE FOR REPAIR OF THE DRAIN COMING FROM THE HOUSE BECAUSE I ACCIDENTLY PULL IT BY PULLING ROOTS OUT,,,JOB CONTINUED
201701144801 | 2017-08-25 | LEAD | 1039 | MARAIS | URSULINES AV | WILK | WM LEAK ON SIDEWALK **ON URSULINES AV SIDE** INLET SERVICE LEAK NO METER IN BOX /** 1) MN: A139876 SN: 0030083, *TAP: SIZE: B LOC: 69 FEET FROM P LINE AT MARAIS, *MB: CODE: BDHN LOC: ON URSULINES AVE., 69' FROM CPL MARAIS IN SIDEWALK ** 2) MN: A302280 SN: 0030083, *TAP: SIZE: A LOC: 70 FEET FROM P LINE AT MARAIS, *MB: CODE: BEHL LOC: ON URSULINES AVE., 65.7' FROM CPL MARAIS IN SIDE- THERE ARE 5 MORE NOT LISTED. ****/ | 2017-09-11 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA(NO METER)
201701144901 | 2017-08-25 | LEAD | 3220 | IBERVILLE |  | WILK | ML- METER LEAK ACCT# 121572-519222 METER# A395141 EXAMINE INLET SERVICE FO LEAK IN MUDPLOT NEAR BOX /** 1) MN: A286603 SN: 0046413, *TAP: SIZE: A LOC: 165 FEET FROM P LINE AT LOPEZ N, *MB: CODE: ADLT LOC: ON IBERVILLE,165' FROM U.S.P.L. NO. LOPEZ ****/ | 2017-09-05 | EXCAVATED 4 X 2 SIDEWALK CUT PLUS 3 X 3 MUD PLOT RAISE METER BOX TO GRADE REPLACED 5/8 INCH METER BOX COCK AND RENEW OUTLET FROM METER BOX TO PROPERTY BACKFILL AND CLEANED THE AREA
201701145301 | 2017-08-25 | LEAD | 3217 | LOWERLINE | OLEANDER | WMTLK | ML METER LEAK ACCT# 141786-578021 METER# A412698 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A275637 SN: 0071537, *TAP: SIZE: B LOC: 138 FEET FROM P LINE AT OLEANDER, *MB: CODE: AE LOC: ON LOWERLINE ST 137.6' FROM PL OLEANDER' ****/ | 2017-12-06 | EXCAVATED A 2 X 3 CUT IN CONCRETE SIDEWALK OVER A 5/8 INLET & OUTLET LEAD ON BOTH CHANGED THE COCK AND RAISE THE BOX UP TO GRADE. JEG
201701146201 | 2017-08-25 | LEAD/PLASTIC | 1814 | MAGAZINE | ST MARY | WMTLK | LOCATIONID#160497-543692 METER#D08034 LEAK INSIDE METERBOX /** 1) MN: D006726 SN: 0003199, *TAP: SIZE: D LOC: 35 FEET FROM P LINE AT ST MARY, *MB: CODE: CDI2 LOC: ON HASTINGS PL 34' P/L ST MARY 14' OUTSIDE 8' ****/ | 2017-11-16 | ARRIVED ON JOB SITE LOCATED METER IN MANHOLE FOUND LEAK ON INLET AND REPAIRED
201701147101 | 2017-08-25 | LEAD | 5738 | DAUPHINE | CARONDELET | WMTLK | ML METER LEAK METER# A333895 ACCT# 143353-425897 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: A277730 SN: 0074782, *TAP: SIZE: B LOC: 76 FEET FROM P LINE AT CHARBONNET, *MB: CODE: BD LOC: ON DAUPHINE 78FT FROM PL CHARBONNET ****/ | 2017-09-06 | EXCAVATED 3 X 3 MUD PLOT MADE REPAIR ON INLET SERVICE LINE AND REPLACED 5/8 METER BOX COCK BACKFILLED AND CLEANED THE AREA LEFT SAFETY CONE ON JOB TO PREVENT CUSTMER FROM DRIVING ON MUDDY AREA TO DRY
201701148601 | 2017-08-25 | LEAD | 907 | LAMANCHE |  | WOLK | BOLT LOCK BROKEN INSIDE METER UNABLE TO RM NEED TO BE TIED IN AND A 5/8 METER SET LOCATION#302716 BROKEN HANDWHEEL CUSTOMER OUT OF WATER RENOVATED HOUSE 9/5/17 ALSO TI IN SERVICE PER SR#12813919 (AJR) /** 1) MN: A262612 SN: 0101949, *TAP: SIZE: A LOC: 37 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CD LOC: ON LAMANCHE, 36.5' FROM P.L. BURGUNDY, 8' OUTSIDE ****/ | 2017-09-06 | EXCAVATED 4 X 2 SIDEWALK RELOCATED METER BOX FROM MUD PLOT TO SIDEWALK ALSO METER BOX IS UP TO GRADE BACKFILLED AND CLEANED THE AREA
201701152202 | 2017-09-06 | LEAD | 2024 | BARTHOLOMEW | N GALVEZ | WILK | EXCAVATED 4 X 4 MUD PLOT NEAR CURB FOUND LEAK COMING FURTHER IN STREET REFER TO ZONE 4 LEAK IN THE STREET BACKFILL JOB WITH RIVERSAND + COLDMILL /** 1) MN: A296275 SN: 0087458, *TAP: SIZE: A LOC: 140 FEET FROM P LINE AT GALVEZ N, *MB: CODE: N1IN LOC: ON BARTHOLOMEW ST 140' FROM URPL N GALVEZ ****/ | 2017-09-07 | EXCAVATED IN ASPHALT STREET + REPLACED 3/4 INCH BEND ADAPTER ON WATER MAIN COMPACTED BACKFILLED + DRESSED UP AREA
201701153701 | 2017-08-28 | LEAD | 2022-24 | KERLEREC |  | WILK | BLEEDER VALVE NEED TO BE REPAIRED BAD LEAK LOCATION #123687 INSPECTOR SET A-429320 INLET SERVICE LEAK IN METER BOX /** AT 2022: 1) MN: A296291 SN: 0055925, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT GALVEZ N, *MB: CODE: CDL LOC: ON KERLEREC,113' FROM U.R.P.L. NO. GALVEZ ****/ | 2017-09-07 | EXCAVATED 3 X 3 MUD PLOT REPLACED 5/8 INCH METER BOX COCK AND RENEWED OUTLET TO PROPERTY BACKFILLED AND CLEANED THE AREA
201701153801 | 2017-08-28 | LEAD | 640 | FLOOD |  | WMTLK | INLET SERVICE NEEDS REPAIR. PLEASE REPAIR AND SET A 5/8 METER. CUSTOMER IS WAITING ON WATER. LOC ID 302712 CUSTOMER REQUEST LEAD BE REMOVED, CURB COCK MISSING IN BOX, ALSO RENEW INLET SERVICE. ***HOUSE UNDER RENOVATIONS*** /** 1) MN: A154218 SN: 0055111, *TAP: SIZE: A LOC: 88 FEET FROM P LINE AT FLOOD, *MB: CODE: BDH1 LOC: ON ROYAL,88' FROM U.R.P.L. FLOOD ****/ | 2017-09-11 | EXCAVATED 4 X 3 SIDEWALK CUT ALSO 15 X1 MUD PLOT TRENCH MOVED METER BOX TO SIDEWALK AND SET 5/8 INCH METER BACKFILLED AND CLEANED THE AREA
201701154201 | 2017-08-28 | LEAD | 3324 | CAMP | TOLEDANO | WMTLK | ACCT#109585 MET#A240331 PLEASE REPAIR LEAK IN MET BOX /** 1) MN: A240331 SN: 0018712, *TAP: SIZE: A LOC: 143 FEET FROM P LINE AT LOUISIANA AVE, *MB: CODE: ADM2 LOC: BET TOLDANO/LA 143'PL LA ****/ | 2018-01-19 | EXCAVATED IN MUD PLOT OVER 5/8 INCH METER FOUND METER BOX STOP COCK LEAKING REPLACE 5/8 INCH METER BOX STOP COCK BACKFILL
201701154801 | 2017-08-28 | LEAD/PLASTIC | 711 | BEHRMAN AV | OPELOUSAS AV | WOLK | LOCATION# 225576 CUSTOMER# 403788 METER# A392869 INSPECTOR MET W/CUSTOMER DID AN INSIDE/OUTSIDE INSPECTION FOUND NO FIXTURE PROBLEMS, DID OUTSIDE INSPECTION FOUND CONSTANT REG ON METER, PERFORM S&WB TEST METER CONTINUES TO RUN. PLEASE REPAIR /** 1) MN: A310870 SN: 0098604, *TAP: SIZE: A LOC: 71 FEET FROM P LINE AT OPELOUSAS AVE, *MB: CODE: BD LOC: RES ON BEHRMAN AVE 71' FROM PL OPELOUSAS 6' OUTSID ****/ | 2017-09-28 | EXCAVATED METER NO LEAK WAS FOUND BUT FONUD LEAD ON OUTLET REMOVED LEAD AND REPLACED WITH PLASTIC
201701155701 | 2017-08-28 | LEAD | 2206 | ALABO |  | WILK | /** 1) MN: SN: 0138817, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT NO. MIRO, *MB: CODE: __ LOC: ON ALABO, 47' FROM P.L. NO. MIRO, 3' INSIDE CURB ****/ | 2017-08-28 | EXCAVATED 2 X 2 MUD PLOT AROUND METER BOX SET NEW METER BOX CASING TO LOWER METER BOX TO GRADE
201701156602 | 2017-08-28 | LEAD | 2226 | GORDON |  | WOLK | EXCAVATED 2 X 2 MUD PLOT UNABLE TO FIX JOB DUE TO HEAVY RAIN BACKFILL THE AREA /** 1) MN: A340522 SN: 0128264, *TAP: SIZE: B LOC: 198 FEET FROM P LINE AT TONTI, *MB: CODE: CDLN LOC: RES ON GORDON 198FT FROM PL TONTI N 6' OUTSIDE PL ****/ | 2017-08-30 | EXCAVATED 5 X 2 MUD PLOT RAISE METER BOX TO GRADE
201701159701 | 2017-08-30 | LEAD | 622 | CAFFIN AV | ROYAL | WMBK | LOCATIONID#105237-425219 METER#A283281 METER CASING MISSING,PLEASE REPLACE /** 1) MN: A305866 SN: 0055666, *TAP: SIZE: B LOC: 96 FEET FROM P LINE AT ROYAL, *MB: CODE: CDL LOC: BY POLE ****/ | 2017-09-11 | CLEANED OUT MUD INSIDE METER AND REPLACED METER BOX CASING
201701159901 | 2017-08-30 | LEAD | 1219 | TREME | BARRACKS | WMTLK | ML METERLEAK MTR#A337210 ACCT#111874-526156 LEAK ON METER /** 1) MN: A337210 SN: 0015795, *TAP: SIZE: A LOC: 119 FEET FROM P LINE AT BARRACKS, *MB: CODE: AEN LOC: ON LIBERTY 119FT FROM BARRACKS ****/ | 2017-09-06 | REPLCAED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201701160801 | 2017-08-30 | LEAD | 2801 | N RAMPART | ST FERDINAND | WILK | ML METER LEAK METER#A330681 INLET SERVICE LEAK NO METER IN BOX /** 1) MN: A300481 SN: 0003830, *TAP: SIZE: A LOC: 52 FEET FROM P LINE AT RAMPART N, *MB: CODE: AFHK LOC: 2ND METER SIDE ST/ST FERDINAND 52FT PL N RAMPART ** 2) MN: A156944 SN: 0003830, *TAP: SIZE: A LOC: 49 FEET FROM P LINE AT RAMPART N, *MB: CODE: AFHK LOC: 3RD METER SIDE ST/ST FERDINAND 49FT PL N RAMPART THERE ARE 2 MORE NOT LISTED. ****/ | 2017-09-15 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201701161801 | 2017-08-30 | LEAD | 2138 | LIZARDI | MIRO | WMTLK | ML- METER LEAK METER#A404473 ACCT#220635-424320 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-09-06 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 3/4 INCH CURB COCK BACKFILLED + DRESSED UP AREA ALSO REPLACED DAMAGED 5/8 INCH WATER METER] **********OLD METER INFO********* MTR:A413134 FAC:14118896 MAKE:HERSEY READ:290
201701162201 | 2017-08-30 | LEAD | 2911 | ST BERNARD AV | AGRICULTURE | WOLK | ML METERLEAK MTR#B036665 ACCT#146323-492842 CONS REG ON METER /** 1) MN: B018882 SN: 0078425, *TAP: SIZE: B LOC: 68 FEET FROM P LINE AT AGRICULTURE, *MB: CODE: BDO2 LOC: 104FT FROM PL AGRICULTURE ON ST BERNARD AVE ****/ | 2017-09-11 | EXAMINED JOB FOUND METER NOT REGISTION REPLACED METER TO FIX PROBLEM. OLD METER INFO: MTR#B036665 FAC:73264460 MAKE:SENSUS READ:090900
201701169701 | 2017-08-31 | LEAD | 1025 | GORDON | EL DORADO | SMHC | MI MISSING MANHOLE COVER IN STREET *******B LEAVE IN SYSTEM****** CRACKED SEWER MANHOLECASING, LEFT 1 (ONE) CONE FOR PROTECTION /** 1) MN: A318880 SN: 0085999, *TAP: SIZE: A LOC: 34 FEET FROM P LINE AT EL DORADO, *MB: CODE: AD LOC: ON GORDON 34FT FROM PL ELDORADO ****/ | 2017-09-14 | EXCAVATED JOB AT ABOVE LOCATION FOUND SEWER CASING BROKE REPLACE CASING JOB COMPLETE
201701171201 | 2017-08-31 | LEAD/PLASTIC | 601 | SLIDELL |  | WMRE | METER BOX BURIED PLEASE RAISE TO GRADE AND SET A 5/8 METER CUSTOMER STATES NEED WATER LOCATION #302675 LOCATE/RAISE/SET 5/8 METER /** 1) MN: A316281 SN: 0033901, *TAP: SIZE: A LOC: 66 FEET FROM P LINE AT SLIDELL, *MB: CODE: BFH LOC: ON VERRET 66' FROM LSPL SLIDELL ****/ | 2017-09-10 | LOCATED AND RAISE 5/8 METER BOX TO GRADE RENEWED OUTLET SERVICE SET A 5/8 METER
201701172501 | 2017-09-01 | LEAD | 4914 | N ROBERTSON | DESLONDE | WILK | ML - METER BOX LEAKING @ VACANT PROPERTY INLET SERVICE LEAK IN A LARGE 44 X 20 CUT IN THE STREET ***LEAKING AGAIN*** /** 1) MN: A283144 SN: 0148211, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT DESLONDE, *MB: CODE: BDK LOC: ON N ROBERTSON 111FT FROM P.L. DESLONDE 8FT OUT- ****/ | 2017-09-12 | CLEANED OUT METER BOX AND REPLACED 5/8 INCH WASHERS TO STOP LEAK METER OFF BY CUSTOMER REQUEST,,,CREW FOUND METER #A283144 AT ABOVE LOCATION.
201701172601 | 2017-09-01 | LEAD | 1552-54 | N DERBIGNY | LAHARPE | WMTLK | MI- LEAK BETWEEN CURB AND SIDEWALK EXAMINE INLET &: OUTLET SERVICE FOR A LEAK IN GARDEN/MUD PLOT /** AT 1552: 1) MN: A269157 SN: 0054811, *TAP: SIZE: A LOC: 105 FEET FROM P LINE AT LAHARPE, *MB: CODE: DK LOC: ON NO. DERBIGNY,105' FROM L.R.P.L. LAHARPE ****/ | 2017-09-14 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201701173901 | 2017-09-01 | LEAD | 2207 | ROYAL |  | WILK | LOCATION ID-181308 MTR-DOO8173 METER LEAK INLET LEAK ON UNION IN MANHOLE /** 1) MN: D004066 SN: 0054646, *TAP: SIZE: D LOC: 38 FEET FROM P LINE AT ROYAL, *MB: CODE: CEHK LOC: ON ELYSIAN FIELDS 38FT FROM PL ROYAL 4' OUTSIDE P ****/ | 2017-12-22 | REPLACED 1 1/2 INCH UNIONS IN MANHOLE
201701175001 | 2017-09-01 | LEAD | 1936 | CLOUET |  | WILK | /** 1) MN: A272276 SN: 0084170, *TAP: SIZE: A LOC: 295 FEET FROM P LINE AT PRIEUR N, *MB: CODE: CD LOC: ON CLOUET ST 295' FROM PL N PRIEUR ****/ | 2017-09-01 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201701175101 | 2017-09-01 | LEAD | 2006 | CLOUET | N JOHNSON | WILK | /** 1) MN: A257807 SN: 0098613, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CD LOC: 45'FROM N.JOHNSON 7' OUTSIDE PL ****/ | 2017-09-01 | EXCAVATED IN MUD PLOT + REPLACED 5/8 CURB COCK BACKFILLED + DRESSED UP AREA (NO METER)
201701178201 | 2017-09-03 | LEAD/PLASTIC | 1673 | LAURADALE DR | GEN DE GAULLE DR | WMTLK | WM-LEAK IN SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR LEAK FLOODING SIDEWALK /** 1) MN: A259089 SN: 0126653, *TAP: SIZE: B LOC: 94 FEET FROM P LINE AT MAGELLAN, *MB: CODE: CDLM LOC: ON LAURADALE DR., 94' FROM P.L. MAGELLAN, 9' OUT- ****/ | 2017-09-20 | EXCAVATED METER BOX INLET AND OUTLET SIDE METER WAS 3 BARRELS DEEP SO WE RAISED IT UP FOUND LEAK ON LEAD OUTLET AND REPLACED FROM PROPERTY TO METER BOX NEED DRESS UP
201701178801 | 2017-09-03 | LEAD/PLASTIC | 2910 | WESTCHESTER PL | BRIGHTON PL | WILK | ML- METER LEAK METER#A311123 ACCT#234470-419781 INLET SERVICE LEAK IN GRASS IN FRONT OF METER FLOODING AREA 09/28/17 METER LEAK AFFECTING WATER PRESSURE IN HOME PER SERVICE REQUEST #12816380 (FCP) 1/8/18 PRESSURE POOR PER S/R # 12826537 (PET) 01/22/18 LEAK HAD GOTTEN WORSE, NOW FLOODING AREA PER SR#12828656 (AJR) 02/22/18 LEAK CAUSING VERY POOR PRESSURE, UPGRADE TO B1ST AM, PER INSPC, SR#12833145 (AJR) /** 1) MN: A311123 SN: 0155115, *TAP: SIZE: B LOC: 123 FEET FROM P LINE AT BRIGHTON PL, *MB: CODE: BD LOC: 123FT FROM PL BRIGHTON 10' OUTSIDE PL 2' INSDIE CU ****/ | 2018-02-23 | EXACAVTED ON THE INLET AND OUTLET SERVICE AND REPAIR LEAK AND RAISE METER BOX TO GRADE THEN WE BACKFILL JOB SITE
201701179401 | 2017-09-04 | LEAD/PLASTIC | 2913 | AMAZON | INDIANA | WOLK | WM-LEAK IN SIDEWALK EXAMINE OUTLET SERVICE @ PROPERTY FOR A LEAK FLOODING GRASS & SIDEWALK. **PER CUST 3 PEOPLE ALMOST FELL DUE TO LEAK, ALSO INSP TRIED LEAVING A CONE CUST SATED TAKE CONE IT WILL NOT HELP /** 1) MN: A230410 SN: 0172440, *TAP: SIZE: A LOC: 25 FEET FROM P LINE AT INDIANA, *MB: CODE: CD LOC: ON AMAZON 25' FROM P.L. INDIANA 8' OUTSIDE 3'IN- ****/ | 2017-10-31 | EXCAVTED METER EXPOSED INLET AND OUTLET EXAMINED METER FOUND LEAK ON INLET WASHERS REPALCED WASHERS AND METER
201701180001 | 2017-09-04 | LEAD/PLASTIC | 446 | HUNTLEE DR | ANSON | WMTLK | ML- METER LEAK METER#A287826 ACCT#226913-703862 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: A287826 SN: 0132737, *TAP: SIZE: A LOC: 191 FEET FROM P LINE AT SULLIVAN PL., *MB: CODE: BFK LOC: ON HUNTLEE DR., 191' FROM P.L. SULLIVAN PL., 2' ****/ | 2017-09-28 | EXCAVATED METER BOX AND FOUND LEAK ON HAND WHEEL REPLACED HANDWHEEL ON OUTLET ***********OLD METER INFO**************** METER:A287826 FAC:49137420 SENSUS:READ:20820
201701181501 | 2017-09-05 | LEAD/PLASTIC | 3204 | MAGELLAN | ODEON AV | WOLK | WM - LEAK ON THE SIDEWALK EXAMINE OUTLET SERVICE FOR LEAK BEHIND BOX 10/11/17 CUST STATES LEAK HAS GOTTEN WORST (KSW) /** 1) MN: A282904 SN: 0132083, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT ODEON AVE, *MB: CODE: BDK7 LOC: ON MAFELLAN 110FT FROM P.L. ODEON OPP FAUCET ****/ | 2017-11-02 | ARRIVED ON JOB SITE EXAMINED METER EXCAVATED BY HAND FOUND LEAK ON INLET AND REPAIRED
201701185202 | 2017-11-29 | LEAD | 4903 | IBERVILLE |  | WSNR | EXAVATE TO CHECK FOR LEAD FROM PROPERTY TO MAIN /** 1) MN: A219511 SN: 0025600, *TAP: SIZE: B LOC: 34 FEET FROM P LINE AT ANTHONY N, *MB: CODE: OOO LOC: ON IBERVILLE 35FT FROM PL N ANTHONY ** 2) MN: SN: 0025600, *TAP: SIZE: B LOC: 34 FEET FROM P LINE AT ANTHONY N, *MB: CODE: __ LOC: ON IBERVILLE 35FT FROM PL N ANTHONY ****/ | 2018-11-06 | JOB WILL BE RE-SCHEDLE AT A LATER DATE DO TO PAVEMENT BACK LOG
201701187001 | 2017-09-05 | LEAD | 631 | KERLEREC | ROYAL | WILK | ML- METER LEAK METER#A224843 ACCT#112298--704597 INLET SERVICE LEAK ON SIDEWALK FLOODING SIDEWALK /** 1) MN: A224843 SN: 0044272, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT ROYAL, *MB: CODE: BEN1 LOC: 95' P.L. ROYAL ****/ | 2017-09-13 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA
201701187201 | 2017-09-05 | LEAD | 3018 | ESPLANADE AV | N LOPEZ | WILK | ML - METER LEAK MTR# A 421318 ACCT# 107962-521950 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A300733 SN: 0015370, *TAP: SIZE: A LOC: 115 FEET FROM P LINE AT GAYOSO N, *MB: CODE: AFN2 LOC: ON ESPLANADE 115 FT FROM PL N GAYOSO ****/ | 2017-09-07 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201701188401 | 2017-09-05 | LEAD/PLASTIC | 1900 | SHALETT | WALL BL | WILK | ML- METER LEAK MN:A320642 ACCT#231628-4063477 INLET SERVICE LEAK AT METER IN GRASS /** 1) MN: A320642 SN: 0143994, *TAP: SIZE: C LOC: 2 FEET FROM P LINE AT WALL BLVD, *MB: CODE: CDN3 LOC: ON SHALETT 2' FROM PL WALL BLVDIDE PL 3' INSIDE CU ****/ | 2017-11-27 | EXCAVATED ON METERBOX FOR LEAK FOUND LEAK INSIDE BOX ON INLET BACKFILLED AND CLEANED JOB SITE
201701191401 | 2017-09-06 | LEAD/PLASTIC | 1728 | RICHLAND RD | GEN MEYER AV | WMTLK | ML - METER LEAK MTR# A 148391 ACCT# 226418-409140 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: A148391 SN: 0123411, *TAP: SIZE: B LOC: 207 FEET FROM P LINE AT HYDT #5, *MB: CODE: AM12 LOC: 207'FROM S S HYDRANT 5 MTR ON RICHLAND ****/ | 2017-09-15 | EXCAVATED METER BOX BY HAND AND FOUND LEAK ON BOX COCK INSTALLED METER BOX COMPLETE BACKFILLED
201701191801 | 2017-09-06 | LEAD/PLASTIC | 801 | ST JOSEPH | CARONDELET | WILK | WM- LEAK IN STREET INLET SERVICE LEAK IN ASPHALT STREET GETING OFF IN DCB 10/31/17 INLET SERVICE LEAK IN AN ASPHALT STREET NEAR CURB FLOODING AREA SOME WATER GETTING OFF IN THE DCB. (KSW) /** 1) MN: G002347 SN: 0000000, *TAP: SIZE: G LOC: 50 FEET FROM P LINE AT ST JOSEPH, *MB: CODE: CD LOC: ON CARONDELET 59FT FROM ST JOSEPH 9.5FT OUTSIDE ** 2) MN: A242034 SN: 0003732, *TAP: SIZE: A LOC: 103 FEET FROM P LINE AT CARONDELET, *MB: CODE: __ LOC: ON ST. JOSEPH,100' FROM P.L. CARONDELET,1' OUTSIDE ****/ | 2018-06-27 | BROKE THE STREET AND EXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEANE UP JOB SITE
201701192401 | 2017-09-06 | LEAD | 1017 | SISTER | N RAMPART | WMLK | MI LEAK IN STREET 20 FT PAST HYDRANT LEAK ON MAIN IN MUDPLOT BETWEEN SIDEWALK/CURB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-09-19 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH ABANDON INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND/COLDMILL,,,NO METER
201701192501 | 2017-09-06 | LEAD | 4231 | N DERBIGNY | FRANCE | WILK | ML- METER LEAK METER#A407239 ACCT#135261-432844 INLET SERVICE LEAK INSIDE METER BOX **CHANGED FROM 4231 N DERBIGNY** /** 1) MN: A307076 SN: 0084752, *TAP: SIZE: A LOC: 156 FEET FROM P LINE AT FRANCE, *MB: CODE: CDL1 LOC: METER ON N DERBIGNY 156 FT FROM PL FRANCE ****/ | 2017-09-08 | R5EPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201701192701 | 2017-09-06 | LEAD | 2222 | PORT |  | WILK | MI - LEAK BETWEEN SIDEWALK & CURB INLET SERVICE LEAK IN MUDPLOT NO METER IN BOX CURBCOCK PASSING WATER /** 1) MN: A151583 SN: 0094484, *TAP: SIZE: A LOC: 50 FEET FROM P LINE AT MIRO N, *MB: CODE: BEM2 LOC: 159'P/L N MIRO 8' OUTSIDE P/L 2' INSIDE CURB ** 2) MN: A328076 SN: 0094484, *TAP: SIZE: A LOC: 153 FEET FROM P LINE AT MIRO N, *MB: CODE: BEM2 LOC: 155' FROM PL. N MIRO 4' OUTSIDE PL ON PORT ****/ | 2017-09-08 | EXCAVATED IN CONCRETE DRIVEWAY + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201701193601 | 2017-09-06 | LEAD | 1701 | FRANKLIN AV |  | WMRE | PLEASE RAISE TO GRADE AND REPAIR SIDEWALK. METER IS UNREADABLE. LOC ID 212559 METER E006505 LOCATE/RAISE METER TO GRADE /** 1) MN: SN: 0072734, *TAP: SIZE: C LOC: 68 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: ADN3 LOC: 63FT FR PL N DERBIGNY LPL NEAR POST ** 2) MN: E006765 SN: 0172955, *TAP: SIZE: E LOC: 120 FEET FROM P LINE AT PORT, *MB: CODE: CD LOC: ON DERBIGNY 120FT FROM PORT 7FT OUTSIDE 10FT ****/ | 2017-09-15 | LOCATED AND MARK WATER METER LOCATION ON SIDEWALK AND STREET METER IS UP TO GRADE NO METER IS AT 68 FT FROM PROPERTY LINE AT N DERBIGNY EXCAVATED 4 X 4 CUT AROUND MANHOLE USDE 2 MOON RING TO BRING MANHOLE TO GRADE ALSO CEMENT AROUND THE BASE BACKFILL AND CLEANED THE AREA
201701194701 | 2017-09-07 | LEAD/PLASTIC | 2710 | SOMERSET DR | ANSON | WOLK | ML METERLEAK MTR#B030738 ACCT#228537-416585 CONS REG ON METER /** 1) MN: B030738 SN: 0123285, *TAP: SIZE: B LOC: 500 FEET FROM P LINE AT ANSON, *MB: CODE: CDLM LOC: BET ANSON-MC ARTHUR 500'FROM P L ANSON ****/ | 2017-10-31 | EXCAVATED METER EXPOASED INLET AND OUTLET METER LEAKING FROM INLET REPAIRED
201701197101 | 2017-09-07 | LEAD | 1537 | N BROAD | LAHARPE | WILK | MI- LEAK BETWEEN THE SIDEWALK AND THE CURB INLET SERVICE LEAK IN BOX NEXT TO ABOVE ADDRESS NO METER IN BOX 09/12/17 PER INSP K GRIFFIN CHANGED ADDRESS FROM 1537 N BROAD TO 1535 N BROAD **(SPOKE TO DENTIST @ ABOVE ADDRESS)** /** 1) MN: A320666 SN: 0047469, *TAP: SIZE: A LOC: 58 FEET FROM P LINE AT BROAD N, *MB: CODE: BDHM LOC: 2ND METER SIDE GUTTER EDGE ON LAHARPE 59' P.L. ****/ | 2017-09-20 | EXCAVATED 3 X 3 MUD PLOT REPLACED 5/8 METER BOX COCK TO STOP LEAK BACKFILL AND CLEANED THE AREA
201701199601 | 2017-09-07 | LEAD | 2136 | PAUGER | N CLAIBORNE AV | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A284655 SN: 0026482, *TAP: SIZE: B LOC: 58 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: AFL LOC: ON PAUGER 57FT PL N ROBERTSON 2' OUTSIDE 6' IN- ****/ | 2017-09-19 | EXCAVATED 3 X 2 MUD PLOT MADE ON INLET SERVICE LINE TO STOP LEAK BACKFILL AND CLEANED THE AREA
201701200001 | 2017-09-07 | LEAD | 2529 | BRISTOL PL | ANSON | WMLK | MI-LEAK IN STREET LEAK ON WATER MAIN IN CONCRETE STREET GETTING OFF IN DCB /** 1) MN: A276547 SN: 0122012, *TAP: SIZE: B LOC: 100 FEET FROM P LINE AT ANSON, *MB: CODE: CDLN LOC: ON BRISTOL 100FT FROM ANSON ****/ | 2018-04-27 | ARRIVED ON JOB SITE EXAMINED WHERE LEAK SHOULD BE IN STREET FOUND NO LEAK EXAMINED METER FOUND WATER IN METER BOX EXCAVATE BY HAND CHOPPED TROUGHT TREE ROOOTS EXPOSED INLET AND OUTLET FOUND NO LEAK FOUND LEAD OM INLET AND BACKFILLED
201701200601 | 2017-09-08 | LEAD/PLASTIC | 832 | 3RD | LAUREL | WOLK | WM-LEAK ON THE SIDEWALK /** 1) MN: 000000 SN: 0033011, *TAP: SIZE: __ LOC: 80 FEET FROM P LINE AT LAUREL, *MB: CODE: CEM LOC: ON THIRD 76FT PL LAUREL 3' OUTSIDE 7' INSIDE CURB ** 2) MN: A124958 SN: 0033011, *TAP: SIZE: B LOC: 80 FEET FROM P LINE AT LAUREL, *MB: CODE: CEM LOC: ON THIRD 77FT PL LAUREL 3' OUTSIDE 7' INSIDE CURB THERE ARE 3 MORE NOT LISTED. ****/ EXAMINE FOR LEAK AT P LINE ON BRICK SIDEWALK FOUND HOLE EXPOSE. | 2017-10-26 | EXAMINE SIX OVERFILLED METER CASING PUMPED OUT EACH METER TO FIND LEAK ON ONE OF THEM REPAIRED METER
201701203201 | 2017-09-08 | LEAD/PLASTIC | 8500 | SPRUCE | JOLIET | WOLK | ****************PICKUP************** OUTLET SERVICE LEAK ON SIDEWALK CAUSING POOR PRESSURE METER LOCATED INSIDE MANHOLE **1ST AM** /** 1) MN: E004776 SN: 0044968, *TAP: SIZE: C LOC: 47 FEET FROM P LINE AT SPRUCE, *MB: CODE: AEHL LOC: ON JOLIET 45FT FROM PL SPRUCE 8' OUTSIDE PL ****/ | 2017-09-09 | FOUND LEAK ON OUTLET SERVICE IN MUD HOLE THAT WAS HAVING POOR PRESSURE MADE REPAIRS TO OUTLET TO STOP LEAK
201701203301 | 2017-09-08 | LEAD | 3316 | CANAL | HAGAN AV | WILK | ML- METER LEAK METER#B031844 ACCT#101693-532060 INLET SERVICE LEAK IN TREEROOTS /** 1) MN: B021978 SN: 0011140, *TAP: SIZE: C LOC: 177 FEET FROM P LINE AT HAGAN AVE, *MB: CODE: ADM6 LOC: ON CANAL 209FT FROM URPL HAGAN AVE ****/ | 2017-09-12 | EXCAVATED IN MUD PLOT + REPLACED 3/4 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201701204901 | 2017-09-08 | LEAD/PLASTIC | 1726 | GEN COLLINS AV | GEN MEYER AV | WILK | ML- METER LEAK MTR# A411303 ACCT# 229717-409201 INLET SERVICE LEAK AT METER IN GRASS /** 1) MN: A322994 SN: 0131622, *TAP: SIZE: B LOC: 356 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: AFMO LOC: ON GEN COLLINS 339FT FROM P.L. GEN MEYER ****/ | 2017-11-01 | EXCAVATED METER BOX AND FOUND LEAK ON INLET AND OUTLET INSTALLED METER BOX COMPLETE
201701205601 | 2017-09-09 | LEAD/PLASTIC | 1429 | DE ARMAS | LEBOUEF | WMTLK | WM-LEAK IN SIDEWALK EXAMINE INLET & OUTLET SERVICE ON ABANDON SERVICE FOR A LEAK, METER BOX UNDER WATER & GUTTER BOTTOM FLOOED /** 1) MN: A285708 SN: 0108593, *TAP: SIZE: B LOC: 169 FEET FROM P LINE AT LEBOEUF, *MB: CODE: ADL LOC: ON DE ARMAS, 169' FROM P.L. LEBOUEF, 5.5' OUTSIDE ****/ | 2017-10-13 | EXCAVATED METER BOX IN DITCH AND FOUND BAD CURB COCK INSTALLED METER BOX COMPLETE NEED DRESS UP
201701210901 | 2017-09-11 | LEAD/PLASTIC | 3711 | HERALD |  | WOLK | ML METER LEAK ACCOUNT #229581415057 METER #A397262 EXAMINE OUTLET SERVICE @ PROPERTY LINE FOR A LEAK FOUND 1 S&WB BARREL ON SITE **PER INSP U SANTIAGO ( B ) LEAAVE IN SYSTEM. 10/12/17 CUSTOMER STATES LEAK HAS GOTTEN WORSE (NLD) /** 1) MN: A317371 SN: 0130526, *TAP: SIZE: B LOC: 565 FEET FROM P LINE AT VICTORY DR, *MB: CODE: CDLK LOC: ON HERALD, 567' FROM P.L. VICTORY DR., 7' OUTSIDE, ****/ | 2017-11-03 | EXCAVATED BY HAND AND REPLACED OUTLET FROM BOX TO PROPERTY
201701211801 | 2017-09-11 | LEAD | 3111 | GRAND RTE ST JOHN |  | WMRE | PLEASE LOCATE AND REMOVE METER A406591 LOC ID 202061 LOCATER & REMOVE METER /** 1) MN: A316322 SN: 0162170, *TAP: SIZE: B LOC: 14 FEET FROM P LINE AT GRAND RTE ST JOHN, *MB: CODE: OOO LOC: ON N LOPEZ 35' FROM CORNER OF N. LOPEZ 7' OUTSIDE ****/ | 2017-09-20 | REMOVED METER FROM THSI LOCATION
201701212101 | 2017-09-11 | LEAD/PLASTIC | 600 | WAGNER | EVELINA | WILK | ML LEAK IN METER BOX METER # A-352683 ACCT # 250516 VACANT PROPERTY INLET SERVICE LEAK CAUSING METER BOX TO OVERFLOW 10/12/17 CUSTOMER STATES LEAK IS GETTING WORSE (NLD) 10/18/17 LEAK GETTNG WORSE PER SR#12818143 (AJR) /** 1) MN: A144704 SN: 0103039, *TAP: SIZE: A LOC: 20 FEET FROM P LINE AT EVELINA, *MB: CODE: AD LOC: ON WAGNER 19.5' FROM PL EVELINA FRONT ****/ | 2017-10-27 | EXAMINED METER BOX EXCAVATED METER FOUND LEAK ON BOX COCK AND HANDWHEEL REPLACED BOTH BROUGHT METER TO GRDAE DUE TO SATURTED SOIL A DRESS UP IS NEEDED LEFT PLACED ON TOP OF METER A BARREL
201701214801 | 2017-09-11 | LEAD | 917 | REYNES | BURGUNDY | WILK | MI-SEE WHY NO WATER METER#A351908 ACCT#180924-424630 DRY INLET ****CUSTOMER OUT OF WATER*** J CLARK @ 20:37PM /** 1) MN: A158873 SN: 0128286, *TAP: SIZE: A LOC: 86 FEET FROM P LINE AT BURGUNDY, *MB: CODE: BDL LOC: ON REYNES 86FT FROM PL BURGUNDY ****/ | 2017-09-11 | EXCAVATED IN MUDPLOT. REPAIR 3/4 LEAD LINE. DRESS UP WITH RIVER SAND. JOB COMPLETE LJF
201701216501 | 2017-09-12 | LEAD | 1702 | ALVAR | N DERBIGNY | WMLK | MI LEAK IN THE STREET EXAMINE LEAK ON ABANDON CONTROLLING LINE ON SIDEWALK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-10-23 | REPLACED 5/8 INCH WAHERS TO STOP LEAK
201701217001 | 2017-09-12 | LEAD | 4426 | S LIBERTY | NAPOLEON AV | WILK | ML-METER LEAK ACCT#143692-570755 METER#A383324 INLET SERVICE LEAK BEHIND CURB COCK /** 1) MN: A218478 SN: 0075027, *TAP: SIZE: B LOC: 220 FEET FROM P LINE AT NAPOLEON AVE, *MB: CODE: BDK2 LOC: BY DRIVE 21FT FROM PL 11FT FROM HSPL CURB METER ON ****/ | 2018-03-18 | REPLACED 5/8 CURB COCK TIED INTO LEAD UNABLE TO REMOVE LEAD DO TO CAR PARKED ON JOB.
201701217002 | 2018-03-18 | LEAD | 4424-26 | S LIBERTY | NAPOLEON AV | WSNR | REFER TO ZONE 3 TO REMOVE LEAD FROM WATER MAIN TO METER /** AT 4426: 1) MN: A218478 SN: 0075027, *TAP: SIZE: B LOC: 220 FEET FROM P LINE AT NAPOLEON AVE, *MB: CODE: BDK2 LOC: BY DRIVE 21FT FROM PL 11FT FROM HSPL CURB METER ON ****/ | 2018-05-14 | GIVE TO CONTRACTOR
201701220301 | 2017-09-12 | LEAD | 840 | CANAL | BARONNE | WILK | WM LEAK BETWEEN STREET & SIDEWALK EXAMINE INLET SERVICE LEAK BETWEEN SIDEWALK & CURB /** 1) MN: D007122 SN: 0002880, *TAP: SIZE: D LOC: 95 FEET FROM P LINE AT CANAL, *MB: CODE: BHR6 LOC: IN MH IN STREET ON BARONNE 90FT FROM PL CANAL 15' ** 2) MN: SN: 0002880, *TAP: SIZE: C LOC: 97 FEET FROM P LINE AT CANAL, *MB: CODE: __ LOC: ON BARONNE,97' FROM U.R.P.L. CANAL ****/ | 2017-09-18 | REPLACE 1 1/2 INCH UNION AND NIPPLE TO STOP LEAK
201701220601 | 2017-09-12 | LEAD/PLASTIC | 1210 | KABEL DR | COPERNICUS | WMTLK | ML-METER LEAK EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: B018596 SN: 0126071, *TAP: SIZE: B LOC: 586 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: AD LOC: ON KABEL DR., 586' FROM P.L. GEN. MEYER AVE., 7' ****/ | 2017-10-30 | EXCAVATED ON METER BOX FOR LEAK FOUND LEAK ON OUTLET MADE REPAIR BACKFILLED AND CLEANED JOB SITE
201701221001 | 2017-09-12 | LEAD | 1939 | BENTON |  | WOLK | /** 1) MN: A143417 SN: 0133207, *TAP: SIZE: A LOC: 46 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CDN2 LOC: 2 APTS ON BENTON 46FT PL N JOHNSON 7' OUTSIDE ****/ | 2017-09-12 | EXCAVATED 3 X 3 MUD PLOT REPLACED 5/8 INCH METER BOX COCK AND RAISED METER BOX TO GRADE BACKFILLED AND CLEANED THE AREA
201701221901 | 2017-09-12 | LEAD | 201 | ROMAN | IBERVILLE | WILK | MI-LEAK IN THE SIDEWALK INLET SERVICE LEAKING BETWEEN SIDEWALK/ CURB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-12-15 | EXCAVATED 2 X 2 MUD PLOT REPLACED 1 INCH HANDWHEEL TO STOP LEAK BACKFILL AND CLEANED THE AREA
201701222001 | 2017-09-12 | LEAD | 919 | BURGUNDY | DUMAINE | WILK | **********PICKUP JOB********** INLET SERVICE LEAK BEHIND METER BOX IN SIDEWALK /** 1) MN: A180975 SN: 0028917, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT DUMAINE, *MB: CODE: AE LOC: METER ON BURGUNDY 131 FT FROM PL DUMAINE ** 2) MN: C021128 SN: 0029917, *TAP: SIZE: G LOC: 124 FEET FROM P LINE AT DUMAINE, *MB: CODE: CDR LOC: ON BURGUNDY 129FT FROM PL DUMAINE 17FT OUTSIDE PL ****/ | 2017-09-18 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACE 3/4 METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201701222501 | 2017-09-12 | LEAD/PLASTIC | 6061 | OXFORD PL |  | WILK | MI-LEAK AT THE CURB INLET SERVICE LEAK IN GRASS /** 1) MN: A260628 SN: 0161939, *TAP: SIZE: B LOC: 52 FEET FROM P LINE AT FALMOUTH DR, *MB: CODE: OOO LOC: ON OXFORD PL., 54' FROM P.L. FALMOUTH, 9' OUTSIDE, ****/ | 2017-11-22 | EXCAVATED METER EXPOSED INLET AND OUTLET OBSERVED LEAK ON INLET LINE REPAIRED LEAK BACKFILLED DRESSED UP WITH SANDRI
201701224101 | 2017-09-13 | LEAD | 127 | N DORGENOIS | IBERVILLE | WOLK | ML METERLEAK MTR#A255706 ACCT#110243-522714 CONS REG ON METER /** 1) MN: A255706 SN: 0120565, *TAP: SIZE: A LOC: 52 FEET FROM P LINE AT IBERVILLE, *MB: CODE: OOOO LOC: 52' P.L. IBERVILLE ****/ | 2017-09-26 | EXCAVATED 4 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INLET SERVICE NO CON REG ON METER MADE REPAIR ON INELT BACKFILLED JOB WITH RIVERSAND/COLDMILL
201701224401 | 2017-09-13 | LEAD | 514 | FRENCHMEN | DECATUR | WOLK | ML METERLEAK MTR#D005097 ACCT#145494-485581 CONS REG ON METER /** 1) MN: D005097 SN: 0001386, *TAP: SIZE: D LOC: 98 FEET FROM P LINE AT DECATUR, *MB: CODE: AEN2 LOC: ON FRENCHMEN 138FT FROM DECATUR ****/ | 2017-09-25 | TIGHTEN 1 1/2 UNION TO STOP LEAK
201701226001 | 2017-09-13 | LEAD | 3337 | ST ANN | HAGAN AV | WILK | ML- METER WAS CHANGED, CUSTOMER STATES METER IS STILL LEAKING METER# A 425923 ACCT#149346-520484 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A268798 SN: 0026730, *TAP: SIZE: B LOC: 284 FEET FROM P LINE AT HAGAN AVE, *MB: CODE: CDLM LOC: HAGAN/MOSS METER ON ST ANN 284 FT FROM PL N HAGAN ****/ | 2017-09-26 | EXCAVATED 4 X 4 MUD PLOT IN GARDEN FOUND LEAK ON 5/8 INLET SERVICE MADE REPAIR ON INELT BACKFILLED JOB WITH RIVERSAND
201701227301 | 2017-09-13 | LEAD | 1023 | 6TH | MAGAZINE | WILK | ML METER LEAK ACCT# 128642-540110 METER# A152562 BAD BLEEDER VALVE FLOODING GUTTER /** 1) MN: A152562 SN: 0056065, *TAP: SIZE: A LOC: 140 FEET FROM P LINE AT MAGAZINE, *MB: CODE: CEL1 LOC: LINE WITH HYDT CRB 140' P.L. MAGAZINE ****/ DOTTIE READY 3-1-18 EXP 3-21-18 | 2018-03-06 | ARRIVED ON JOB EXCAVATED IN DRIVEWAY FOUND 5/8 METER BOX COCK LEAKING MADE REPAIRS AND BACKFILLED JOB COMPLETE. TIED INTO LEAD
201701230801 | 2017-09-13 | LEAD/PLASTIC | 305 | HOMER | BROOKLYN | WILK | WM LEAK IN SIDEWALK INLET SERVICE LEAK AT VACANT SERVICE /** 1) MN: A258765 SN: 0082880, *TAP: SIZE: B LOC: 48 FEET FROM P LINE AT BROOKLYN AVE, *MB: CODE: CDL LOC: ON HOOMER 48FT FROM BROOKLYN 6FT OUTSIDE ****/ | 2017-10-11 | EXCAVATED METER BOX AND FOUND COCK LEAKING ON INLET REPLACED BOX COCK AND HAND WHEEL NEED TO REMOVE LEAD
201701231101 | 2017-09-13 | LEAD/PLASTIC | 2020 | VALENTINE CT | GEN MEYER AV | WILK | ML-METER LEAK INLET SERVICE LEAK IN GRASS AT CURB /** 1) MN: A242151 SN: 0140808, *TAP: SIZE: C LOC: 427 FEET FROM P LINE AT EASTER LANE, *MB: CODE: CD2 LOC: 427FT FROM P.L. EASTER LANE ****/ | 2017-11-13 | EXCAVATED AND REPAIRED INLET SERVICE ALSO RAISED METER BOX TO GRADE
201701231201 | 2017-09-14 | LEAD | 4909 | PERRIER | UPPERLINE | WILK | ML- METER LEAK METER#A191317 ACCT#120695-589191 /** 1) MN: A191317 SN: 0036580, *TAP: SIZE: A LOC: 65 FEET FROM P LINE AT UPPERLINE, *MB: CODE: BD LOC: 65FT FROM UPL UPPERLINE ON PERRIER ****/ EXAMINE FOR POSSIBLE ABANDON INLET SERVICE IN FRONT OF THE HOUSE NEAR THE SIDEWALK. | 2018-03-17 | EXCAVATED IN MUDPLOT. REPAIR 5/8 STOP & WASTE LEAD LINE. DRESS UP WITH RIVERSANDREFER TO ZONE 3 TO TAKE LEAD LINE FROM WATER MAIN TO METER BOX
201701231202 | 2018-03-17 | LEAD | 4909 | PERRIER | UPPERLINE | WSNR | REFER TO ZONE 3 TO TAKE LEAD LINE FROM WATER MAIN TO METER BOX /** 1) MN: A191317 SN: 0036580, *TAP: SIZE: A LOC: 65 FEET FROM P LINE AT UPPERLINE, *MB: CODE: BD LOC: 65FT FROM UPL UPPERLINE ON PERRIER ****/ DOTTIE READY 6-4-18 EXP 6-24-18 | 2018-06-20 | EXCAVATED OVER 6'' WATER MAIN . REMOVE LEAD FROM PROPERTY TO WATER MAIN INLET AD OUTLET SERVICE .REPLACE WITH 3/4 PLASTIC FROM WATER MAIN TO PROPERTY . RAISE METER4 BOX TO GRADE . MADE 5' X 5' CUT IN STREET AND 3' X 5' CUT IN THE SIDEWALK NEED TO PUT BRICKS BACK IN SIDEWALK WHEN THEY COME PAVE IT.
201701232701 | 2017-09-14 | LEAD/PLASTIC | 3002 | GENTILLY BL |  | WILK | MI- LEAK ON THE SIDEWALK INLET SERVICE LEAK IN MANHOLE FLOODING SIDEWALK AND REPLACE LEAD SERVICE STREET FOUND 1 BARREL ON SITE /** 1) MN: E006254 SN: 0102725, *TAP: SIZE: C LOC: 97 FEET FROM P LINE AT TOURO, *MB: CODE: OOO LOC: IN FRONT OF BLDG 95' P.L. TOURO 4' OUTSIDE 11' ****/ | 2017-10-08 | EXCAVATED A 10X5 SIDEWALK CUT TO REPLACE 4 FEET OF 6"SEWER PIP AND REPAIR BROKEN 2 " INLET SERVICE- P S REMOVED LEAD FROM STREET TO METER REPLACED WITH PVC
201701233001 | 2017-09-14 | LEAD | 3107 | JENA |  | WOLK | LEAKING BEHIND THE WHEEL UNABLE TO LEAVE METER ON CUSTOMER IS WAITING ON WATER A-426590 OUT SERVICE NEED TO BE UPDATED LOCATION #139528 ********L.THOMPSON @ 11:22AM******** OUTLET SERVICE LEAK BEHIND HANDWHEEL /** 1) MN: A274726 SN: 0070426, *TAP: SIZE: B LOC: 31 FEET FROM P LINE AT DERBIGNY S, *MB: CODE: BEL2 LOC: ON JENA, 34' FROM L.S.P.L. SO. DERBIGNY ****/ | 2017-09-14 | ARRIVED ON SITE FOUND LEAK 5/8 CURB COCK ,EXCAVATED IN HOLE OVER INLET FOUND LEAD INLET REPLACED WITH NEW CURB COCK AND ALSO REPLACED BROKEN WATER METER REQUEST CONTINUATION TO BACKFILL 5 X 5 SIDEWALK CEMENT CUT...JOB CONTINUED OLD METER A430189 FACTORY: 16355778 MAKE: HERSEY READ: 333
201701233701 | 2017-09-14 | LEAD | 137 | S RENDON | CLEVELAND AV | WMTLK | LOCATIONID#101481-701507 METER#A413717 LEAK INSIDE METERBOX /** 1) MN: SN: 0004048, *TAP: SIZE: B LOC: 175 FEET FROM P LINE AT CLEVELAND AVE, *MB: CODE: CDM4 LOC: ON S RENDON 175FT FROM PL CLEVELAND AVE ****/ | 2017-09-25 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 CURB COCK BACKFILLED AREA
201701234101 | 2017-09-14 | LEAD/PLASTIC | 601 | WASHINGTON AV | ST THOMAS | WOLK | ML METER LEAK METER# A338690 ACCT# 150065-53972 OUTLET SERVICE LEAK BEHIND HAND HANDWHEEL FDLOODING GUTTER /** 1) MN: A338690 SN: 0048593, *TAP: SIZE: B LOC: 58 FEET FROM P LINE AT WASHINGTON AVE, *MB: CODE: BD LOC: ON ST THOMAS 56FT FROM WASHINGTON ****/ | 2017-10-16 | EXCAVATED METER BOX AND BROKE SECTION OF SIDEWALK TO REPAIR LEAK ON HAND WHEEL BACKFILLED WITH SAND AND COLDMILL
201701235901 | 2017-09-14 | LEAD/PLASTIC | 2843 | HYMAN PL |  | WOLK | INLET AND OUTLET NOT LIINING UP LEAKING PLEASE REPAIR ASAP CUSTOMER IS COMPLAINING LOCATION #230277 EXAMINE OUTLET SERVICE FOR LEAK AT PROPERTY LINE AREA SATURATED /** 1) MN: A290436 SN: 0135734, *TAP: SIZE: B LOC: 298 FEET FROM P LINE AT MAC ARTHUR BLVD, *MB: CODE: BDL LOC: 298FT FROM P.L. MAC ARTHUR ****/ | 2017-10-30 | EXCAVATED AND REPLACED OUTLET SERVICE FROM METER BOX TO PROPERTY
201701239301 | 2017-09-15 | LEAD | 3701 | N CLAIBORNE AV |  | WMBK | INLET AND OUTLET NOT LINING UP. OUTLET IS LEAKING. WATER WAS LEFT OFF AND CUSTOMER IS WAITING FOR SERVICE TO BE RESTORED. METER A426459 LOC ID 146477 ************M.DAIGLE @ 12:27PM************* BROKEN METER BOX CASING UNABLE TO SET METER CUSTOMER OUT OF WATER /** 1) MN: A306471 SN: 0095923, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: ADH6 LOC: ON INDEPENDENCE 45' FROM P L N CLAIBORNE AVE ****/ | 2017-09-18 | EXCAVATED 3 X 3 MUD PLOT MADE REPAIR ONOUTLET SERVICE LINE AND REPLACED 5/8 METER BOX COCK BACKFILLED AND CLEANED THE AREA
201701239501 | 2017-09-15 | LEAD | 2235 | S CARROLLTON AV | NERON PL | WILK | ML METER LEAK METER # B040757 ACCOUNT # 110941-580274 INLET SERVICE LEAK IN GRASS NEAR SIDEWALK /** 1) MN: B027230 SN: 0012122, *TAP: SIZE: B LOC: 91 FEET FROM P LINE AT CARROLLTON AVE S, *MB: CODE: AFHO LOC: 60FT FROM SIDE ENTRANCE ON NERON 88FT FR PL ****/ | 2017-10-05 | EXAMINE AND FOUND LEAK ON CRUB COCK EXCAVATED MUD PLOT AND TREE ROOTS BY HAND ALSO MADE 4X4 CUT TO SIDEWALK BACK FILLED WITH SAND AND COLDMILL CUSTOMER ALSO REQUISTED THAT LEAD BE REMOVED TO MAIN AND RE-ROUTE METER BOX TO OTHER SIDE TOSIDEWALK AND RASE TO GRADE OLD METER B040757 FACT:15501189 MAKE: HERSEY READ: 1653
201701240501 | 2017-09-15 | LEAD/PLASTIC | 3343 | LANCASTER | BERKLEY DR | WMTLK | MI- METER LEAK MTR# A310192 ACCT# 228166-420307 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A310192 SN: 0120633, *TAP: SIZE: B LOC: 345 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: ADK LOC: ON LANCASTER 345FT FROM P.L. BERKLEY ****/ | 2017-11-01 | EXCAVATED METER EXPOSED INLET OUT LED SERVICE OBSERVED LEAK ON INLET SERVICE COCK REPAIRED BAD HANDWHEEL RAISED TO GRADE AND DRESSED UP AND BACKFILLED
201701240601 | 2017-09-15 | LEAD | 3016 | PARIS AV | ABUNDANCE | WILK | ML: METER LEAK, LEAK ON METER, ACCT # 118710-492733, METER # A406341 EXAMINE INLET SERVICE FOR A LEAK WITH CONSTANT REGISTRATION. ***FOUND OFF LEFT OFF*** /** 1) MN: A147041 SN: 0062071, *TAP: SIZE: A LOC: 139 FEET FROM P LINE AT ABUNDANCE, *MB: CODE: BFK2 LOC: ON PARIS AVE.,144' FROM P.L. ABUNDANCE ****/ | 2017-09-26 | EXAMINED JOB FOUND NO LEAK ON CONSTRANT METER WAS ON
201701240701 | 2017-09-15 | LEAD | 2226 | PAINTERS | N TONTI | WILK | MI- LEAK IN SIDEWALK CHANGED FROM 2238 PAINTERS INLET SERVICE LEAK NO METER IN BOX /** 1) MN: A273864 SN: 0103574, *TAP: SIZE: A LOC: 113 FEET FROM P LINE AT TONTI N, *MB: CODE: BO2 LOC: 112FT FROM PL N TONTI 10FT LPL CURB ****/ | 2017-09-29 | EXCAVATED 4 X 2 MUD PLOT METER BOX COCK 5/8 INCH REPLACED BACKFILLED AND CLEANED AREA UP.
201701241901 | 2017-09-15 | LEAD/PLASTIC | 1201 | BELLEVILLE | DE ARMAS | WMTLK | WM - LEAK ON THE SIDEWALK EXAMINE INLET/OUTLET SERVICE FOR LEAK AT SIDEWALK /** 1) MN: A302006 SN: 0113969, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT BELLEVILLE, *MB: CODE: BD LOC: ON DE ARMAS, 48' FROM P.L. BELLEVILLE, 8' OUTSIDE ****/ | 2017-10-13 | EXCAVATED METER BOX AND FOUND LEAK ON OUTLET UNDER SIDE WALK BROKE SIDEWALK WITH SLEDGE HAMMER AND RENEWED ENTIRE OUTLET BACKFILL AND DRESS UP NEEDED
201701243301 | 2017-09-16 | LEAD/PLASTIC | 748 | CAMP | JULIA | WILK | MI SEE WHY NO WATER ACCT# 134654-530014 MTR# B030562 ******1ST AM****** INLET SERVICE LEAK CAUSING POOR PRESSURE ALSO UNABLE TO VERIFY DUE TO BUSINESS CLOSE /** 1) MN: B030562 SN: 0065424, *TAP: SIZE: B LOC: 102 FEET FROM P LINE AT JULIA, *MB: CODE: AELM LOC: ON CAMP 102' FROM PL JULIA ** 2) MN: SN: 0000000, *TAP: SIZE: C LOC: 101 FEET FROM P LINE AT JULIA, *MB: CODE: AEMN LOC: ON CAMP 101' FROM LSPL OF JULIA THERE IS 1 MORE NOT LISTED. ****/ | 2017-09-20 | BROKE THE SIDEWALK AND EXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOB SITE
201701243801 | 2017-09-17 | LEAD/PLASTIC | 717 | FERN | MAPLE | WLPR | PP- POOR PRESSURE ACCT# 122121-584394 MTR# A364959 **********1ST AM********** EXAMINE INLET SERVICE FOR POOR PRESSURE /** 1) MN: A243572 SN: 0040085, *TAP: SIZE: A LOC: 121 FEET FROM P LINE AT MAPLE, *MB: CODE: AFL LOC: ON FERN ST 139' FROM RPL MAPLE ST ****/ | 2017-09-20 | MADE A 5 X 6 DRIVEWAY CUT EXCAVATED AND MADE REPAIRS ONA 5/8 LEAD LINE OUTLET PLASTIC REFER THAT DRIVE WAY CUT TO PAVING. JOB COMPLETE. JEG
201701244701 | 2017-09-18 | LEAD | 1222 | AMELIA |  | WILK | ML- METER LEAK ACCT# 112991-557676 MTR# A376817 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A274759 SN: 0034714, *TAP: SIZE: A LOC: 136 FEET FROM P LINE AT CHESTNUT, *MB: CODE: __ LOC: 137' P.L. CHESTNUT ****/ DOTTIE READY 2-1-18 EXP 2-21-18 | 2018-02-07 | EXAMINE JOB AND PUMP WATER OUT METER BOX AND FOUND BAD METER COCK AND MADE A 3 X 3 CUT ON SIDEWALK AND EXCAVATED ON SIDEWALK AND EXCAVATED ON SIDEWALK AND MADE REPAIRS TO BAD CURB COCK.TIE COCK BACK ONTO LEAD LINE.
201701245201 | 2017-09-18 | LEAD | 2601 | CAFFIN AV | LAW | WILK | MI- LEAK AT THE SIDEWALK INLET SERVICE LEAK NEAR DRIVEWAY NEAR MUDPLOT /** 1) MN: A281762 SN: 0163041, *TAP: SIZE: B LOC: 27 FEET FROM P LINE AT LAW, *MB: CODE: __ LOC: ON CAFFIN 27FT FROM PL LAW 3FT INSD CURB ****/ | 2017-09-28 | EXCAVATED 3 X 2 MUD PLOT REPLACED 5/8 METER BOX COCK AND MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201701245301 | 2017-09-18 | LEAD/PLASTIC | 1949 | LAFAYETTE | BOLIVAR | WILK | WM-LEAK IN SIDEWALK **************1ST AM*************** INLET SERVICE LEAK IN ROCK BED INFRONT ADDRESS FLOODING AREA 09/18/17 CUSTOMER STATES THAT LEAK IS GETTING INTO HIS BUSINESS PER SR#12815195 (AJR) /** 1) MN: A310749 SN: 0173839, *TAP: SIZE: A LOC: 174 FEET FROM P LINE AT BERTRAND, *MB: CODE: BEMW LOC: ON LAFAYETTE,60.5' FROM P.L. BERTRAND ****/ | 2017-09-19 | EXCAVATED ON THE INLET SERVICE AND REPAIR THEN WE BACKFILL AND CLEAN UP JOB SITE AND THEN WE BARRICADE JOB SITE OFF TO COMEBACK AND PUT LIME STONE ON JOB SITE...JOB CONTINUED
201701246001 | 2017-09-18 | LEAD/PLASTIC | 812 | DIANA |  | WILK | ML- METER LEAK MTR# A379451 ACCT# 225456-402572 INLET SERVOCE LEAK IN MUDPLOT 09/22/17 LEAK GETTING WORSE, FLOODING AREA PER SR#12815646 (AJR) /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-11-10 | EXCAVATED METER EXPOSE BOTH INLET AND OUTLET LINES OBSERVED ON OUTLET LINE REPAIRED AND BACKFILLED
201701246101 | 2017-09-18 | LEAD/PLASTIC | 321 | WHITNEY AV | PELICAN | WOLK | MI- LEAK BETWEEN SIDEWALK & CURB OUTLET SERVICE LEAK ON SIDEWALK SIGNS OF PREVIOUS REPAIRS 10/04/17 NOW CAUSING POOR PRESSURE PER SR#12816861 (AJR) 10/06/17 CUSTOMER STILL HAVING POOR PRESSURE PER SR#12817108 (AJR) /** 1) MN: A305601 SN: 0102090, *TAP: SIZE: B LOC: 141 FEET FROM P LINE AT PELICAN AVE, *MB: CODE: BD LOC: ON WHITNEY 161FT FROM PELICAN 10FT OUTSIDE ****/ | 2017-10-30 | EXAMINED METER FOUND LEAK ON INLET REPAIRED LEAK PRESSURE IS GOOD
201701246201 | 2017-09-18 | LEAD/PLASTIC | 1403 | PTOLEMY | LEBOUEF | WMTLK | LOCATIONID#301972-707417 METER#A428852 METERBOX OVERFLOWING /** 1) MN: A258241 SN: 0146286, *TAP: SIZE: B LOC: 44 FEET FROM P LINE AT LEBOEUF, *MB: CODE: CDLM LOC: ON PTOLEMY 44FT FROM LEBOUEF 6FT OUTSIDE ****/ | 2017-11-02 | EXCAVATED METER EXPOSED INLET AND OUTLET OBSERVED LEAK ON INLET REPAIRED LEAK BACKFILLED AND DRESSED UP WITH SAND
201701246301 | 2017-09-18 | LEAD | 839 | SPAIN | BURGUNDY | WMTLK | LOCATIONID#119963-480646 METER#A284407 LEAK INSIDE METERBOX /** 1) MN: A293356 SN: 0034092, *TAP: SIZE: B LOC: 22 FEET FROM P LINE AT SPAIN, *MB: CODE: BHL LOC: ON BURGUNDY 21FT FROM PL SPAIN 2FT OUTSIDE PL 8FT ****/ | 2017-09-28 | EXAMINED JOB AT ABOVE LOCATION FOUND 5/8 HAND WHEELWAS DAMAGE REPLACED HANDWHEEL + WASHER NO LEAK JOB COMPLETE
201701246501 | 2017-09-18 | LEAD | 911 | MANDEVILLE | BURGUNDY | WILK | ***DO NOT CREATE RESTORATION WORK ORDER: DPW ALREADY HAS THE RESTORATION WORK ORDER FROM PREVIOUS JOB*** WM - LEAK ON THE SIDEWALK INLET SERVICE LEAK IN OLD CUT /** 1) MN: A249571 SN: 0051337, *TAP: SIZE: A LOC: 85 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CDM LOC: ON MANDEVILLE,83' FROM L.S.P.L. BURGUNDY ****/ | 2017-09-28 | EXCAVATED 4 X 4 MUD PLOT IN SIDEWALK FOUND LEAK ON INLET SERVICE MADE REPAIR ON INELT BACKFILLED JOB WITH RIVERSAND
201701248601 | 2017-09-18 | LEAD | 6361 | PAULINE DR |  | WMTLK | ML- METER LEAK MTR # A425189 ACCT # 301184 -704150 EXAMINE INLET/OUTLET SERVICE FOR LEAK AREA SATURATED SIDEWALK FLOODED /** 1) MN: A255642 SN: 0119291, *TAP: SIZE: B LOC: 432 FEET FROM P LINE AT FRANKFORT, *MB: CODE: CDN LOC: ON PAULINE 432FT FROM FRANKFORT ****/ | 2017-09-29 | EXAMINE LOCATION FOUND INLET SERVICE LEAKING. EXXCAVATED DOWN ON INLET SERVICE. FOUND A LEAD SERVICE. MADE REPAIRS BY REPLACING 2FT OF SERVICE & METER BOX COCK, WASHERS. BACKFILLED DRESS UP. REPLACED METER BECAUSE IT WAS CHOKE. *******OLD METER INFO**************** METER:A425189 FAC:16310201 MAKE:HERSEY READ:5
201701251001 | 2017-09-19 | LEAD | 206 | BOURBON | IBERVILLE | WILK | CUT WATER SERVICE, (1 1/2 INCH( CUT BY BOH BROTHERS CONSTRUCTION CO. CUSTOMER HAVE VERY POOR PRESSURE) ***********DAMAGE CLAIM********** SWB NEEDS TO MAKE THE REPAIRS (PER SWB INSPECTOR CHRIS FONTAN) /** 1) MN: E004673 SN: 0087592, *TAP: SIZE: E LOC: 57 FEET FROM P LINE AT IBERVILLE, *MB: CODE: OOOO LOC: IN MANHOLE ON BOURBON, 57' FROM P.L. IBERVILLE, ****/ | 2017-09-19 | MADE REPAIR ON 1 INCH SERVICE LINE
201701252101 | 2017-09-19 | LEAD/PLASTIC | 1635 | FOY | BRUXELLES | WOLK | **********PICK UP********** OUTLET SERVICE LEAK IN METER BOX FROM HANDWHEEL /** 1) MN: A290979 SN: 0101039, *TAP: SIZE: A LOC: 267 FEET FROM P LINE AT PARIS AVE, *MB: CODE: BDK2 LOC: ON FOY 267' FROM PL PARIS AVE 7' OUTSIDE PL 2' INS ****/ | 2017-09-22 | EXCAVATED A 3 X 4 TRENCH IN MUDPLOT THROUGH DEBRIS OVER A 5/8 OUTLET SERVICE LEAK PLASTIC INLET & LEAD OUTLET. REPLACED THE OUT FROM METERBOX TO PROPERTY BACKFILLED . JEG
201701252501 | 2017-09-19 | LEAD/PLASTIC | 3736 | LANG | GEN DE GAULLE DR | WMTLK | ML - METER LEAK MTR # A391842 ACCT # 229827-415091 EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A243721 SN: 0132631, *TAP: SIZE: B LOC: 52 FEET FROM P LINE AT GEN DE GAULLE DR, *MB: CODE: ADLM LOC: ON LANG 52' FROM DPL GEN DE GAULLE DR 3' INSIDE CU ****/ | 2017-11-06 | EXCAVATED METER BOX EXPOSED BOTH LINE REMOVED LEAD LINE TO PROPERTY REPLACED BOX COCK AND HAND WHEEL FOUND LEAK ON OUTLET NEED TO BE DRESSED ALSO RAISED TO GRADE
201701252901 | 2017-09-19 | LEAD | 2106 | PAUGER | N VILLERE | WMTLK | WM - LEAK ON THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-10-03 | EXAMINED INLET FOR LEAK WASHERS WAS BAD CHANGED WASHERS AND STOP LEAK METER:A133638 FACTORY: 18707400 MAKE:ROCKWELL READ:3766
201701253601 | 2017-09-19 | LEAD | 2135 | MANDEVILLE | N MIRO | WMTLK | LOCATIONID#134012-483997 METER#A401215 LEAK INSIDE METERBOX /** 1) MN: A330562 SN: 0065289, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT MIRO N, *MB: CODE: BDN1 LOC: ON MANDEVILLE,48' FROM P.L. NO. MIRO ****/ | 2017-09-25 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 CURB COCK BACKFILLED AREA
201701253901 | 2017-09-19 | LEAD/PLASTIC | 3904 | GEN MEYER AV | GEN COLLINS AV | WMTLK | LOCATIONID#226397-410530 METER#A330625 LEAK INSIDE METERBOX /** 1) MN: A330625 SN: 0123494, *TAP: SIZE: A LOC: 38 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: AGHL LOC: ON LINCOLN 38FT FROM P.L. GEN MEYER ****/ | 2017-11-03 | EXCAVATED METER EXPOSED BOTH INLET AND OUTLET OBSERVED LEAK ON OUTLET LINE REPAIRED BACKFILLED DRESSED UP TO PROPERTY
201701254001 | 2017-09-19 | LEAD/PLASTIC | 3812 | GEN MEYER AV | GEN COLLINS AV | WMTLK | LOCATIONID#226403-410531 METER#A135969 LEAK INSIDE METERBOX /** 1) MN: A135969 SN: 0123875, *TAP: SIZE: B LOC: 146 FEET FROM P LINE AT RICHLAND RD, *MB: CODE: BDM5 LOC: MTR ON GEN MEYER 146FT FRM PL RICHLAND ****/ | 2017-11-03 | EXCAVATED METER OBSERVED LEAK ON WASHER BACKFILLED AND CALLED FOR DRESS UP
201701254401 | 2017-09-19 | LEAD/PLASTIC | 1907 | ODEON AV | HORACE | WMTLK | LOCATIONID#235984-407973 METER#A241689 METERBOX OVERFLOWING /** 1) MN: A241689 SN: 0164731, *TAP: SIZE: A LOC: 13 FEET FROM P LINE AT CANAL, *MB: CODE: __ LOC: ON ODEON 13FT FROM PL CANAL 9FT OUTSIDE PL 3' INSI ****/ | 2017-10-09 | ARRIVED ON JOB SITE EXAMINED METER EXACAVTED BY HAND FOUND LEAK ON INLET AND A BROKE HAND WHEEL REPAIRED INLET AND REPALCED HAND WHEEL RAISED METER TO GRADE
201701254601 | 2017-09-19 | LEAD/PLASTIC | 1910 | ELIZARDI BL | WALL BL | WMTLK | LOCATIONID#234486-471519 METER#A355234 AREA FLOODED,LEAK INSIDE METERBOX /** 1) MN: C027876 SN: 0143471, *TAP: SIZE: C LOC: 101 FEET FROM P LINE AT WALL BLVD, *MB: CODE: BDM2 LOC: ON ELIZARDI 102' FROM PL WALL BLVD 5' OUTSIDE PL ****/ | 2017-10-27 | EXAMINED JOB FOR LEAK FOUND LEAK ON OUTLET MADE REPAIR FROM INLET TO PROPERTY BACKFILLED AND CLEANED JOB SITE
201701254701 | 2017-09-19 | LEAD/PLASTIC | 1141 | SOUTHLAWN BL | DIANA | WMTLK | LOCATIONID#227050-406137 METER#A388682 LEAK INSIDE METERBOX /** 1) MN: A298745 SN: 0123656, *TAP: SIZE: __ LOC: 261 FEET FROM P LINE AT LANE, *MB: CODE: CDL LOC: ON SOUTHLAWN BLVD., 264' FROM P.L. LANE, 5' OUT- ****/ | 2017-11-09 | EXCAVATWED METER OBSERVED LEAK ON BOX COCK EXCAVATED INLET AND OUTKLET LINE OBSERVED LEAD ON OUTLET EXCAVATED TO PROPERTY REPLACE LEAD LINE WITH PLASTIC BACKFILLED DRESS UP NEEDED
201701254801 | 2017-09-19 | LEAD/PLASTIC | 1641 | PACE BL | LAWRENCE ST | WMBK | LOCATIONID#228706-406258 METER#A375145 METER CASING BROKEN,PLEASE REPLACE /** 1) MN: A271342 SN: 0123434, *TAP: SIZE: B LOC: 337 FEET FROM P LINE AT LAWRENCE, *MB: CODE: ADLM LOC: ON PACE BLVD., 337' FROM P.L. LAWRENCE, 12' OUT- ****/ | 2017-10-17 | EXCAVATED OLD METER BOX RAISED TO GRADE CHANGED HAND WHEEL REPLACE UPPER CASING BACKFILLED REPLACED WASHERS
201701255001 | 2017-09-19 | LEAD | 2521 | PAINTERS | N DORGENOIS | WMTLK | MI RAISE METER TO GRADE METER # A146341 ACCOUNT # 184193-485177 WATER METER BELOW GRADE /** 1) MN: A146341 SN: 0136276, *TAP: SIZE: B LOC: 171 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CDMN LOC: 171FT PL N DORGENOIS 8' OUTSIDE 2' INSIDE CURB ****/ | 2017-09-29 | EXCAVATED 3 X 3 MUD PLOT RAISE METER BOX TO GRADE BACKFILL AND CLEANED THE AREA
201701255401 | 2017-09-19 | LEAD | 1721 | FRANCE | N DERBIGNY | WOLK | INLET AND OUTLET NOT LINING UP. CAUSING LEAK. UNABLE TO LEAVE WATER ON. PLEASE REPAIR METER A426785. LOC ID 302852 METER BOX CASING SHIFTED. (RENOVATED PROPERTY - NO NONE LIVES THERE) (C) /** 1) MN: A329102 SN: 0175486, *TAP: SIZE: A LOC: 167 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: DL7 LOC: ON FRANCE 167' FROM PL OF DERBIGNY N ****/ | 2017-10-03 | EXCAVATED 5 X 2 SIDEWALK RAISE METER BOX TO GRADE ALSO SET ONE METER BOX COMPLETE BACKFILL AND CLEANED THE AREA
201701255701 | 2017-09-19 | LEAD | 1720 | URSULINES AV | N DERBIGNY | WILK | ML-METER LEAK ACCT#116013-525673 METER#A240336 INLET INSIDE METER BOX. /** 1) MN: A240336 SN: 0020779, *TAP: SIZE: A LOC: 117 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: ADLN LOC: ON URSULINES 117FT FROM DERBIGNY N ****/ | 2017-09-25 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 CURB COCK BACKFILLED AREA
201701256801 | 2017-09-20 | LEAD/PLASTIC | 24 | CHATHAM DR |  | WILK | MI LEAK ON SIDEWALK INLET SERVICE LEAK IN THE MUD PLOT FLOODING GRASS /** 1) MN: A269681 SN: 0117025, *TAP: SIZE: A LOC: 256 FEET FROM P LINE AT CHASE DR., *MB: CODE: BDK LOC: ON CHATHAM DR., 254.5' FORM P.L. CHASE DR.,8.6' ****/ | 2017-12-30 | EXCAVATED IN MUDPLOT TO LOCATE AND RAISE METER BOX TO GRADE ALSO RENEWED OUTLET SERVICE LINE. FOUND LEAD ON INLET NEED TO BE REMOVED AT LATER DATE. JEG
201701258301 | 2017-09-20 | LEAD | 1202 | SONIAT | COLISEUM | WILK | MI- CUST SERVICE GREADY CONSTRUCTION 504-874-8583. * NOT SURE IF SERVICE WAS INTERRUPTED* **********DAMAGE CLAIM********** ZONE 3 M ROBINSON @ 11:38 CUT INLET SERVICE BY GREADY CONSTRUCTION, ***UNKNOWN IF ANYONE OUT OF WATER /** 1) MN: A277515 SN: 0017444, *TAP: SIZE: A LOC: 77 FEET FROM P LINE AT SONIAT, *MB: CODE: AFHT LOC: ON COLSIEUM 76.3FT FROM SONIAT ****/ | 2017-09-19 | ARRIVED ON SITE FOUND CUT SERVICE ON 3/4 LEAD INLET SERVICE MADE REPAIR TO STOP LEAK.FORCE ACCOUNT TO GREADY CRAWFORD CONSTUCTION COMPANY.
201701259301 | 2017-09-20 | LEAD/PLASTIC | 337 | N MURAT | BIENVILLE | WOLK | MI- CHECK FOR LEAK AT PROPERTY LINE NEED TO REMOVE TWO PALM TREES TO MAKE REPAIRS EXAMINE OUTLET SERVICE FOR LEAK CON REG, NO VISIBLE STOP AND WASTE VALVE /** 1) MN: A323751 SN: 0176353, *TAP: SIZE: B LOC: 258 FEET FROM P LINE AT BIENVILLE, *MB: CODE: CDL LOC: ON MURAT 258' FROM PL OF BIENVILLE ****/ | 2017-12-28 | EXCAVATED IN TREE ROOTS AND RENEWED A 3/4 OUTLET SERVICE WITH PLASTIC LEAD ON THE INLET JOB COMPLETE. JEG **********OLD METER INFO********* METER:A323751 FAC:53375126 MAKE:SENSUS READ:24550
201701260401 | 2017-09-21 | LEAD/PLASTIC | 1565 | MURL | SOCRATES | WMBK | LOCATION ID# 226064 METER # A406101 FOUND A LEAK INSIDE METER BOX CASING CONS REGISTION ON METER PROPERTY OCC /** 1) MN: A296386 SN: 0129409, *TAP: SIZE: B LOC: 468 FEET FROM P LINE AT SOCRATES, *MB: CODE: BD LOC: 470FT FROM P.L. SOCRATES ****/ | 2017-10-17 | EXAMINED METER BOX USE HAND PUMP TO REMOVE WATER FROM CASING OBSERVED LEAK ON HAND WHEEL EXCAVATED METER BOX AND REPLACED HAND WHEEL AND WASHERS
201701261401 | 2017-09-21 | LEAD/PLASTIC | 326 | VALLETTE | PELICAN | WMTLK | ML METER LEAK ACCOUNT# 225234-400807 METER# A352161 EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A305337 SN: 0069340, *TAP: SIZE: B LOC: 163 FEET FROM P LINE AT ALIX, *MB: CODE: BDK LOC: ON VALLETTE 163FT FROM ALIX ****/ | 2017-10-24 | EXCAVATED METER RAISED TO GRADE RENEWED LEAD TO PROPERTY AND REPLACED WITH PLASTIC TUBING
201701261901 | 2017-09-21 | LEAD/PLASTIC | 1800-02 | HASTINGS PL | MAGAZINE | WILK | LEAK BETWEEN SIDEWALK AND STREET CONTACT UPON ARRIVAL AT 504-352-7380 INLET SERVICE LEAK IN AN ASPHALT STREET NEAR CURB /** 1) MN: A236290 SN: 0013500, *TAP: SIZE: C LOC: 78 FEET FROM P LINE AT MAGAZINE, *MB: CODE: AEH3 LOC: 1ST METER SIDE ST ON FELICITY 79' P.L. MAGAZINE ****/ | 2017-11-28 | BROKE COCNCRETE WITH MAUL EXCAVATED METER BOX EXPOSED METER LEAK FOUND ON INLET SERVICE COCK INSTALLED METER OKLACED BARRELS AROUND SITE REPLACED LEAD LINE TO PROPERTY WITH PLASTIC THEN RAISED TO GRADE
201701262001 | 2017-09-21 | LEAD | 540 | AUDUBON | DOMINICAN | WILK | ML METER LEAK ACCT# 114233-585398 METER# B026267 INLET SERVICE LEAK BAD BLEEDER VALVE FLOODING GRASSY AREA METER SITS ON DOMINICAN 10/04/17 LEAK GETTING WORSE PER SR#12816930 (AJR) /** 1) MN: B026267 SN: 0016890, *TAP: SIZE: B LOC: 60 FEET FROM P LINE AT AUDUBON, *MB: CODE: ADH6 LOC: ON DOMINICAN 59FT FROM PL AUDUBON 7' OUTSIDE PL 1 ****/ DOTTIE READY 12-20-17 EXP 1-9-17 | 2018-03-05 | ARRIVED ON JOB EXCAVATED IN SIDEWALK FOUND 3/4 METER BOX LEAKING MADE REPAIRS AND BACKFILLED JOB COMPLETE TIED INTO LEAD
201701263301 | 2017-09-21 | LEAD | 1923 | WASHINGTON AV | DANNEEL | WMRE | SERVICE BURIED. PLEASE LOCATE AND SET 5/8 METER. LOC ID 117663 LOCATE & MARK METR /** 1) MN: A338959 SN: 0032265, *TAP: SIZE: A LOC: 123 FEET FROM P LINE AT DANNEEL, *MB: CODE: CDN2 LOC: CURB DRIVE - 102' P.L. DANNEEL ****/ DOTTIE READY 10-2-17 EXP 10-22-17 | 2017-10-05 | EXPOSED METER AT ABOVE LOCATION FOUND METER A368774 ALREADY SET AND ON
201701263302 | 2017-10-22 | LEAD | 1923 | WASHINGTON AV | DANNEEL | WMRE | /** 1) MN: A338959 SN: 0032265, *TAP: SIZE: A LOC: 123 FEET FROM P LINE AT DANNEEL, *MB: CODE: CDN2 LOC: CURB DRIVE - 102' P.L. DANNEEL ****/ | 2017-10-21 | EXCAVATED IN MUD PLOT LOCATED RAISED 5/8 INCH METER BOX TO GRADE METER BOX ALREADY HAD METER
201701263801 | 2017-09-21 | LEAD | 2620 | N ROCHEBLAVE | ARTS | WMTLK | MI-LEAK AT THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER IN LOWLINE AREA /** 1) MN: A303779 SN: 0075627, *TAP: SIZE: A LOC: 139 FEET FROM P LINE AT ARTS, *MB: CODE: ADL1 LOC: ON NO. ROCHEBLAVE, 139' FROM U.R.P.L. ARTS ****/ | 2017-09-25 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201701264401 | 2017-09-21 | LEAD | 1441 | FRANCE |  | WILK | ML- METER LEAK ACCT#203966-431101 METER#A421702 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A338601 SN: 0071732, *TAP: SIZE: B LOC: 13 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: __ LOC: ON FRANCE 13FT FROM PL N ROBERTSON 6' OUTSIDE PL ****/ | 2018-01-06 | ARRIVED AT ABOVE LOCATION FOUND CUSTOMER PARKING ON METER BOX IN GUTTER BOTTOM EXCAVATED 4 X 2 SIDEWALK CUT RELOCATED METER FROM GUTTER BOTTOM PLACE METER IN MUD PLOT CLOSE T5O HOUSE RENEWED OUTLET SERVICE LINE TO PROPERTY BAQCKFILL AND CLEANED THE AREA
201701264801 | 2017-09-21 | LEAD | 4508 | ST CLAUDE AV | KENTUCKY | WILK | **************PICKUP************ INLET SERVICE LEAK IN MUDPLOT 09/27/17 EAK IN STREET (CUSTOMER STATES IS FLOODING AREA AND PREVENTING CONTRACTORS FROM POURING CONCRETE) (KSW) 10/03/17 LEAK GETTING WORSE CAUSING AREA TO FLOOD PER SR#12816703 (AJR) 10/04/17 WATER NOW SPEWING OUT OF LINE WETTING NEIGHBORS PROPERTY PER SR#12816871 (AJR) /** 1) MN: SN: 0060115, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT KENTUCKY, *MB: CODE: AFL LOC: ON ST. CLAUDE AVE.,71.4' FROM L.R.P.L. KENTUCKY ****/ | 2017-10-20 | EXCAVATED 3 X 3 MUD PLOT REPAIR INLET SERVICE LINE ALSO BURIED THE LINE DEEPER BACKFILL AND CLEANED THE AREA FORCE ACCOUNT TO MR BILLEAUD FOR REPAIRS
201701265101 | 2017-09-21 | LEAD | 2826 | BROADWAY | PRITCHARD PL | WILK | WM LEAK @ THE CURB INLET SERVICE LEAK @ THE CURB 01/23/18 PER INSP L GOMEZ UPGRD GIVE OUT *****POSSIBLE BROKEN WATER MAIN UNDER DRIVEWAY CAUSING LARGE DEP UNDER DRIVEWAY FLOODING AREA ***M ROBINISON 13:27** /** 1) MN: A301608 SN: 0079724, *TAP: SIZE: A LOC: 117 FEET FROM P LINE AT PRITCHARD, *MB: CODE: CD LOC: ON BROADWAY 117FT FROM PRITCHARD 2FT OUTSIDE CURB ****/ | 2018-01-23 | EXCAVATED IN MUDPLOT. REPAIR 1 1/2" INLET LEAD LINE. DRESS UP WITH RIVER SAND JOB COMPLETE
201701265801 | 2017-09-22 | LEAD/PLASTIC | 5340 | LACOUR MONIQUE | ETON | WMTLK | LOCATIONID#233152-417131 METER#C034352 LEAK INSIDE METERBOX /** 1) MN: C025183 SN: 0149447, *TAP: SIZE: C LOC: 189 FEET FROM P LINE AT ETON, *MB: CODE: ADLM LOC: RES. ON LACOUR MONIQUE 192' FROM PL ETON 7' OUTSID ****/ | 2017-11-07 | EXAMINED METER OBSERVED LEAK ON INLET SERVICE REPAIRED THE LEAK
201701266001 | 2017-09-22 | LEAD/PLASTIC | 2346 | SOMERSET DR | BRISTOL PL | WMTLK | LOCATIONID#228514-416559 METER#B026905 METERBOX OVERFLOWING /** 1) MN: B026905 SN: 0121705, *TAP: SIZE: B LOC: 409 FEET FROM P LINE AT BRISTOL PL, *MB: CODE: CDMN LOC: 409'FROM P L BRISTOL ****/ | 2017-10-03 | ARRIVED ON JOB SITE EXAMINED METER EXCAVTED BY HAND FOUND LEAK ON INLET AND REPAIRED
201701266101 | 2017-09-22 | LEAD/PLASTIC | 2331 | SOMERSET DR | BRISTOL PL | WMTLK | LOCATIONID#228923-709943 METER#A257842 METERBOX OVERFLOWING /** 1) MN: A257842 SN: 0125602, *TAP: SIZE: A LOC: 308 FEET FROM P LINE AT BRISTOL PL, *MB: CODE: CDLM LOC: ON SOMERSET DR 308'P.L. BRISTOL PL 7FT OUTSIDE P.L ****/ | 2017-10-02 | ARRIVED ON JOB SITE EXAMINED METER EXCAVATED BY HAND FOUND LEAK ON INLET REPAIRED INLET AND RAISE METER TO GRADE
201701267801 | 2017-09-22 | LEAD | 1601 | BASIN | N ROBERTSON | WILK | MI- LEAK AT THE SIDEWALK INLET ON ABANDON SERVICE, LINE EXPOSED /** 1) MN: SN: 0008279, *TAP: SIZE: B LOC: 64 FEET FROM P LINE AT ORLEANS AVE LSPL, *MB: CODE: ANS7 LOC: 64' FROM ISPL ORLEANS ****/ | 2017-09-26 | FOUND LINE EXPOSED AND FIX LEAK ON INLET
201701267901 | 2017-09-22 | LEAD | 1604 | ST ANN | N ROBERTSON | WILK | ************PICKUP************* INLET ON ABANDON SERVICE ALSO LEAKING IN DRIVEWAY /** 1) MN: SN: 0002903, *TAP: SIZE: B LOC: 34 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: CEM4 LOC: 2ND METER FRONT ON ST ANN 34' FROM LSPL N ROBERTSO ****/ | 2017-09-26 | EXCAVATED 4 X 3 DRIVEWAY MADE REPAIR ON ABANDON INLET SERVICE TO STOP LEAK
201701269701 | 2017-09-22 | LEAD/PLASTIC | 339 | ATLANTIC AV |  | WILK | ML-METER LEAK ACCT. 224900-402208 MTR.# A 387057 INLET SERVICE LEAK /** 1) MN: A269393 SN: 0061379, *TAP: SIZE: A LOC: 88 FEET FROM P LINE AT ALIX, *MB: CODE: DL LOC: ON ATLANTIC AVE., 87' FROM U.R.P.L. ALIX ****/ | 2017-11-20 | EXCAVATED METER OBSERVED LEAK ON HAMDWHEEL OBSERVED LEAK ON CONTRACTORS FITTING OBSERVED LEAK ON BOX COCK REMOVED LEAD TO PROPERTY REPLACE METER WITH METER BOX COMPLETE REPAIRED LEAK
201701271901 | 2017-09-22 | LEAD | 3806 | PITT |  | WILK | ML METER LEAK ACCT#203949-557041 METER#A156057 INLET SERVICE LEAK AT METER /** 1) MN: A283010 SN: 0012506, *TAP: SIZE: B LOC: 67 FEET FROM P LINE AT PENISTON, *MB: CODE: OOOO LOC: ON PITT 67' FROM COR PL PENISTON 6' OUTSIDE PL ****/ | 2018-03-17 | EXCAVATED IN MUDPLOT. REPAIR 5/8 STOP & WASTE LEAD LINE. DRESS UP WITH RIVERSAND REFER TO ZONE 3 TO TAKE LEAD LINE FROM WATER MAIN TO METER BOX
201701274701 | 2017-09-24 | LEAD/PLASTIC | 1653 | FARRAGUT | LAWRENCE RD | WILK | ML- METER LEAK MTR# A394247 ACCT# 226323-404721 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A346344 SN: 0104014, *TAP: SIZE: A LOC: 421 FEET FROM P LINE AT LAWRENCE, *MB: CODE: ADL4 LOC: 421FT FROM P.L. LAWRENCE 7' OUTSIDE PL ****/ | 2017-11-15 | EXACAVATED METER EXPOSED INLET AND OUTLET LEAD FOUND ON INLET AND OUTLET REPLACE TO PROPERTY OUTLET BACKFILLED LEAD ON INLET NEEDS TO BE REPLACED WITH MACHINE ALSO LEAK WAS FOUND ON OUTLET LINE
201701276103 | 2017-10-11 | LEAD/PLASTIC | 829 | CONRAD | GEN DIAZ | WILK | /** 1) MN: A259524 SN: 0119765, *TAP: SIZE: A LOC: 41 FEET FROM P LINE AT CONRAD, *MB: CODE: BDHM LOC: 41FT PL CONRAD 8' OUTSIDE 7' INSIDE CURB ****/ | 2017-10-12 | EXCAVATED A 7 X 7 MUDPLOT CUT TO REPAIR INLET SERVICE LEAK ON METERBOX RAISE TO GRADE AND RENEW OUTLET SERVICE FROM METERBOX TO P.L. FOUND LEAD ON INLET SERVICE JEG
201701276501 | 2017-09-25 | LEAD | 1740 | INDUSTRY | N BROAD | WMTLK | OLD ACCT# 081151125 NEW ACCT# 147220-490340 METER# A342480 ****METER STILL LEAKING EXCESSIVELY**** /** 1) MN: A336154 SN: 0079243, *TAP: SIZE: A LOC: 143 FEET FROM P LINE AT BROAD N, *MB: CODE: ADK LOC: ON INDUSTRY 143FT FROM PL N BROAD 15' HPL CURB ****/ | 2017-10-17 | REPLACED 5/8 HANDWHEEL + GUTS IN METER BOX
201701281801 | 2017-09-25 | LEAD | 2371 | ST CLAUDE AV |  | WILK | MI -LEAK BETWEEN SIDEWALK & STREET. INLET SERVICE LEAK ON ABANDON SERVICE IN FRONT RALLY'S IN LARGE TREE BY DRIVE THRU CAUSING A LARGE HOLE. LEFT 2 ONE ON TOP /** 1) MN: C022270 SN: 0168265, *TAP: SIZE: C LOC: 12 FEET FROM P LINE AT SPAIN, *MB: CODE: AD2 LOC: ON ST CLAUDE AVE. 12' FROM DPL OF SPAIN 8' OUTSIDE ** 2) MN: 000000 SN: 0060510, *TAP: SIZE: A LOC: 50 FEET FROM P LINE AT ST ROCH AVE, *MB: CODE: CDLN LOC: ON ST CLAUDE AVE 50' FROM USPL ST ROCH AVE ****/ | 2017-09-27 | EXCAVATED 5 X 2 MUD PLOT MADE REPAIR ON ABANDON INLET SERVICE LINE BACKFILLED AND CLEANED TEH AREA
201701282601 | 2017-09-25 | LEAD | 2258 | N ROMAN | MARIGNY | WILK | WM-LEAK IN SIDEWALK EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A242040 SN: 0171962, *TAP: SIZE: B LOC: 168 FEET FROM P LINE AT MARIGNY, *MB: CODE: BDN1 LOC: ON N ROMAN 168FT FROM PL MARIGNY ****/ | 2018-01-06 | EXCAVATED 4 X 4 GUTTER BOTTOM 4 X 3 SIDEWALK CUT AND 4 X 2 MUD PLOT TRENCH UP TO PROPERTY MOVED METER BOX FROM GUTTER BOTTOM INTO SIDEWALK SET 2 NEW METER BOX COMPLETE AND RENEWED OUTLET TO PROPERTY BACKFILLED AND CLEANED THE AREA
201701283301 | 2017-09-25 | LEAD | 2356 | N TONTI |  | WILK | ML-METER LEAK ACCT.# 161906-484700 MTR.# A 421377 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A246750 SN: 0100804, *TAP: SIZE: A LOC: 142 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: ADK2 LOC: 142FT PL MANDEVILLE 8' OUTSIDE ****/ | 2018-01-07 | EXCAVATED 4 X 4 SIDEWALK CUT ALSO 3 X 2 GUTTER BOTTOM MOVED METER BOX INTO SIDEWALK AND RENEWED OUTLET SERVICE LINE TO PROPERTY BACKFILL AND CLEANED THE AREA
201701286701 | 2017-09-26 | LEAD/PLASTIC | 8438 | BELFAST | JOLIET | WOLK | ML- METER LEAK ACCT# 140036-593177 METER# A 420744 OUTLET SERVICE LEAKING FROM HANDWHEEL RENEW OUTLET SERVICE /** 1) MN: A292992 SN: 0070809, *TAP: SIZE: B LOC: 52 FEET FROM P LINE AT BELFAST, *MB: CODE: __ LOC: ON JOLIET ST 53' FROM PL BELFAST ****/ | 2017-10-13 | EXCAVATED AND RENEWED A 5/8 OUTLET SERVICE LEAK. PLASTIC ON THE OUTLET LEAD ON THE INLET. JOB COMPLETE JEG
201701286801 | 2017-09-26 | LEAD | 5447 | DAUPHINE | ANDRY | WILK | ML- METER LEAK ACCT# 155375-425489 METER# A 280626 INLET SERVICE LEAK INTO METER BOX /** 1) MN: A280626 SN: 0083224, *TAP: SIZE: A LOC: 355 FEET FROM P LINE AT ANDRY, *MB: CODE: AD LOC: ON DAUPHINE, 355' FROM P.L. ANDRY,8' OUTSIDE P.L., ****/ | 2017-10-06 | EXCAVATED 2 X 4 CONCRETE SLATE SIDEWALK FOUND LEAK ON 5/8 INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND + COLDMILL
201701286901 | 2017-09-26 | LEAD | 1127 | BOURBON | URSULINES AV | WILK | ML-METER LEAK ACCT#172031-529245 METER#C021091 INLET SERVICE LEAK INTO METER BOX /** 1) MN: C021091 SN: 0002319, *TAP: SIZE: C LOC: 207 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: BE7 LOC: 207FT FROM PL URSULINE AVE 4' OUTSIDE PL 6' INSIDE ** 2) MN: SN: 0002319, *TAP: SIZE: B LOC: 111 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: __ LOC: 111' P.L. GOV NICHOLLD ****/ | 2017-10-04 | EXAMINED JOB FOUND LEAK ON INLET SERVICE EXCAVATED 4 X 2 IN SIDEWALK CUT OUT
201701287001 | 2017-09-26 | LEAD/PLASTIC | 9403 | FIG | LIVE OAK | WMTLK | MI- CHECK FOR LEAK AT PROPERTY LINE RENEW OUTLET SERVICE EXAMINE INLET AND OUTLET SERVIC EFOR LEAK METER UNDER WATER FLOODING SIDEWALK AND GRASS METER LOCATED ON LIVE OAK, HOUSE UNDER CONSTRUCTION /** 1) MN: A343736 SN: 0109050, *TAP: SIZE: A LOC: 1 FEET FROM P LINE AT LIVE OAK, *MB: CODE: BDK1 LOC: FRONT - 1' P/L LIVE OAK 8' OUTSIDE ****/ | 2017-10-13 | EXCAVATED AND RAISE A 5/8 METER BOX TO GRADE. ALSO RENEWED THE OUTLET. LEAD ON THE INLET PLASTIC ON THE OUTLET. JOB COMPLETE. JEG
201701289101 | 2017-09-26 | LEAD/PLASTIC | 1001 | TERRY | PATTERSON RD | WOLK | WM LEAK ON THE SIDEWALK EXAMINE OUTLET SERVICE LEAK UP TO PROPERTY LINE 10/26/17 SIDEWALK LEAK WORSE. MORE RUNNING WATER WASHING AWAY THE SOIL (KSW) /** 1) MN: B024344 SN: 0128828, *TAP: SIZE: B LOC: 42 FEET FROM P LINE AT PATTERSON RD, *MB: CODE: AL LOC: ON TERRY 67FT FROM P.L. PATTERSON 4FT INSD CURB ****/ | 2017-11-14 | EXCAVATED METER EXPOSED TO PORPERTY OBSERVED LEAK ON AT PROPERTY REPAIRED LEAK BACKFILLED
201701289301 | 2017-09-26 | LEAD | 2929 | CASTIGLIONE | ROSIERE | WMTBG | MI - METER BOX BELOW GRADE MTR# A 399725 /** 1) MN: A249054 SN: 0071090, *TAP: SIZE: A LOC: 237 FEET FROM P LINE AT GAYOSO N, *MB: CODE: __ LOC: ON CASTIGLIONE 237' FROM GAYOSO N ****/ | 2017-09-29 | EXCAVATED IN MUD PLOT + REPLACED BOOKEN 5/8 INCH METER BOX CASING BACKFILL + DRESSED UP AREA
201701289901 | 2017-09-26 | LEAD | 2139 | BENTON | BENTON | WILK | WM- LEAK IN THE STREET CHANGED FROM N/A N MIRO/BENTON INLET SERVICE LEAK IN STREET INTEREFFINGN WITH CONTRACTORS WORK /** 1) MN: A148538 SN: 0140014, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT MIRO N, *MB: CODE: CDN1 LOC: RES ON BENTON 44FT PL N MIRO 6' OUTSIDE ****/ | 2017-10-09 | EXCAVATED 4X 8 LIMESTONE STREET CUT FOUND LEAK ON 5/8 INCH ABANDON INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND + COLDMILL
201701290301 | 2017-09-26 | LEAD | 2826 | N DORGENOIS | ALMONASTER AV | WMRE | ML- METER LEAK MTR# A 408211 ACCT# 142583-484942 LOCATE, MARK & RAISE TO GRADE /** 1) MN: A307381 SN: 0076519, *TAP: SIZE: A LOC: 198 FEET FROM P LINE AT EADS, *MB: CODE: CDLN LOC: 198' P.L. EADS ****/ | 2017-10-09 | EXCAVATEDE 3 X 3 GUTTER REPLACE 5/8 INCH WASHER AND BROKEN METER BOX CASING MARKED SIDEWALK AND STREET ALSO METER BOX TOP FOR LOCATION
201701291001 | 2017-09-26 | LEAD | 2737 | DREUX AV |  | WOLK | MI--- LEAD WHIP CHANGE ACCT# 302673-711271 METER# A431737 RENEW OUTLET 09/30/17 ALSO INLET SERVICE LEAK IN BOX PER SR#12816546 (AJR) /** 1) MN: A319938 SN: 0086200, *TAP: SIZE: A LOC: 28 FEET FROM P LINE AT BACCICH, *MB: CODE: CE6 LOC: DREUX AVE 28' FROM PL BACCICH ST ****/ | 2017-10-05 | MADE A ADDITIONAL 5X2 CUT TO A EXISTING CUT IN SIDEWALK. EXCAVATED DOWN ON OUTLET SERVICE FROM METER TO PROPERTY. FOUND LEAD. MADE REPAIR'S BY REPLACING OUTLET SERVICE FROM METER TO PROPERTY. BACKFILLED.
201701292001 | 2017-09-26 | LEAD/PLASTIC | 743 | 4TH | ANNUNCIATION | WILK | ML METER LEAK ACCT# 100780-488871 METER# A320737 INLET SERVICE LEAK 10/27/17 LEAK NOW FLOODING STREET PER SR#12819152 (AJR) 11/14/17 CUSTOMER STATES LEAK HAS GOTTEN WORSE CAUSING AREA TO FLOOD (NLD) /** 1) MN: A216506 SN: 0003920, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT ANNUNCIATION, *MB: CODE: BFK5 LOC: ON FOURTH 74FT FROM PL ANNUNCIATION ****/ | 2017-11-17 | EXAMINED METER BROKE CONCRETE WITH MAUL EXCAVATED METER EXPOSED INLET AND OUTLET OBSERVED LEAK ON INLET REPLACED LEAKING LEAD LEAD ON INLET NEED TO BE REPLACED TO MAIN PLACED 2CONE ON WHOLE NEED SAND AND COAL MILL I CALL FOR BARRELS
201701292601 | 2017-09-27 | LEAD | 1621 | BENTON | N CLAIBORNE AV | WMBK | LOCATIONID#160127-423678 METER#A396996 METERBOX CASING BROKEN.PLEASE REPLACE /** 1) MN: A113734 SN: 0136468, *TAP: SIZE: A LOC: 166 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: ADL LOC: ON BENTON, 166' FROM P.L. NO. CLAIBORNE AVE.,8' ****/ | 2017-09-28 | EXCAVATED 2 X 2 DRIVEWAY CUT REPLACED BROKEN METER BOX CASING BACKFILLED AND CLEANED THE AREA
201701292701 | 2017-09-27 | LEAD/PLASTIC | 3543 | HAMBURG | SERE | WMTLK | LOCATIONID#131208-497483 METER#A307014 METERBOX OVERFLOWING /** 1) MN: A307014 SN: 0108722, *TAP: SIZE: A LOC: 44 FEET FROM P LINE AT HAMBURG, *MB: CODE: CEH LOC: ON SERE,43.8' FROM P.L. HAMBURG,7' OUTSIDE P.L. ****/ | 2017-10-22 | MADE A 4 X 8 SIDEWALK CUT EXCAVATED AND MADE REPAIRS ON A 5/8 INLET LEAK LEAD LINE. RENEWED THE OUTLET AND RAISED THE METER TO GRADE. REFER THAT SIDEWALK CUT TO PAVING. JOB COMPLETE. JEG
201701293601 | 2017-09-27 | LEAD | 3900 | CLERMONT DR | MONTEPELIER | WOLK | ML- METER LEAK MTR.# A-307475 EXAMINE OUTLET SERVICE FOR LEAK @ PROPERY LINE ***METER HAS C/O COVER ON IT*** /** 1) MN: A114823 SN: 0092068, *TAP: SIZE: A LOC: 275 FEET FROM P LINE AT MONTPELIER, *MB: CODE: BDM1 LOC: ON CLERMONT DR., 275' FROM P.L. MONTPELIER,7' OUT- ****/ | 2017-10-20 | EXCAVATED BY HAND AND REPAIRED A LEAK ON A 3/4 LEAD OUTLET SERVICE. BACKFILL CLEANED UP JOB.,,,CREW FOUND METER NUMBER A114823 AT AOVE LOCATIONS
201701294801 | 2017-09-27 | LEAD | 2318 | MANDEVILLE | N TONTI | WILK | ML-- METER LEAK METER # A406921 ACCT#136177-484478 EXAMINE INLET SERVICE IN MUD PLOT IN METER /** 1) MN: A239103 SN: 0116034, *TAP: SIZE: A LOC: 135 FEET FROM P LINE AT TONTI N, *MB: CODE: ADNO LOC: 135FT FROM PL N TONTI ****/ | 2017-10-23 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201701295401 | 2017-09-27 | LEAD/PLASTIC | 8315 | S CLAIBORNE AV |  | WMTLK | BAD LEAK COMING FROM METER BOX. UNABLE TO PUMP OUT WATER FAST ENOUGH TO SET METER. PLEASE REPAIR AND SET 5/8 METER. LOC ID 302970 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER BOX UNDER WATER ALSO SET 5/8 METER /** 1) MN: A279225 SN: 0172564, *TAP: SIZE: B LOC: 166 FEET FROM P LINE AT DANTE, *MB: CODE: CDL LOC: ON SO. CLAIBORNE AVE., 163.5' FROM P.L. DANTE ****/ | 2017-10-04 | EXCAVATED AND RAISED THE METER TO GRADE AND RENEWED THE OUTLET AND SET A 5/8 METER. JOB COMPLETE LEAD ON THE INLET. PLASTIC ON THE OUTLET. JEG
201701296502 | 2017-10-05 | LEAD/PLASTIC | 340 | MOUND AV |  | WMRE | EXAMINED AND EXCAVATED IN MUDPLOT TRYING TO LOCATE BURIED METER BOX WAS UNABLE TO DUE TO DUMPSTER ON TOP OF AREA WHERE MEASURMENTS FELL. REFER TO PROPERTY TO REMOVE DUMPSTER. **************************SET 5/8 METER********************************* /** 1) MN: A325694 SN: 0086921, *TAP: SIZE: C LOC: 231 FEET FROM P LINE AT MILNE, *MB: CODE: AFN LOC: ON MOUND 270' FROM PL OF MILNE ****/ | 2017-10-19 | EXCAVATED A 4 X 25 TRENCH IN MUDPLOT TO LOCATE A 5/8 SERVICE LEAD INLET & PLASTIC OUTLET REPLACED THE INLET SERVICE WITH PVC PIPE FROM CONTROLLING LINE TO PROPERTY BACKFILLED AND DRESSUP WITH RIVERSAND. ALSO SET A 5/8 METER.
201701297001 | 2017-09-27 | LEAD | 201 | DECATUR |  | WMBK | METER CASING OVER CURB COCK PLEASE REPAIR LOCATION #102549 METER BOX SHIFTED OVER CURB COCK /** 1) MN: B026411 SN: 0002249, *TAP: SIZE: B LOC: 62 FEET FROM P LINE AT DECATUR, *MB: CODE: AEH4 LOC: ON IBERVILLE 62FT FROM LSPL DECATUR ****/ | 2017-10-09 | EXCAVATED 2 X 2 SIDEWALK CUTALIGN METER BOX IN THE CORRECT POSITION BACK FILLED AND CLEANED THE AREA ALSO REMOVED CONCRETE FROM AROUND METER
201701297301 | 2017-09-27 | LEAD/PLASTIC | 2847 | KENT DR | GEN MEYER AV | WILK | ML- METER LEAK ACCT#233533-419008 METER#A304322 INLET SERVICE LEAK /** 1) MN: A304322 SN: 0150794, *TAP: SIZE: B LOC: 283 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: CDM7 LOC: ON KENT 30FT FROM DIV P/L ZION 3FT INSIDE ****/ | 2017-11-15 | EXAMINED METER BOX NO LEAK FOUND EXAMINED PROPERTY NO LEAK OBSERVED LEAK OBSERVE COMING FROM CURB AT EDGE OF DRIVEWAY CLEAN OUT METER BOX...JOB CONTINUED
201701297901 | 2017-09-27 | LEAD | 7 | PRESS | DAUPHINE | WILK | ML - METER LEAK MTR # A424279 ACCT # 222612-427113 EXAMINE INLET SERVICE FOR A LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-10-06 | REPLACE BOTH INLET /OUTLET SERVICE WASHERS AT ABOVE LOCATION INLET + OUTLET BEEN REPLACE WITH PLASTIC
201701299701 | 2017-09-27 | LEAD | 6419 | N ROBERTSON | DELERY | WMLK | MI - LEAK IN THE STREET CHANGED FROM 6319 N. ROBERTSON LEAK ON WATER MAIN IN MIDDLE OF STREET /** 1) MN: 000000 SN: 0133063, *TAP: SIZE: B LOC: 179 FEET FROM P LINE AT DELERY, *MB: CODE: BDM3 LOC: RES ON N ROBERTSON 179' P/L DELERY 6' OUTSIDE ****/ | 2017-10-05 | EXCAVATED 6 X 56 ASPHALT STREET CUT FOUND LEAK ON 5/8 ABANDON INLET SERVICE MADE REPAIR ON 1 INLET BACKFILL JOB WITH RIVERSAND + COLDMILL
201701302301 | 2017-09-28 | LEAD/PLASTIC | 2422 | EAGLE |  | WILK | ML METER LEAK ACCOUNT #137828591009 METER # A406517 INET SERVICE LEAK IN GRASS FLOODING GRASSY AREA /** 1) MN: A156358 SN: 0068241, *TAP: SIZE: A LOC: 101 FEET FROM P LINE AT NELSON, *MB: CODE: CDL6 LOC: ON EAGLE 162.6FT FROM PL OF NELSON ****/ | 2017-10-08 | EXCAVATED AND MADE REPAIRS ON A 5/8 INLET SERVICE LEAK LEAD LINE PLASTIC ON THE OUTLET JOB COMPLETE JEG
201701302701 | 2017-09-28 | LEAD | 1539 | N ROBERTSON | LAHARPE | WILK | ML- METER LEAK ACCT# 302004-536119 METER # A426167 INLET SERVICE LEAK IN METER BOX /** 1) MN: A261242 SN: 0043106, *TAP: SIZE: B LOC: 27 FEET FROM P LINE AT N CLAIBORNE, *MB: CODE: CD LOC: ON LAHARPE 34' FROM P.L. N CLAIBORNE 2'OUTSIDE 6' ****/ | 2017-10-06 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILL + DRESSED UP AREA
201701303101 | 2017-09-28 | LEAD | 541 | WARRINGTON DR |  | WILK | MI- LEAK AT THE SIDEWALK INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A316976 SN: 0110313, *TAP: SIZE: A LOC: 992 FEET FROM P LINE AT STEPHEN GIRARD AVE, *MB: CODE: ADL4 LOC: ON WARRINGTON DR 992FT FROM P.L. OF STEPHEN GIRARD ****/ | 2017-12-21 | EXCAVATED IN MUDPLOT ON INELT LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVER SAND.
201701304501 | 2017-09-28 | LEAD | 417 | S DUPRE |  | WMTLK | ML-METER LEAKING MTR.# A 426732 ACCT.# 114137-531090 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A290572 SN: 0017507, *TAP: SIZE: A LOC: 173 FEET FROM P LINE AT BANKS, *MB: CODE: CFL LOC: 174' P.L. BANKS ****/ | 2017-10-06 | FOUND NO LEAK AT ABOVE LOCATION REPLACED BROKEN 5/8 INCH METER BOX CASING
201701305201 | 2017-09-28 | LEAD | 3127 | DUMAINE |  | WILK | MI-LEAK IN STREET INLET SERVICE LEAK /** 1) MN: A282138 SN: 0175310, *TAP: SIZE: A LOC: 111 FEET FROM P LINE AT RENDON N, *MB: CODE: BDK LOC: ON DUMAINE,110' FROM L.R.P.L. NO. RENDON ****/ | 2017-10-11 | EXCAVATED IN ASPHALT STREET + REPLACED 3/4 INCH CORPORATION COCK IN WATER MAIN COMPACTED BACKFILL + DRESSED UP AREA
201701306601 | 2017-09-28 | LEAD | 1400 | GOV NICHOLLS | MARAIS | WILK | ML-METER LEAK ACCT# 204465-526399 METER# A285494 INLET SERVICE LEAKING INSIDE METER BOX /** 1) MN: A310955 SN: 0040877, *TAP: SIZE: D LOC: 44 FEET FROM P LINE AT GOV.NICHOLLS, *MB: CODE: CDN1 LOC: ON MARAIS 41'FROM P.L. GOV.NICHOLLS 9'OUTSIDE P.L. ** 2) MN: A305004 SN: 0040877, *TAP: SIZE: B LOC: 42 FEET FROM P LINE AT GOV.NICHOLLS, *MB: CODE: CDN1 LOC: ON MARAIS 42'FROM P.L. GOV.NICHOLLS 9'OUTSIDE P.L. THERE ARE 4 MORE NOT LISTED. ****/ | 2017-10-06 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201701307001 | 2017-09-28 | LEAD | 618 | PAULINE | DECATUR | WILK | ML METER LEAK METER#A398268 ACCOUNT#123964-428259 INLET SERVICE LEAKING INSIDE METER BOX /** 1) MN: A246757 SN: 0051468, *TAP: SIZE: A LOC: 147 FEET FROM P LINE AT CHARTRES, *MB: CODE: BDLN LOC: ON PAULINE,148' FROM U.S.P.L. CHARTRES ****/ | 2017-10-05 | EXCAVATED 2 X 2 BRICK SIDEWALK REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILL AND CLEANED THE AREA
201701309801 | 2017-09-29 | LEAD | 2234-36 | FRANCE | POLAND AV | WILK | WM - LEAK ON THE SIDEWALK INLET SERVICE LEAK ON ABANDON SERVICE IN VACANT LOT BY OVERGROWN GRASS /** AT 2234: 1) MN: SN: 0079338, *TAP: SIZE: A LOC: 206 FEET FROM P LINE AT MIRO N, *MB: CODE: BDK LOC: ON FRANCE ST 206' FROM PL N MIRO STREET ****/ | 2017-10-06 | EXCAVATED 4 X 8 MUD PLOT FOUND LEAK ON 6 INCH WATER MAIN ABANDON INLET SERVICE MADE REPAIR ON INLET SERVICE BACKFILL JOB WITH RIVERSAND
201701310601 | 2017-09-29 | LEAD/PLASTIC | 1509 | TITA | GEN MEYER AV | WILK | ML-METER LEAK ACCOUNT #226083-407697 METER #A277879 EXMINE INLET SERVICE @ SIDEWALK FOR A LEAK 10/16/17 LEAK GETTING WORSE CAUSING AREA TO FLOOD PER SR#12817963 (AJR) 10/27/17 CUST STATES METER LEAK HAS BECOME WORSE POSSIBLY CAUSING POOR PRESSURE IN HOME (KSW) /** 1) MN: A277879 SN: 0122456, *TAP: SIZE: B LOC: 459 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: AK25 LOC: 48FT FROM P.L. GEN MEYER ON TITA ****/ | 2017-11-15 | ARRIVED ON JOB SITE EXAMINED METER EXCAVATED HAND FOUND LEAK ON INLET AND REPAIRED
201701315801 | 2017-09-30 | LEAD | 1677 | AGRICULTURE | REPUBLIC | WMTLK | MI-METER LEAK EXAMINE INLET & OUTLET SERVICE FOR A LEAK IN GUTTER BOTTOM FLOODING GUTTER BOTTOM /** 1) MN: A269840 SN: 0089825, *TAP: SIZE: A LOC: 35 FEET FROM P LINE AT AGRICULTURE, *MB: CODE: CDH LOC: 35FT FROM PL AGRICULTURE ON REPUBLIC ****/ | 2017-10-06 | EXCAVATED 4 X3 MUD PLOT MADE REPAIR ON INLET SERVICE REPLACED 5/8 INCH METER BOX COCK AND HANDWHEEL BACKFILLED AND CLEANED THE AREA
201701318601 | 2017-10-02 | LEAD/PLASTIC | 6600 | BRUNSWICK CT | PRESTON PL | WOLK | LOCATION# 233208 CUSTOMER # 418799 METER# A197877 INSPECTOR DID AN OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION ON METER, NOT SURE WHO SIDE THE LEAK ON. PLEASE CHECK AND REPAIR /** 1) MN: A197877 SN: 0149641, *TAP: SIZE: B LOC: 45 FEET FROM P LINE AT PRESTON PL, *MB: CODE: CDL2 LOC: ON BRUNSWICK CT 42' FROM PL PRESTON 7' OUTSIDE PL ****/ | 2017-11-10 | EXCAVATED METER EXPOSED BOTH INLET AND OUTLET EXCAVATED TO PROPERTY LINE CONNECTION OBSERVED NO LEAK NOTIFIED CUSTOMER OF LEAK CONCERNS BACKFILLED LEAK IS SOMEWHERE ON CUSTOMER PROPERTY
201701322301 | 2017-10-02 | LEAD/PLASTIC | 321 | WHITNEY AV | ALIX | WILK | PP POOR PRESSURE ACCT# 234964-403482 METER# A350474 ******1ST AM****** INLET SERVICE LEAK IN SDEWALK CAUSING VERY LOW WATER PRESSURE & DEPRESSION /** 1) MN: A305601 SN: 0102090, *TAP: SIZE: B LOC: 141 FEET FROM P LINE AT PELICAN AVE, *MB: CODE: BD LOC: ON WHITNEY 161FT FROM PELICAN 10FT OUTSIDE ****/ | 2017-10-03 | BROKE THE SIDEWALK AND EXCAVATED ON THE OUTLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOB SITE
201701325001 | 2017-10-03 | LEAD | 5902 | DAUPHINE | ALABO | WMTBG | METER BOX IS DEEP PLEASE RAISE TO GRADE AND CH/M A-249881 LOCATION #148007 RAISE METER TO GRADE AND CHANGE METER /** 1) MN: A249881 SN: 0058776, *TAP: SIZE: A LOC: 40 FEET FROM P LINE AT DAUPHINE, *MB: CODE: CDH2 LOC: ON ALABO 40FT FROM DAUPHINE ****/ | 2017-10-20 | EXCAVATED 3 X 3 MUD PLOT RAISED METER BOX TO GRADE BACKFILLED AND CLEANED THE AREA
201701329601 | 2017-10-03 | LEAD | 1946 | N TONTI | ALLEN | WMTLK | WM LEAK ON SIDEWALK EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER ON ALLEN /** 1) MN: A309294 SN: 0056929, *TAP: SIZE: A LOC: 23 FEET FROM P LINE AT TONTI N, *MB: CODE: BF LOC: FRONT INSIDE OPP DOOR ON ALLEN 22FT FROM LRPL ****/ | 2017-10-05 | EXCAVATED 2 X 2 IN MUD PLOT FOUND LEAK ON METER BOX COCK REPLACED METER BOX COCK BACKFILLAND CLEANED AREA
201701329701 | 2017-10-03 | LEAD/PLASTIC | 2383 | ROUSSEAU | 1ST | WOLK | ML- METER LEAK MTR# A422337 ACCT# 118095-541381 OUTLET SERVICE LEAKING AT HANDWHEEL CAUSING CONSTANT REG ON METER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-11-07 | BROKE CONCRETE WITH MAUL HAMMER EXCAVTED METER BOX LOCATED LEAK ON HANDWHEEL REMOVED LEAD LINE TO PROPERTY REPLACED HAND WHEEL BACKFILLED WILL NEED CONCRET REPLACED (3X3)
201701334001 | 2017-10-04 | LEAD | 1428 | FRANCE | N VILLERE | WILK | METER LEAK - ACCOUNT NUMBER - 169443-431003 METER NUMBER - B036970 BAD BLEEDER VALVE LEAKING IN ON POSITION /** 1) MN: A322925 SN: 0111568, *TAP: SIZE: A LOC: 168 FEET FROM P LINE AT VILLERE N, *MB: CODE: ADK2 LOC: ON FRANCE 166' FROM PL N VILLERE 9' OUTSIDE PL 1 ' ****/ | 2017-10-10 | EXCAVATED 2 X 2 DRIVEWAY CUT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILL AND CLEANED THE AREA
201701336201 | 2017-10-04 | LEAD/PLASTIC | 1353 | RAPIDES DR |  | WMRE | METER BOX BURIED PLEASE RAISE TO GRADE AND SET A 5/8 METER LOCATION #303033 LOCATE & RAISE TO GRADE, ALSO SET A METER /** 1) MN: A292648 SN: 0118113, *TAP: SIZE: A LOC: 138 FEET FROM P LINE AT CARTIER AVE, *MB: CODE: ADLM LOC: 136FT PL CARTIER AV 7' OUTSIDE ****/ | 2017-10-16 | EXCAVATED A 6 X 6 MUDPLOT CUT TO RAISE METER BOX TO GRADE, RENEWED OUTLET SERVICE FROM METERBOX TO P.L. AND SET A 5/8 WATER METER. FOUND LEAD ON INLET SERVICE JEG
201701338101 | 2017-10-04 | LEAD/PLASTIC | 3456 | CONSTANCE | ALINE | WMTLK | ML-METER LEAK ACCT #108227-585502 METER#A151744 EXAMINE INLET AND OUTLET SERVICE INSIDE METER BOX FOR A LEAK DOTTIE READY 4-12-18 EXP 5-2-18 /** 1) MN: A151744 SN: 0009237, *TAP: SIZE: B LOC: 78 FEET FROM P LINE AT ALINE, *MB: CODE: CELM LOC: ON CONSTANCE 79 FT FROM PL ALINE ****/ | 2018-04-25 | ARRIVED ON JOB SITE AND FOUND LEAK ON INLET EXCAVATED ON 6 X 6 BRICK SIDEWALK AND MADE REPAIRS ON METER COCK.BACKFILL AND DRESSED CUT UP ALSO TIED ONTO LEAD NEED TO BE REMOVED FROM WATER MAIN TO PROPERTY.
201701340801 | 2017-10-05 | LEAD | 1906 | ST PHILIP | N ROMAN | WILK | ML-METER LEAK ACCT#119861-522477 METER#A354564 BAD BLEEDER VALVE IN BOX /** 1) MN: A229074 SN: 0034607, *TAP: SIZE: A LOC: 38 FEET FROM P LINE AT NO. ROMAN, *MB: CODE: AFK5 LOC: ON ST. PHILIP,38' FROM P.L. NO. ROMAN ****/ | 2017-10-17 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND + COLDMILL
201701341601 | 2017-10-05 | LEAD | 4116 | N ROMAN | MAZANT | WMTLK | ML - METER LEAK ACCOUNT NUMBER: 182739-433115 METER NUMBER: A406923 EXAMINE ILET AND OUTLET SERVICE FOR LEAK /** 1) MN: A153112 SN: 0125665, *TAP: SIZE: B LOC: 118 FEET FROM P LINE AT MAZANT, *MB: CODE: ADK5 LOC: ON ROMAN 119'P L MAZANT 8FT OUTSD PL ****/ | 2017-10-24 | EXCAVATED 2 X 2 MUD PLOT REPALCED 5/8 INCH METER BOX TO STOP LEAK BACKFILLED AND CLEANE DTHE AREA
201701341801 | 2017-10-05 | LEAD/PLASTIC | 3210 | LAWRENCE RD | HORACE | WOLK | ML- METER LEAK METER#A326095 ACCT#227774-VACANT EXAMINE OUTLET SERVICE FOR LEAK @ PROPERTY LINE /** 1) MN: A277256 SN: 0149965, *TAP: SIZE: A LOC: 203 FEET FROM P LINE AT LAWRENCE, *MB: CODE: BDL2 LOC: ON LAWRENCE 20FT FROM DIV P/L HOARCE ****/ | 2017-11-13 | EXCAVATED TO PROPERTY OBSERVED NO LEAK ON METER OR PROPERTY BACKFILLED
201701344901 | 2017-10-06 | LEAD | 2474 | N GALVEZ |  | WMRE | METER BOX BURIED PLEASE RAISE TO GRADE AND SET A 5/8 METER LOCATION #303075 LOCATE, RAISE TO GRADE AND SET 5/8 METER VACANT LOT /** 1) MN: SN: 0057619, *TAP: SIZE: A LOC: 31 FEET FROM P LINE AT GALVEZ N, *MB: CODE: ADH1 LOC: ON ARTS 32FT FROM PL OF N GLAVEZ ****/ | 2017-10-17 | EXCAVATED 2 X 2 SIDEWALK RENEW OUTLET SERVICE TO PROPERTY AND SET 5/8 METER
201701345701 | 2017-10-06 | LEAD/PLASTIC | 4027 | ERATO |  | WILK | BROKEN CURB COCK PLEASE REPAIR AND SET 5/8 METER LOCATION #302977 REPLACE BROKEN CURB COCK /** 1) MN: A245137 SN: 0079224, *TAP: SIZE: A LOC: 249 FEET FROM P LINE AT WHITE S, *MB: CODE: AEN2 LOC: ON ERATO 225FT FROM WHITE ****/ DOTTIE READY 10-27-17 EXP 11-16-17 | 2017-12-03 | ARRIVED ON JOB EXCAVATED IN DRIVEWAY BY HAND FOUND 5/8 METER BOX COCK LEAKING MADE REPAIRS AND BACKFILLED . JOB COMPLETE NO METER FOUND.
201701346401 | 2017-10-06 | LEAD | 6317 | BARRETT | CALHOUN | WILK | ML METER LEAK METER# A326453 ACCOUNT# 136490-567066 INLET SERVICE LEAK IN THE GRASS FLOODING GRASS 02/16/18 LEAK IS GOTTEN WORSE CUSTOMER IS WHEELCHAIR BOND AND HEALTH CARE PROVIDERS CANT GET TO HOME PER SR#12832256 (AJR) 02/28/18 LEAK IS GOTTEN WORSE CUSTOMER IS WHEELCHAIR BOND AND HEALTH CARE PROVIDERS CANT GET TO HOME PER SR#12833810 (AJR) 03/16/18 LEAK IS GOTTEN WORSE CUSTOMER IS WHEELCHAIR BOND AND HEALTH CARE PROVIDERS CANT GET TO HOME PER SR#12835492 (AJR) ***1ST AM**** /** 1) MN: A326453 SN: 0067093, *TAP: SIZE: B LOC: 134 FEET FROM P LINE AT CALHOUN, *MB: CODE: CEN2 LOC: ON BARRETT 132' FROM PL OF CALHOUN ****/ | 2018-03-17 | EXCAVATED IN MUDPLOT.REPAIR 5/8 STOP &WASTE LEAD LINE.DRESS UPWITH RIVERSAND. JOB REFER TO ZONE 3 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201701347301 | 2017-10-06 | LEAD | 2334 | PORT | N ROCHEBLAVE | WILK | ML-METER LEAK ACCT#300757-711676 METER#A432010****/ INLET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-10-16 | EXCAVATED 2 X 2 IN EXPOSE SIDEWALK REPLACED 5/8 INCH METER BOX CORK AND SET NEW METER BOX CASING BACKFILL + CLEANED TEH AREA
201701348401 | 2017-10-08 | LEAD | 2654 | N GALVEZ | ALMONASTER AV | WMTLK | WM-LEAK IN SIDEWALK EXAMINE INLET AND OOTLET SERVICE FOR LEAK @ SIDEWALK FLOODING SIDEWALK, LEFT 1 CONE FOR SAFTY /** 1) MN: B030423 SN: 0076619, *TAP: SIZE: B LOC: 136 FEET FROM P LINE AT ALMONASTER, *MB: CODE: OOO LOC: ON GALVEZ 135FT FROM ALMONASTER ****/ | 2017-10-16 | REPLACED 3/4 INCH WASHERS TO STOP LEAK
201701349801 | 2017-10-09 | LEAD | 412 | BOURBON | CONTI | WILK | MI-CUT SERVICE IN STREET ****HOLE IS EXPOSED***** ****CUST IS WITHOUT WATER******* BOH BROTHERS CONSTRUCTION LLC. 730 S TONTI. ST, NEW ORLEANS LA., 70119 504-821-2400 **********DAMAGE CLAIM********** ZONE 4 J GILLIAM @ 10:33 CUT INLET SERVICE @ THE MAIN BY BOH BROS /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-10-09 | MADE REPAIRS ON 1 INCH SERVICE LINE PULLED ON 12 INCH WATER MAIN BY BOH BROS CONSTRUCTION FORCE ACCOUNT BOH BROS CONSTRUCTION
201701354301 | 2017-10-09 | LEAD | 1239 | REYNES | URQUHART | WILK | MI LEAK ON SIDEWALK INLET SERVIE LEAK NO METER IN BOX /** 1) MN: A307755 SN: 0099387, *TAP: SIZE: A LOC: 31 FEET FROM P LINE AT REYNES, *MB: CODE: CFH LOC: 2 APTS ON URQUHART 31FT FROM PL REYNES ****/ | 2017-10-18 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED CLEANED THE AREA, OUTLET SERVICE RENEWED TO PROPERTY ALSO
201701356901 | 2017-10-10 | LEAD/PLASTIC | 1208 | SHIRLEY DR | DE ARMAS | WOLK | LOCATION# 226010 CUSTOMER# 405216 METER# A398885 INSPECTOR DID AN INSIDE/OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION ON METER, PERFORMED S&WB TEST METER CONTINUES TO RUN. PLEASE REPAIR /** 1) MN: A260617 SN: 0095697, *TAP: SIZE: B LOC: 127 FEET FROM P LINE AT DE ARMAS, *MB: CODE: AD25 LOC: ON SHIRLEY DR., 152.5' FROM P.L. DE ARMAS, 6' OUT- ****/ | 2017-10-31 | EXCAVATED METER LOCATE LEAK ON HAND WHEEL REPLACED HANDWHEEL AND WASHERS
201701358401 | 2017-10-10 | LEAD | 1865 | N GALVEZ | ALLEN | WILK | ML METER LEAK METER # A399580 ACCOUNT # 200871-494328 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A220297 SN: 0063301, *TAP: SIZE: B LOC: 147 FEET FROM P LINE AT ANNETTE, *MB: CODE: ADL1 LOC: ON N GALVEZ 146' PL ANNETTE 10' OUTSIDE 2' INSIDE ****/ | 2017-10-17 | REPLACED 5/8 WASHERS TO STOP
201701359401 | 2017-10-10 | LEAD/PLASTIC | 8506 | FORSHEY | JOLIET | WMTLK | ML METER LEAK ACCT# 146134-593848 METER#A397627 EXAMINE INLET AND OUTLET SERIVCE FOR LEAK LFLOODING GRASSY AREA METER BOX UNDER WATER, CARS ROLLING OVER METER 12/04/17 JOB UPGRADED TO 1ST AM PER INSP C PLAINS AREA FLOODED (FCP) /** 1) MN: A309147 SN: 0078006, *TAP: SIZE: B LOC: 73 FEET FROM P LINE AT JOLIET, *MB: CODE: ADLN LOC: 73FT FROM PL JOLIET ON FORSHEY ****/ | 2017-12-05 | EXCAVATED A 2 X 4 CUT IN CONCRETE SIDEWALK TO REPAIR A 5/8 INLET SERVICE LEAK PLASTIC INLET AND LEAD OUTLET UNDERNEATH A 3'' PLASTIC TUBING CHANGED THE COCK RAISE METER BOX UP TO GRADE & REPLACED THE OUTLET WITH 8 FT OF 3/4 PVC PIPE BACKFILLED & DRESSUP WITH RIVERSAND AND COLDMILL METER WAS CHOKED SO I REPLACED IT. JOB COMPLETE 2 X 4 CUT S/W JOB COMPLETE,,,OLD METER A397627 FACT:14103388 MAKE:HERSEY READ :1302 JEG
201701361201 | 2017-10-10 | LEAD/PLASTIC | 3729 | INWOOD AV | TALL OAKS DR | WMTLK | ML-METER LEAK ACCOUNT #232887-412854 METER #A156908 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A156908 SN: 0148061, *TAP: SIZE: B LOC: 286 FEET FROM P LINE AT TALL OAK DR, *MB: CODE: BDN1 LOC: ON INWOOSD 31.8FT FROM TALL OAK 8FT INSIDE CURB ****/ | 2017-10-27 | EXAMINE METER FOR LEAK FOUND LEAK ON OUTLET EXCAVATED ROUND METER TO MAKE REPAIRS CLEANED SIDEWALK WITH SOAP AND WATER
201701362501 | 2017-10-10 | LEAD | 1016 | LOUISA | ST CLAUDE AV | WILK | MI- LEAK IN SIDEWALK CHANFED FROM 1018 LOUISA INLET SERVICE LEAK AT CURB GETTING OFF IN DCB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-10-24 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA...NO METER
201701362601 | 2017-10-10 | LEAD | 1800 | LAPEYROUSE |  | WILK | MI METER BOX LEAKING INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A261896 SN: 0039894, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: AFH LOC: SIDE ST UNDER LAST WINDOW 47' P.L. LAPEYROUSE ****/ | 2017-10-24 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH HANDWHEEL TO STOP LEAK BACKFILL + CLEANED THE AREA
201701362901 | 2017-10-10 | LEAD | 40 | VIVIAN CT | HUNTLEE DR | WILK | MI- LEAK IN SIDEWALK EXAMINE INLET SERVICE FOR LEAK NEAR SIDEWALK /** 1) MN: A317615 SN: 0117658, *TAP: SIZE: A LOC: 264 FEET FROM P LINE AT HUNTLEE DR, *MB: CODE: BFK LOC: ON VIVIAN CT., 266' FROM P.L. HUNTLEE DR., 4' OUT- ****/ | 2017-12-02 | EXAMINED AND FOUND 5/8 INCH METER WASHER LEAKING ON INLET SIDE OF METER REPLACED METER BOX WASHERS
201701363801 | 2017-10-11 | LEAD | 8012 | SYCAMORE | SHORT | WILK | ***********PICKUP*************** BAD BLEEDER VALVE MN#A366192 ACC#116275-580315 /** 1) MN: A318294 SN: 0072303, *TAP: SIZE: A LOC: 162 FEET FROM P LINE AT CARROLLTON AVE S, *MB: CODE: AFN2 LOC: ON SYCAMORE 116FT FROM PL OF S CARROLLTON AVE ****/ | 2017-12-19 | EXCAVATED IN MUDPLOT ON INLET LEAK MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVER SAND ON LEAD LINE. LJF
201701365701 | 2017-10-11 | LEAD | 4866 | MAGAZINE | UPPERLINE | WILK | ML- METER LEAK ACCT#185903-560835 METER#A429529 INLET SERVICE LEAK BEHIND CURB COCK FLOODING SIDEWALK 03/21/17 CUSTOMER STATES BEEN LEAKING FOR 2 YEARS (KSW) /** 1) MN: A334178 SN: 0024854, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT MAGAZINE, *MB: CODE: BFLT LOC: ON UPPERLINE 75.6 FT PL MAGAZINE ****/ DOTTIE READY 4-3-18 EXP 4-23-18 | 2018-04-04 | EXCAVATED IN BRICK SIDEWALK REPAIR 5/8 STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND ALSO PUT BRICK BACK IN SIDEWALK JOB REFER TO ZONE 3 TO TAKE OUT LEAD LINE OUT FROM WATER MAIN TO METER BOX
201701367301 | 2017-10-11 | LEAD/PLASTIC | 1215 | S SARATOGA | CLIO | WILK | LEAK IN STREET ********J.MARSHALL @ 13:10PM******** INLET SERVICE LEAK IN ASPHALT STREET CAUSING A LARGE DEPRESSION, FLOODING AREA GETTING OFF IN DCB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-10-11 | ARRIVED AT JOB TO FINE 6X8 HOLE IN ASPHALT STREET WITH WATER PUSING OUT OF IT AFTER PUMPING WATER DOWN WE DUG 2FT BY SHOVEL AND FOUND A BROKEN LEAD LINE WE REMOVED LEAD AND RECONNECT LINE TO THE SERVICE ON A EMPTY LOT AND BAC FILLED BY EXCAVATOR
201701368701 | 2017-10-11 | LEAD | 2100 | ST PHILIP | N JOHNSON | WMLK | MI- LEAK IN STREET **********DAMAGE CLAIM********** BROKEN WATER MAIN BY GIBBS CONSTRUCTION /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-01-07 | EXCAVATED 4 X 6 MUDPLOT,FOUND LEAK ON ABANDON 3/4 INLET SERVICE.MADE REPAIRS ON INLET,BACKFILL JOB WITH RIVERSAND.
201701368901 | 2017-10-11 | LEAD/PLASTIC | 1823 | HORACE | COLUMBUS | WOLK | ML- METER LEAK MTR.# A-330960 OUTLET SERVICE LEAK IN THE GRASS FLOODING THE DITCH *****PER C PLAINS ( B ) LEAVE IN SYSTEM /** 1) MN: A330960 SN: 0172314, *TAP: SIZE: B LOC: 1 FEET FROM P LINE AT HORACE, *MB: CODE: AK2 LOC: ON MAGELLAN 1' OUTSIDE PL PL HORACE 4' OUTSIDE PL ****/ | 2017-10-30 | EXAMINED METER AND SURROUND AREA OF METER NO LEAK WAS FOUND METER TESTED TO BE WORKING ACCURATELY
201701369001 | 2017-10-11 | LEAD | 1307 | MONTEGUT | URQUHART | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: 000000 SN: 0063752, *TAP: SIZE: B LOC: 35 FEET FROM P LINE AT URQUHART, *MB: CODE: BEL2 LOC: METER ON MONTEGUT 35 FT FROM PL URQUHART ****/ | 2017-10-23 | EXCAVATED 2 X 2 MUD PLOT MADE REPAIR ON ABANDON INLET SERVICE LINE BACKFILL AND CLEANED THE AREA
201701369101 | 2017-10-11 | LEAD | 1240 | BARTHOLOMEW | URQUHART | WVLK | WATER LEAK - VALVE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS /** 1) MN: A188157 SN: 0067504, *TAP: SIZE: B LOC: 46 FEET FROM P LINE AT BARTHOLOMEW, *MB: CODE: OOOO LOC: 46' P/L BARTHOLOMEW 8' OUTSIDE 3' INSIDE CURB ****/ | 2017-10-24 | EXCAVATED 4 X 10 ASPHALT STREET CUT FOUND 6 INCH WATER VALVE LEAKING REFER TO ZONE 4 FOR REPAIRS TO MADE
201701369201 | 2017-10-11 | LEAD | 4024 | N ROBERTSON | MAZANT | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A309646 SN: 0075206, *TAP: SIZE: B LOC: 178 FEET FROM P LINE AT BARTHOLOMEW, *MB: CODE: CDL1 LOC: ON N ROBERTSON ST 184' FROM PL BARTHOLOMEW ****/ | 2017-10-23 | EXCAVATED 2 X 2 DRIVEWAY CUT MADE REPAIR IN INLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201701369301 | 2017-10-11 | LEAD | 3501 | ST CLAUDE AV |  | WMTLK | WATER LEAK - METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS /** 1) MN: SN: 0056836, *TAP: SIZE: B LOC: 76 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: DH LOC: ** 2) MN: C007440 SN: 0166330, *TAP: SIZE: C LOC: 70 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: OOOO LOC: ON GALLIER 70' FROM PL ST CLAUDE AVE 7' OUTSIDE PL ****/ | 2017-10-24 | REPLACED 5/8 INCH WASHERS TO STOP LEAK
201701369701 | 2017-10-11 | LEAD | 1339 | BARTHOLOMEW | N VILLERE | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A319244 SN: 0066046, *TAP: SIZE: A LOC: 299 FEET FROM P LINE AT URQUHART, *MB: CODE: CDL1 LOC: ON BARTHOLOMEW, 299' FROM P.L. URQUHART ****/ | 2017-10-23 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH WASHERS TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201701369801 | 2017-10-11 | LEAD | 3723 | N VILLERE | PAULINE | WMTLK | WATER LEAK - METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS /** 1) MN: B032392 SN: 0118235, *TAP: SIZE: B LOC: 185 FEET FROM P LINE AT INDEPENDENCE, *MB: CODE: BDKO LOC: ON NO. VILLERE, 185' FROM P.L. INDEPENDENCE, 7' ****/ | 2017-10-23 | FOUND NO LEAK REMOVED PVC PIPE OUT OF METER BOX AND TURNED METER BOX COCK OFF ALSO REMOVED THE HANDWHEEL
201701370101 | 2017-10-11 | LEAD/PLASTIC | 6151 | KINGSTON CT | AURORA DR | WILK | ML-METER LEAK ACCOUNT #234234-419413 METER #A217605 INLET SERVICE LEAK IN STREET /** 1) MN: A217605 SN: 0154072, *TAP: SIZE: B LOC: 38 FEET FROM P LINE AT AURORA DR, *MB: CODE: CD LOC: ON KINGSTON 38' FROM PL AURORA DR 10' OUTSIDE PL 2 ****/ | 2018-01-03 | EXCAVATED METER BOX AND FOUND LEAK ON OUTLET BROKE CONCRETE AROUND METER BOX AND REPLACED HANDWHEEL
201701373001 | 2017-10-12 | LEAD | 2220 | FRENCHMEN | N MIRO | WMBK | MI- CUSTOMER STATES METER BOX BROKEN METER# A 224210 ACCT# 193417-495268 BROKEN LOWER METER BOX /** 1) MN: A224210 SN: 0028431, *TAP: SIZE: B LOC: 127 FEET FROM P LINE AT MIRO N, *MB: CODE: AD LOC: 127' P/L N MIRO 8' OUTSIDE 2' INSIDE CURB ****/ | 2017-10-25 | REPLACED BROKEN METER BOX CASING
201701375601 | 2017-10-12 | LEAD/PLASTIC | 2801 | SULLEN PL |  | WMTLK | LOCATION ID-232075 MTR-A337553 BAD METER LEAK/AREA FLOODED /** 1) MN: A199448 SN: 0144915, *TAP: SIZE: B LOC: 32 FEET FROM P LINE AT SIMPSON PL, *MB: CODE: AFHL LOC: ON SULLEN 32FT FROM SIMPSON 6FT OUTSIDE ****/ | 2017-11-02 | EXCAVATED METER EXPSOED INLET AND OUTLET OBSERVED LEAK ON BOX COCK REPAIED LEAK REPLACED OLD HANDWHEEL BACKFILLED AND DRESSED UP WITH SAND
201701376001 | 2017-10-12 | LEAD | 2231 | N CLAIBORNE AV | MARIGNY | WMTLK | ACCOUNT# 155934-704890. METER#A405456. THE METER HAS WATER COMING FRON THE SIDES OF THE METER. 10/13/17 LEAK HAS GOTTEN WORSE PER SR#12817785 (AJR) /** 1) MN: A267032 SN: 0042693, *TAP: SIZE: B LOC: 42 FEET FROM P LINE AT MARIGNY, *MB: CODE: CFLM LOC: 43FT FROM PL MARIGNY ****/ | 2017-10-25 | REPLACED METER AND 5/8 WASHERS TO STOP LEAK OLD METER A405456 FACTORY: 14111218 MAKE: HERSEY READ: 527
201701376601 | 2017-10-12 | LEAD | 6121 | HURST | HENRY CLAY AV | WILK | ML- METER LEAK METER#A176192 ACCT#116336-562708 INLET LEAK AT THE SIDEWALK 03/13/18 LEAK NOW CAUSING A DEPRESSION UNDER SIDEWALK PER INSPC L GOMEZ (AJR) /** 1) MN: A134833 SN: 0121271, *TAP: SIZE: A LOC: 67 FEET FROM P LINE AT HENRY CLAY AVE, *MB: CODE: CFK6 LOC: ON HURST 68FT FROM HENRY CLAY ****/ | 2018-03-28 | EXAMINE IN SIDEWALK ON INLET LEAK MADE ALL REPAIRS TO STOP LEAKBACK FILLED WITH RIVERSAND AND COLD MILL LEAD LINE
201701379101 | 2017-10-13 | LEAD | 2523 | PAUGER |  | WILK | ML- METER LEAK MTR# A 426570 ACCT# 129875-494655 *****CUSTOMER OUT OF WATER***** ZONE 4 J GILLIAM @ 10:24 INLET SERVICE LEAK /** 1) MN: A287401 SN: 0059125, *TAP: SIZE: A LOC: 158 FEET FROM P LINE AT ROMAN S, *MB: CODE: BDN LOC: 156FT FROM LSPL ROMAN ****/ | 2017-10-13 | EXAMINED 4X 6 LIMESTONES IN GUTTER BOTTOM FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND + COLDMILL
201701380601 | 2017-10-13 | LEAD | 7224 | PONTCHARTRAIN BL | ROBERT E LEE BL | WMTLK | ML- METER LEAK METER# A323436 ACCT# 130781-599473 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A323436 SN: 0133798, *TAP: SIZE: A LOC: 176 FEET FROM P LINE AT ROBERT E LEE W, *MB: CODE: AFL6 LOC: ON PONTCHARTRAIN 175FT FROM PL ROBERT E LEE ****/ | 2018-06-02 | EXCAVATED IN CONCRETE DRIVEWAY. REPAIR INLET & OUTLET SERVICE LINES. ALSO RAISE TO GRADE. DRESS UP WITH RIVERSAND & COLD MILL REFER TO ZONE 1 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201701381901 | 2017-10-13 | LEAD | 2102 | CHARBONNET | N GALVEZ | WILK | MI LEAK IN VACANT METER BOX INLET SERVICE LEAK ON ABANDON SERVICE IN FRONT VACANT LOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-11-04 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 3/4 INCH ABANDON INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201701382801 | 2017-10-13 | LEAD/PLASTIC | 811 | JEWEL |  | WOLK | ML-METER LEAK ACCT#178069-535828 METER#C008784 OUTLET SERVICE WITH CONSTANT REG IN MUDPLOT FLOODING SIDEWALK 10/29/17 LEAK GETTING WORSE (NLD) /** 1) MN: C008784 SN: 0123532, *TAP: SIZE: C LOC: 137 FEET FROM P LINE AT SERVITUDE, *MB: CODE: GK7 LOC: 141' P/L SERVITUDE 3' OUTSIDE 10' INSIDE CURB ****/ | 2018-05-27 | EXCAVATED IN MUD PLOT AND REPLACED 1" OUTLET TO PROPERTY MUD MADE REPAIRS ON 1" TAP ON 8" WATER MAIN BACKFILLED AREA
201701385301 | 2017-10-14 | LEAD | 49 | ORIOLE | BEAUREGARD DR | WILK | METER LEAK C-22623 INLET SERVICE LEAK ON THE SIDEWALK (C) /** 1) MN: C022623 SN: 0109311, *TAP: SIZE: C LOC: 763 FEET FROM P LINE AT BEAUREGARD AVE, *MB: CODE: AFK4 LOC: 762FT FROM PL BEAUREGARD AVE 3' OUTSIDE PL 11' IN ****/ | 2018-01-28 | EXCAVATED AND REPAIRED INLET SERVICE INISDE METER BOX
201701386301 | 2017-10-15 | LEAD | 2820 | ST CLAUDE AV | ST FERDINAND | WMTLK | ML- METER LEAK METER#A372285 ACCT#114086-426690 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A295839 SN: 0056898, *TAP: SIZE: A LOC: 160 FEET FROM P LINE AT ST FERDINAND, *MB: CODE: BDK LOC: 160FT FROM LRPL ST FERDINAND METER CLAUDE AVE ****/ | 2017-10-27 | EXCAVATED 3 X 2 MUD PLOT REPAIR INLET SERVICE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201701391601 | 2017-10-16 | LEAD | 1304-06 | KENTUCKY | URQUHART | WMTLK | WM - LEAK IN THE SIDEWALK CHANGED FROM 1301 KENTUCKY EXAMINE INLET AND OUTLET SERVICE LEAK /** AT 1304: 1) MN: C016947 SN: 0053524, *TAP: SIZE: C LOC: 22 FEET FROM P LINE AT URQUHART, *MB: CODE: ADL2 LOC: ON KENTUCKY 23FT FROM URQUHART ****/ | 2017-10-30 | EXCAVATED 3 X 2 MUD PLOT REPLACED 1 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201701392001 | 2017-10-16 | LEAD/PLASTIC | 2476 | PRANCER |  | WMTLK | ML METER LEAK ACCOUNT #229895410338 METER # A396465 EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A149107 SN: 0133373, *TAP: SIZE: B LOC: 47 FEET FROM P LINE AT PRANCER, *MB: CODE: B LOC: ON FIESTA DR 46FT FROM P.L. PRANCER 7FT OUTSIDE P. ****/ | 2017-10-31 | EXCAVATED METER FOUND LEAD ON OUTLET TRACED LEAD LINE TO PROPERTY REPLACED WITH PLASTIC TUBING REPLACED HANDWHEEL AND BROKEN SERVICE COCK ON INLET AD OUTLET RAISED TO GRADE
201701394101 | 2017-10-16 | LEAD | 1414 | MANDEVILLE | N VILLERE | WMTLK | ML- METER LEAK AT METER# A 429924 ACCT# 115827-482156 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A215504 SN: 0044685, *TAP: SIZE: A LOC: 90 FEET FROM P LINE AT VILLERE N, *MB: CODE: AE5 LOC: ON MANDEVILLE 89.6FT FROM PL OF N VILLERE ****/ | 2017-10-27 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201701395202 | 2017-10-27 | LEAD | 728 | MOSS |  | WILK | EXCAVATED 3 X 2 MUD PLOT FOUND LEAK COMING OUT THE STREET REFER BACK TO ZONE 4 BACKFILL AND CLEANED THE AREA /** 1) MN: A187947 SN: 0089120, *TAP: SIZE: Y LOC: 102 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: CDLN LOC: ON MOSS,100' FROM P.L. ORLEANS AVE.,8' OUTSIDE ****/ | 2017-10-30 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 1 INCH CONTROLLING LINE BACKFILLED + DRESSED UP AREA
201701398001 | 2017-10-17 | LEAD | 803 | N BROAD |  | WILK | ML-- METER LEAK METER # A400922 ACCT# 109800-520849 INLET SERVICE LEAK N SIDEWLK FLOODING SIDEWALK /** 1) MN: A270296 SN: 0042752, *TAP: SIZE: B LOC: 40 FEET FROM P LINE AT ST ANN, *MB: CODE: ADM4 LOC: 40' P.L. ST ANN ****/ | 2017-10-26 | EXCAVATED 3 X 2 SIDEWALK CUT REPALCED 3/4 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201701401501 | 2017-10-17 | LEAD/PLASTIC | 3718 | PRESTON PL | BERKLEY DR | WMTLK | MI- LEAK IN STREET EXAMINE INLET AND OUTLET SERVICE ON SIDEWALK FOR A LEAK /** 1) MN: A273459 SN: 0145696, *TAP: SIZE: B LOC: 25 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: AD LOC: ON PRESTON PL 2.5' FROM DPL BERKLEY DR 2'INSIDE CU ****/ | 2017-11-02 | EXCAVATED METER EXPOSED INLET AND OUTLET SERVICE LINE OBSERVED LEAK ON PLASTIC TUBING BEHIND BOX COCK REPAIRED LEAK BACKFILLED AND DRESSED UP WITH SAND
201701408002 | 2017-12-04 | LEAD/PLASTIC | 523 | WAGNER |  | WILK | WENT TO JOB AND CAR WAS PARKED ON METER CALLED HOME OWNER AND THEY SAID THE CAR COULD NOT BE MOVED CAR WANT START DID WHAT WE COULD WITH THE ALLOWED SPACE NEED MACHINE AND NEED CAR MOVED /** 1) MN: A119936 SN: 0131769, *TAP: SIZE: A LOC: 168 FEET FROM P LINE AT ELIZA, *MB: CODE: BD LOC: ON WAGNER 166FT FROM P.L. ELIZA 7FT OUTSIDE P.L. ****/ | 2018-06-20 | EXAMAINED AREA CLEANED OUT METER BOX EXCAVATED METER BOX TRACED LEAK ON INLET SERVICE ALSO OBSERVED LEAK ON HANDWHEEL REPAIRED LEAK RAISED TO GRADE BACKFILLED CLEANED AREA NOTE USED AIR GUN TO BREAK THROUGH ROCK AND SHELL BED LEAD FOUND ON INLET
201701411201 | 2017-10-18 | LEAD/PLASTIC | 1014 | 3RD |  | WOLK | LOCATION ID-106002 MTR-A421846 METER LEAK OUTLET SERVICE LEAK BEHIND HANDWHEEL, CONSTANT REG ON METER /** 1) MN: A306204 SN: 0021924, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT CONSTANCE, *MB: CODE: AEN1 LOC: 112'; P.L. CONSTANCE ****/ | 2017-10-26 | EXAMINED FOR LEAK FOUND LEAK AND REPAIRED LEAK ON INLET AND OUTLET
201701411401 | 2017-10-18 | LEAD/PLASTIC | 2113 | ANNUNCIATION | JOSEPHINE | WILK | ML METER LEAK ACCT# 146324-542067 METER# A251411 INLET SERVICE LEAK BEHIND CURB COCK /** 1) MN: A251411 SN: 0078188, *TAP: SIZE: A LOC: 80 FEET FROM P LINE AT JOSEPHINE, *MB: CODE: CELN LOC: 80FT FROM PL JOSEPHINE ON ANNUNCIATION ST ****/ | 2017-12-07 | ARRIVED ON JOB SITE EXAMINED METER BROKE CONCRETE EXCAVATED BY HAND FOUND LEAK ON INLET AND REPAIR
201701413701 | 2017-10-19 | LEAD/PLASTIC | 8306 | OLEANDER | DANTE | WOLK | ML - METER LEAK ACCOUNT NUMBER - 141590-593522 METER NUMBER - A295531 CUSTOMER STATES METER IS LEAKING AGAIN EXAMINE OUTLET SERVICE UP TO PROPERTY LINE, CONSTANT REG ON METER /** 1) MN: A295531 SN: 0072894, *TAP: SIZE: B LOC: 51 FEET FROM P LINE AT DANTE, *MB: CODE: ADL2 LOC: ON OLEANDER, 52' FROM P.L. DANTE ****/ | 2017-12-21 | EXCAVATED IN MUDPLOT OVER A 3/4 INLET SERVICE LEAK. LEAD INLET AND PLASTIC OUTLET. REPLACED 10 FT OF LEAD WITH 3/4 PVC PIPE FROM THE CURB TO THE METERBOX NO METER. JEG
201701415401 | 2017-10-19 | LEAD | 1938 | TREASURE | ANNETTE | WILK | ML METER BOX LEAK INLET SERVICE LEAK ON ABANDON SERVICE IN FRONT OF VACANT LOT FLOODING GUTTER BOTTOM GETTING OFF IN DCB /** 1) MN: A311334 SN: 0095399, *TAP: SIZE: A LOC: 36 FEET FROM P LINE AT ANNETTE, *MB: CODE: BD LOC: 288FT FROM PL ALLEN ON TREASURE ****/ | 2017-11-13 | EXCAVATED IN MUDPLOT. REPAIR 5/8 STOP & WASTE. DRESS UP WITH RIVER SAND REF TO ZONE 5 TO TAKE LEAD LINE OUT THE GROUND. JOB COMPLETE LJF
201701415601 | 2017-10-19 | LEAD | 836 | HENRY CLAY AV | CAMP | WILK | ML METER LEAK ACCT# 101741-562975 METER# B027993 INLET SERVICE ON ABANDON LINE 03/02/18 LEAK NOW GUSHING PER SR#12834104 (AJR) /** 1) MN: B027993 SN: 0025401, *TAP: SIZE: A LOC: 258 FEET FROM P LINE AT HENRY CLAY AVE, *MB: CODE: CDM1 LOC: ON HENRY CLAY AVE.,258' FROM U.S.P.L. MAGAZINE ****/ | 2018-03-08 | ARRIVED ON JOB EXCAVATED IN MUDPLOT FOUND LEAD SERVICE LEAKING BUT NEED TO GO IN STREET TO FIX LEAK
201701416501 | 2017-10-19 | LEAD/PLASTIC | 721 | NUNEZ | SLIDELL | WMTLK | ML METER LEAK ACCT# 224279-401009 METER# A321252 EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A236274 SN: 0023883, *TAP: SIZE: A LOC: 132 FEET FROM P LINE AT SLIDELL, *MB: CODE: CF LOC: ON NUNEZ 132FT FROM SLIDELL ****/ | 2017-11-02 | EXCAVATED METER EXCAVATED FOR LEAK ABSERVED ON BOX COCK LEAD ON INLET SERVICE UNABLE TO COMPLETE DUE TO TIME...JOB CONTINUED
201701416502 | 2017-11-03 | LEAD/PLASTIC | 721 | NUNEZ | SLIDELL | WMTLK | EXCAVATED METER EXCAVATED FOR LEAK ABSERVED ON BOX COCK LEAD ON INLET SERVICE UNABLE TO COMPLETE DUE TO TIME /** 1) MN: A236274 SN: 0023883, *TAP: SIZE: A LOC: 132 FEET FROM P LINE AT SLIDELL, *MB: CODE: CF LOC: ON NUNEZ 132FT FROM SLIDELL ****/ | 2017-11-03 | EXCAVATED METER REPLACED SERVICE INLET COCK BACKFILLED WHOLE AND DRESSED WITH SAND
201701416901 | 2017-10-19 | LEAD | 3104 | CLEVELAND AV | S SALCEDO | WMTLK | ML- METER LEAK ACCT#122378-532318 METER#A412192 EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A344937 SN: 0039214, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT SALCEDO N, *MB: CODE: ADL6 LOC: METER ON CLEVELAND AVE,47.6 FT FROM PL N SALCEDO ****/ | 2017-11-02 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 METER BOX COCK TO STOP LEAK BACKFILLED NAD CLEANED THE AREA
201701417701 | 2017-10-19 | LEAD/PLASTIC | 723 | DUFOSSAT | LAUREL | WILK | MI METER BOX LEAKING NO METER IN BOX, CURB COCK IN OFF POSITION WATER PASSINGTHROUGH, FLOODING GRASS & GUTTER BOTTOM /** 1) MN: A287300 SN: 0050476, *TAP: SIZE: A LOC: 131 FEET FROM P LINE AT CONSTANCE, *MB: CODE: ADK LOC: ON DUFOSSAT 132' FROM RPL CONSTANCE ****/ DOTTIE READY 5-24-18 EXP 6-13-18 | 2018-05-23 | ARRIVED AT THE ABOVE LOCATION MADE REPAIR ON THE INLET .RAN PLASTIC FROM THE INLET TO THE CURB AND ALSO REMOVE THE LEAD FROM THE OUTLET AND ALSO RAISE THE METER BOX UP AND THEN CLEANED THE AREA ALSO NEED CREW TO REMOVE THE LEAD LINE FROM THE CURB TO THE MAIN.
201701418301 | 2017-10-19 | LEAD | 2820 | METROPOLITAN | INDUSTRY | WILK | ML--METER LEAK ACCT# 159976-434400 METER# A350271 INLET SERVICE LEAK IN THE SIDEWALK /** 1) MN: A284130 SN: 0098260, *TAP: SIZE: B LOC: 135 FEET FROM P LINE AT INDUSTRY, *MB: CODE: AGK2 LOC: ON METROPOLITAN 136FT FR PL INDUSTRY 2' OUTSIDE PL ****/ | 2017-11-13 | EXCAVATED IN CONCRETE DRIVEWAY. REPAIR 3/4 LEAD LINE DRESS UP WITH RIVER SAND & COLD MILL. REF TO ZONE 5 TO TAKE LEAD LINE OUT THE GROUND. JOB REF TO PAVE 3 X 4 CONCRETE D/W LJF
201701420701 | 2017-10-19 | LEAD | 2664 | VERBENA | FRANKLIN AV | WILK | MI--LEAK IN THE STREET INLET SERVCE LEAK /** 1) MN: A326696 SN: 0088489, *TAP: SIZE: A LOC: 464 FEET FROM P LINE AT FRANKLIN AVE, *MB: CODE: ADL LOC: 463FT FROM PL FRANKLIN AVE ****/ | 2017-11-11 | EXCAVATED IN ASPAHLT STREET + REPLACED 12 FT OF 3/4 INCH LEAD INLET SERVICE LINE COMPACTED BACKFILL + DRESSED UP AREA
201701422401 | 2017-10-20 | LEAD/PLASTIC | 106 | SHARON DR | PONTCHARTRAIN BL | WMTLK | ML-METER LEAK ACCOUNT #183570-597142 METER #A419947 EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A153724 SN: 0134941, *TAP: SIZE: B LOC: 115 FEET FROM P LINE AT PONTCHARTRAIN BLVD, *MB: CODE: CDM1 LOC: ON SHARON DR 114' FROM PL PONTCHARTRAIN BLVD 8' OU ****/ | 2017-11-21 | EXCAVATED A 4 X 10 TRENCH IN MUDPLOT OVER A 5/8" INLET SERVICE LEAK ( PLASTIC INLET & LEAD OUT LET CHANGE THE COCK AND RAISE METER BOX UPTO GRAE & REPLACED 8FT OF LEAD OUTLET WITH 3/4" PVC PLASTIC FROM METER TO PROPERTY FOUND 5/8 METR WAS CHOKED SO I CHANGED IT JOB CONT - TO REPLACE LEAD FROM MAIN TO METER BOX *************OLD METER INFO**************** METER:A419947 FAC:15486193 MAKE:HERSEY READ:1260
201701422402 | 2017-11-22 | LEAD | 106 | SHARON DR | PONTCHARTRAIN BL | WSNR | EXCAVATED A 4 X 10 TRENCH IN MUDPLOT OVER A 5/8" INLET SERVICE LEAK ( PLASTIC INLET & LEAD OUT LET CHANGE THE COCK AND RAISE METER BOX UPTO GRAE & REPLACED 8FT OF LEAD OUTLET WITH 3/4" PVC PLASTIC FROM METER TO PROPERTY FOUND 5/8 METR WAS CHOKED SO I CHANGED IT REPLACE LEAD SERVICE FROM MAIN TO METER BOX /** 1) MN: A153724 SN: 0134941, *TAP: SIZE: B LOC: 115 FEET FROM P LINE AT PONTCHARTRAIN BLVD, *MB: CODE: CDM1 LOC: ON SHARON DR 114' FROM PL PONTCHARTRAIN BLVD 8' OU ****/ | 2018-11-06 | JOB WILL BE RE- SCHEDULE AT A LATER DATE DO TO PAVEMENT BACK LOG
201701424001 | 2017-10-20 | LEAD/PLASTIC | 2025 | WAGNER | HERO BL | WOLK | ML METERLEAK MTR#D006988 ACCT#238848-406016 CONS REG ON METER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-10-30 | EXAMINED WATER METER EXAMINED SURROUNDING BLOCK NO LEAK FOUND
201701428403 | 2017-12-14 | LEAD/PLASTIC | 306 | WHITNEY AV | PELICAN | WILK | STILL TO MAKE REPAIRS /** 1) MN: A150455 SN: 0108090, *TAP: SIZE: A LOC: 52 FEET FROM P LINE AT PELICAN AVE, *MB: CODE: BE LOC: ON WHITNEY 51FT FROM PELICAN ****/ | 2017-12-14 | BROKE CONCRETE REPLACING LEAD LINE EXCAVATED TO PROPERTY REPLACE LEAD LINE WITH PLASTIC TUBING BACKFILLED WITH SAND AND COAL MILL LEAD LINE COMING FROM MAIN NEED MACHINE TO REMOVE
201701429401 | 2017-10-22 | LEAD/PLASTIC | 168 | PINEWOOD CT | CYPRESS ACRES DR | WMTLK | LOCATION# 236010 CUSTOMER# 407304 METER# A414085 INSPECTOR MET W/CUSTOMER DID INSIDE/OUTSIDE INSPECTION FOUND NO FIXTURE PROBLEMS INSIDE/DID OUTSIDE INSPECTION FOUND LEAK CAN'T DETERMINE WHERE IT'S COMING FROM. PLEASE REPAIR /** 1) MN: A319650 SN: 0164448, *TAP: SIZE: A LOC: 10 FEET FROM P LINE AT CYPRESS ACRES DR, *MB: CODE: OOO LOC: ON PINEWOOD CT 10FT FROM PL CYPRESS ACRES ****/ | 2017-11-02 | ARRIVED ON JOB SITE EXAMINED METER EXCAVATED BY HAND FOUND LEAK ON INLET AND REPAIRED
201701429701 | 2017-10-22 | LEAD | 1641 | CALHOUN | MARQUETTE PL | WILK | ML- METER LEAK METER#C019436 ACCT#143640-567845 EXAMINE INLET SERVICE FOR A LEAK 04/23/18 METER LEAK FLOODING AREA PER SERVICE REQUEST #12838995 (FCP) /** 1) MN: C019436 SN: 0075041, *TAP: SIZE: D LOC: 34 FEET FROM P LINE AT MARQUETTE PL, *MB: CODE: BELM LOC: 1ST FRONT GET 6240 MARQUETTE 2ND METER 253' P.L. ****/ DOTTIE READY 4-17-18 EXP 5-7-18 | 2018-04-23 | ARRIVED ON JOB EXCAVATED IN MUD PLOT AND SIDEWALK FOUND LEAK ON 1" LEAD SERVICE BEHIND METER BOX COCK STOPPED LEAK TIED INTO LEAD.LEAD NEED TO BE REMOVED FROM METER BOX TO MAIN
201701431101 | 2017-10-23 | LEAD | 3139 | ST PETER | ORLEANS | WMTLK | ML- METER LEAK AT METER# A 404961 ACCT# 142179 - 540422 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER BOX UNDER WATER /** 1) MN: A329028 SN: 0073213, *TAP: SIZE: A LOC: 33 FEET FROM P LINE AT ST PETER, *MB: CODE: CDGK LOC: 1ST METER ON S RENDON 31' P/L ST PETER 7' OUTSIDE ****/ | 2017-10-26 | EXCAVATED 4 X 3 MUD PLOT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201701432901 | 2017-10-23 | LEAD/PLASTIC | 1483 | GRANADA DR |  | WOLK | UNABLE TO SET METER / METER BOX NEED TO BE RESET PLEASE REPAIR & SET 3/4 METER LOCATION: 302190 CUSTOMER HOME WAITING ON WATER!!!!!! BROKEN HANDWHEEL, ALSO RAISE AND SET 3/4 METER, HOUSE UNDER RENOVATION /** 1) MN: B022692 SN: 0108143, *TAP: SIZE: B LOC: 236 FEET FROM P LINE AT PERLITA, *MB: CODE: CDM LOC: ON GRANADA DR 236'FRM PL PERLITA 8' OUTSIDE PL 3' ****/ | 2017-10-30 | EXCAVATED IN MUDPLOT RENEWED 3/4" METER BOX SERVICE FROM INLET TO PROPERTY . INLET HAS PLASTIC , OUTLT HAS LEAD ALSO FOUND METER SET ALREADY RAISED MEETR BOX TO GRADE AND BACKFILLED JOB CONT- TO RENEW OUTLET SERVICE *****METER SET WITH ANOTHER METER********** METER:B041124 FACTORY:15510151 MAKE:HERSEY READ:0 METER:B041124FACTORY:15510151 MAKE:HERSEY READ:0
201701434201 | 2017-10-23 | LEAD/PLASTIC | 1330 | SHIRLEY DR | SOCRATES | WMTLK | ML-METER LEAK EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A277429 SN: 0095115, *TAP: SIZE: B LOC: 59 FEET FROM P LINE AT DE AMRAS, *MB: CODE: BDM4 LOC: ON SHIRLEY DR., 50' FROM P.L. DE ARMAS ****/ | 2017-11-09 | EXCAVATED METER BOX OBSERVED LEAK ON LEAK BOX COCK EXPOSED INLET AND OUTLET OBSERVED LEAD ON OUTLET EXCAVATED TO PROPERTY REPLACED LEAD LINE BACKFILLED CALLED FOR DRESS UP
201701436701 | 2017-10-23 | LEAD/PLASTIC | 1506 | MAGAZINE | RACE | WMTLK | ML METER LEAK ACCT# 107283-584587 METER# B023163 EXAMINE INLET/OUTLET SERVICE FORLEAK /** 1) MN: B030583 SN: 0000000, *TAP: SIZE: B LOC: 53 FEET FROM P LINE AT RACE, *MB: CODE: AD LOC: 55FT FROM URPL RACE ** 2) MN: A336483 SN: 0003951, *TAP: SIZE: G LOC: 6 FEET FROM P LINE AT RACE, *MB: CODE: MROC LOC: ON MAGAZINE, 8' FROM D.P.L. RACE, 9' OUTSIDE, 3' THERE ARE 3 MORE NOT LISTED. ****/ | 2017-11-16 | EXAMINED METER LEAK BROKE CONCRETE WITH MAUL EXPOSED LEAD LINE ON SERVICE COCK REPLACE BROKEN SERVICE COCK BACKFILLED AND LEFT CONE ON TOP JOB NEED COAL MAEL TO FINISH ROCKS NEED FOR PICKED UP NEAR CURB...JOB CONTINUED
201701440401 | 2017-10-24 | LEAD | 1663 | DUELS | BROAD PL | WILK | ML- METER LEAK MTR# A426701 ACCT.# 188621-492187 INLET SERVICE LEAK CAUSING METER BOX TO OVERFLOW /** 1) MN: A324208 SN: 0069621, *TAP: SIZE: B LOC: 80 FEET FROM P LINE AT NO. BROAD, *MB: CODE: CD1 LOC: ON DUELS, 83' FROM P.L. NO. BROAD, 8' OUTSIDE,2' ****/ | 2017-11-03 | REPLACED 5/8 WASHERS TO STOP LEAK
201701442301 | 2017-10-24 | LEAD | 1712 | EAGLE |  | WMTLK | CURB COCK LEAKING. PLEASE REPAIR METER A408981 LOC ID 135105 EXAMINE INLET/OUTLET SERVICE FOR LEAK INSIDE METER BOX /** 1) MN: A309165 SN: 0065893, *TAP: SIZE: A LOC: 101 FEET FROM P LINE AT GREEN, *MB: CODE: CDL6 LOC: ON EAGLE, 101' FROM P.L. GREEN ****/ | 2018-03-11 | EXCAVATED IN MUDPLOT.REPAIR 5/8 STOP AND WASTE AND REPLACE BOTTOM. DRESS UP WITH RIVERSAND. JOB REFERRED TO ZONE 1 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METERBOX
201701442401 | 2017-10-24 | LEAD/PLASTIC | 2723 | MONROE |  | WILK | ML-- METER LEAK METER # B040496 ACCT # 161544-592234 INLET SERVICE LEAK NEAR METER BOX AREA FLOODED /** 1) MN: B024853 SN: 0100073, *TAP: SIZE: C LOC: 139 FEET FROM P LINE AT BELFAST, *MB: CODE: BDO2 LOC: ON MONROE 141FT FROM PL OF BELFAST 9FT OUTSIDE PL ****/ | 2017-12-06 | EXCAVATED IN GRAVEL/ MUDPLOT OVER A 3/4 INLET SERVICE LEAK LEAD ON INLET CHANGED THE COCK RAISE METERBOX TO GRADE AND REPLACED THE OUTLET WITH 9 FT 3/4 PVC PIPE FROM METERBOX TO PROPERTY BACKFILLED AND DRESSUP WITH RIVERSAND & COLMILL. JEG
201701442801 | 2017-10-24 | LEAD | 1561 | GENTILLY BL | PONCE DE LEON | WILK | ML- METER LEAK METER#A371628 ACCT#148243-491464 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A336203 SN: 0049696, *TAP: SIZE: A LOC: 71 FEET FROM P LINE AT GENTILLY BLVD, *MB: CODE: BDHL LOC: ON FLORIDA AVE 71' FROM USPL GENTILLY BLVD ****/ | 2017-11-03 | EXCAVATYED 2 X 3 MUD PLOT MADE REPAIRS ON OUTLET SERVICE LINE AT PROPERTY BACKFILLED AND CLEANED THE AREA
201701445901 | 2017-10-25 | LEAD | 1019 | KENTUCKY | ST CLAUDE AV | WILK | ML- METER LEAK ACCT# 154747-581517 MTR# A349098 INLET SERVICE LEAK IN THE MUD PLOT FLOODING CURB /** 1) MN: A140092 SN: 0091235, *TAP: SIZE: A LOC: 156 FEET FROM P LINE AT RAMPART N, *MB: CODE: CDL LOC: ON KENTUCKY, 155.3' FROM P.L. NO. RAMPART,9' OUT- ****/ | 2017-11-13 | EXCAVATED IN GUTTER BOTTOM + REPLACED 5/8 INCH TO GRADE BACKFILLED + DRESSED UP AREA
201701448301 | 2017-10-25 | LEAD | 231 | S BROAD |  | WMBK | UNABLE TO CHANGE METER / CASING OVER WHEEL PLEASE REPAIR AND CHANGE MTR# C 007323 LOCATION: 108071 UPPER METER BOX CASING SHIFTED OVER HANDWHEEL, CHANGE METER /** 1) MN: C007323 SN: 0060989, *TAP: SIZE: C LOC: 62 FEET FROM P LINE AT PALMYRA, *MB: CODE: __ LOC: BROAD 59FT. LS PL. PALMYRA ****/ | 2017-11-06 | EXCAVATED 2 X 2 SIDEWALK REMOVED OLD METER TO NEW METER BACKFILLED AND CLEANED THE AREA,,,OLD METER C007323 FACTORY:17231809 MAKE:ROCKWELL READ: 2935
201701449202 | 2017-10-27 | LEAD | 5515 | S ROBERTSON | OCTAVIA | WLPR | PP-- POOR PRESSURE ACCT #144341-568405 METER # A246670 EXAMINE INLET FOR POOR PRESSURE /** 1) MN: A246670 SN: 0089547, *TAP: SIZE: B LOC: 123 FEET FROM P LINE AT OCTAVIA, *MB: CODE: BD23 LOC: ON SO. ROBERTSON, 123' FROM P.L. OCTAVIA,11' OUT- ****/ EMREGENCY DOTTIE CALLED 10-27-17 /** 1) MN: A246670 SN: 0089547, *TAP: SIZE: B LOC: 123 FEET FROM P LINE AT OCTAVIA, *MB: CODE: BD23 LOC: ON SO. ROBERTSON, 123' FROM P.L. OCTAVIA,11' OUT- ****/ | 2017-10-28 | REPLACED CHOKED 5/8 INCH METER AT ABOVE LOCATION AFTER REPLACED MENT FOUND 50 PSI OF PRESSURE AT OUTSIDE FAUCET,,,OLD METER A246670 FACTORY:34076126 MAKE:ROCKWELL READ:713
201701449501 | 2017-10-25 | LEAD/PLASTIC | 212 | RHODES AV | WESTCHESTER PL | WILK | ML-METER LEAK ACCT#226953-419612 METER #A128363 INLET SERVICE LEAK IN THE TREE ROOTS IN THE GRASS /** 1) MN: A128363 SN: 0130567, *TAP: SIZE: A LOC: 523 FEET FROM P LINE AT WESTCHESTER, *MB: CODE: CD LOC: ON RHODES AVE 523FT FROM P.L. WESTCHESTER 2FT OUT- ****/ | 2018-01-03 | EXAMINED LEAK ON METER EXCAVATED OUTLET SERVICED EXCAVATED THROUGH ROOTS WITH AXE EXPOSED OUTLET SERVICE LINE OBSERVED LEAK ON INLET AND OUTLET SERVICE REPAIRED LEAK BACKFILLED
201701449601 | 2017-10-25 | LEAD/PLASTIC | 3326 | PLYMOUTH PL | DOVER PL | WILK | ML- METER LEAK AT METER# A 364576 ACCT# 228647-414911 INLET SERVICE LEAK IN THE MUD PLOT IN THE GRASS BY THE CURB /** 1) MN: A317308 SN: 0126140, *TAP: SIZE: C LOC: 261 FEET FROM P LINE AT DOVER PL., *MB: CODE: BDLM LOC: ON PLYMOUTH PL., 235' FROM P.L. DOVER PL., 8' OUT- ****/ | 2018-01-03 | EXAMINED METER LEAK EXCAVATED METER OBSERVED LEAK ON OUTLET SERVICE REPAIRED LEAK BACKFILLED HOLE
201701451001 | 2017-10-25 | LEAD/PLASTIC | 2947 | MAGELLAN | MURL | WMTLK | ML METER LEAK METER# C024573 ACCT# 231442-406891 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: C024573 SN: 0141600, *TAP: SIZE: C LOC: 1 FEET FROM P LINE AT SOUTHLAWN BLVD, *MB: CODE: BDK2 LOC: ON MAGELLAN, 1' FROM P.L. SOUTHLAWN BLVD., 6' OUT- ****/ | 2017-11-22 | EXCAVATED METER OBSERVED LEAK ON INLET SERVICE EXPOSED OUTLET REPLACE FITTING ON STOP COCK JOB REPAIRED BACKFILLED AND DRESS UP WITH SANDRI
201701451601 | 2017-10-25 | LEAD | 2223 | N CLAIBORNE AV | MARIGNY | WILK | ML-METER LEAK ACCT#121858-482215 METER#A412643 EXAMINE INLET SERVICE AT SIDEWALK FOR LEAK /** 1) MN: A260264 SN: 0042641, *TAP: SIZE: A LOC: 119 FEET FROM P LINE AT MARIGNY, *MB: CODE: AF LOC: ON N CLAIBORNE AVE 119' FROM USPL MARIGNY ST ****/ | 2017-12-07 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201701454301 | 2017-10-26 | LEAD/PLASTIC | 2366 | ST THOMAS |  | WILK | PP-- POOR PRESSURE METER # A 413265 *******S.SLACK @ 10:08AM******** CHANGED FROM 2348 ST THOMAS INLET SERVICE LEAK @ VACANT LOT FLOODING AREA CAUSING POOR PRESURE TO AREA /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-10-26 | EXCAVATED AFTER SERCHING FOR METER EXPOSED LINE ON INLET FOUND LEAK ON INLET REPLACED BOX COCK AND PLACED BARREL ON TOP NEED SAND FOR DRESS UP NO METER IN METER BOX
201701455501 | 2017-10-26 | LEAD/PLASTIC | 4712 | MAGAZINE | BORDEAUX | WILK | ML-METER LEAK ACCT# 120706-561701 METER# B024329 INLET SERVICE LEAK BEHIND CURB COCK, CARS ROLLING OVER METER /** 1) MN: A283563 SN: 0051140, *TAP: SIZE: A LOC: 105 FEET FROM P LINE AT VALENCE, *MB: CODE: ADL LOC: ON MAGAZINE,105' FROM U.P.L. VALENCE ****/ | 2017-10-29 | EXCAVATED IN MUDPLOT AND REPLACED 5/8"CURB COCK ,BACKFILLED AND DRESSED UP AREA (3 FT. X 3 FT MUDPLOT..
201701458401 | 2017-10-26 | LEAD | 3119 | NASHVILLE AV | S ROBERTSON | WOLK | BAD LEAK COMING FROM OUTSIDE OF THE CASING. PLEASE REPAIR METER A380165 LOC ID 153282 OUTLET SERVICE LEAK /** 1) MN: A246923 SN: 0089127, *TAP: SIZE: B LOC: 141 FEET FROM P LINE AT JOHNSON S, *MB: CODE: CD LOC: ON NASHVILLE AVE., 140' FROM P.L. SO. JOHNSON,11' ****/ DOTTIE READY 11-1-17 EXP 11-21-17 | 2017-10-30 | EXAMINED THE LEAK INSIDE THE METER BOX AND DISCOVERED A BAD CURB COCK. WE CHANGED THE FITTING AND RESTORED THE CUSTOMER'S WATER. ***********OLD METER INFO************ METER:A431834 FACTORY:16357423 MAKE:HERSEY READ:21 LJF
201701460002 | 2017-11-10 | LEAD/PLASTIC | 8424 | APPLE |  | WMRE | METER BOX BURIED PLEASE LOCATIE AND SET A 5/8 METER LOCATION #303263 /** 1) MN: A351471 SN: 0073873, *TAP: SIZE: A LOC: 262 FEET FROM P LINE AT CAMBRONNE, *MB: CODE: CDLM LOC: ON APPLE, 262' FROM P.L. CAMBRONNE ****/ | 2017-11-19 | MADE A 4 X 4 SIDEWALK CUT EXCAVATED LOCATED AND RAISED A 5/8 METER TO GRADE LEAD ON THE INLET OLASTIC ON THE OUTLET. ALSO SET A 5/8 METER. REFER THAT CUT TO PAVING JEG
201701460501 | 2017-10-27 | LEAD | 3216 | ST PHILIP | N RENDON | WILK | WM LEAK BETWEEN THE SIDEWALK AND THE STREET INLET LEAK IN TREE ROOTS, FLOODING THE CURB (C) /** 1) MN: A292074 SN: 0036232, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT RENDON N, *MB: CODE: CDL LOC: METER ON ST PHILIP 134 FT FROM PL N RENDON ****/ | 2017-11-04 | EXCAVATED IN MUD PLOT THROUGH HEAVY TREE ROOTS + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE ALSO RAISED 5/8 INCH METER BOX BOTTOM TO GRADE BACKFILLED + DRESSED UP AREA
201701460901 | 2017-10-27 | LEAD | 2519 | ANNETTE | N DORGENOIS | WILK | WM - LEAK IN THE STREET AND THE SIDEWALK. INLET LEAK IN THE MUDPLOT FLOODING THE AREA GETTING OFF IN DCB (C) /** 1) MN: 000000 SN: 0073907, *TAP: SIZE: A LOC: 142 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CDL LOC: 145FT FROM PL DORGENOIS 7' OUTSIDE PL ****/ | 2017-11-10 | EXCAVATED 3 X 3 MUD PLOT RAISE METER BOX TO GRADE AND REPLACED 5/8 INCH METER BOX TO STOP LEAK BACKFILL AND CLEANED
201701461701 | 2017-10-27 | LEAD | 247 | S ROBERTSON | TULANE AV | WILK | MI- LEAK IN THE SIDEWALK INLET SERVICE LEAK @ THE SIDEWALK, SIDEWALK FLOODED ***LEFT 1 CONE FOR PROTECTION*** /** 1) MN: A151341 SN: 0024424, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT TULANE AVE, *MB: CODE: CELM LOC: RES 105FT FROM LSPL TULANE,METER ON S ROBERTSON ****/ | 2017-11-08 | EXCAVATED 4 X 6 CONCRETE SIDEWALK FOUND LEAK ON 5/8 ABANDON INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND + COLDMILL
201701462701 | 2017-10-27 | LEAD | 1229 | ST ANTHONY | ST CLAUDE AV | WILK | ML- METER LEAK METER# A409575 ACCT # 150064-486649 INLET SERVICE LEAK IN ON POSITION, ALSO RENEW OUTLET SERVICE /** 1) MN: A307880 SN: 0049514, *TAP: SIZE: A LOC: 146 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: BF25 LOC: ON ST ANTHONY 147FT FROM ST CLAUDE ****/ | 2017-11-10 | EXCAVATED 3 X 3 MUD PLOT REMOVED BAD METER AND REPLACED 5/8 INCH METER BOX COCK BACKFILL AND CLEANED THE AREA
201701464101 | 2017-10-27 | LEAD | 1124 | MANDEVILLE | MARAIS | WMTLK | WM LEAK ON THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE AT SIDEWALK FOR A LEAK /** 1) MN: A290563 SN: 0055976, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT MARAIS, *MB: CODE: CE LOC: 2ND BOX 46' P.L. MARAIS ****/ | 2017-11-16 | EXCAVATED 4 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201701468401 | 2017-10-29 | LEAD | 1556 | N ROCHEBLAVE | LAHARPE | WMRE | LOCATION ID# 117018 MTR# A199590 CAN'T LOCATE/METER BELOW GRADE /** 1) MN: A199590 SN: 0079368, *TAP: SIZE: A LOC: 103 FEET FROM P LINE AT LAHARPE, *MB: CODE: BFLM LOC: ON ROCHEBLAVE 105FT FROM LAHARPE ****/ | 2017-11-13 | LOCATED METER BOX NOT BELOW GRADE REMOVED LIMESTONE AND MUD OUT OF METER BOX
201701469102 | 2017-11-16 | LEAD/PLASTIC | 437 | VALLETTE | ELIZA | WILK | EXCAVATED METER AFTER FINDING IT WITH MEASUREMENT WHEEL EXAMINED BOTH LINE INLET AND OUTLET PLASTIC TUBING ON INLET FOUND NO LEAK LEAKING UNKNOWN COMING FROM UNDER STREET LEAD ON OUTLET FOUND NEED MACHINE TO BREAK THROUGH DRIVEWAY AND SIDEWALK /** 1) MN: A305327 SN: 0034111, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT ELIZA, *MB: CODE: ADL2 LOC: ON VALLETTE 75FT FROM ELIZA ****/ | 2018-02-24 | EXAMINED LEAKING AREA EXCAVATED IN STREET EXPOSED LEAD LINE EXPOSED 6" MAINE LEAK OBSERVED ON CORPORATION COCK REPLACED LEAD TO PLASTIC LINE BACKFILLED WITH SAND AND COAL MILL DRESS UP LEAK REPAIRED
201701469501 | 2017-10-29 | LEAD | 513 | DUMAINE | DECATUR | WMRE | LOCATION ID# 116304 MTR# A308844 METER BURIED/PLEASE LOCATE AND RAISE /** 1) MN: A308844 SN: 0021013, *TAP: SIZE: A LOC: 79 FEET FROM P LINE AT DECATUR, *MB: CODE: BEN1 LOC: 78FT FROM PL DECATUR ON DUMAINE ****/ | 2017-11-10 | LOCATED METER AT ABOVE LOCATION ALSO REMOVED CONCRETE FROM METER BOX
201701472302 | 2017-10-30 | LEAD | 633 | ST ROCH AV | ROYAL | WLPR | EXCAVATED 8 X16 CONCRETE BASE STREET CUT FOUND NO TAP ON WATER MAIN JOB CONTINUED TO MAKE REPAIRS LEAK WAS FOUND BY EARTH TECH BACKFILLED JOB WITH RIVERSAND + COLDMILL (633-631 ON SAME TAP) /** 1) MN: A190547 SN: 0087226, *TAP: SIZE: B LOC: 264 FEET FROM P LINE AT CHARTRES, *MB: CODE: BELN LOC: ON ST ROCH AVE 293FT FROM PL CHARTRES ****/ | 2017-10-31 | EXCAVATED 2 X 8 CONCRETE SIDEWALK MARKED BY (EARTH TECH) FOUND LEAK ON 3/4 INCH CONTROLLING LINE ON THE SIDE OF CATCH BASIN MAD REPAIRS ON CONTROLLING LINE BACKFILL JOB WITH RIVER SAND + COLDMILL CUSTOMER HAS GOOD WATER PRESSURE NOW
201701474401 | 2017-10-30 | LEAD | 2015 | LAPEYROUSE | S JOHNSON | WILK | ML- METER LEAK MTR#A396646 ACCT.# 116021-488105 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A302721 SN: 0020369, *TAP: SIZE: A LOC: 118 FEET FROM P LINE AT JOHNSON S, *MB: CODE: AF LOC: ON LAPEYROUSE 118.2FT FROM JOHNSON ****/ | 2017-11-09 | EXCAVATED 3 X 3 MUD PLOT MADE REPAIRS ON INLET SERVICE BACKFILL AND CLEANED THE AREA
201701474601 | 2017-10-30 | LEAD | 2538 | CONTI |  | UNKN | CUSTOMER WAITING. CEMENT IN BOX, UNABLE TO SET METER. PLEASE REPAIR AND SET 1" METER. LOC ID 172039 ********J.GILLIAM @ 12:36PM******** CEMENT IN BOX UNABLE TO SET 1" METER /** 1) MN: C016301 SN: 0115017, *TAP: SIZE: C LOC: 293 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: CDKO LOC: ON CONTI 293FT FROM PL N ROCHEBLAVE 9' OUTSIDE PL ****/ | 2017-10-30 | EXCAVATED 3 X 3 SIDEWALK CUT 1 INCH METER BOX COMPLETE AND 1 INCH METER BACKFILL AND CLEANED THE AREA ********SET METER NOT COMING UP SERVICE ORDER FOREMAN FOUND THIS METER THERE************ METER:C036561 FACTORY:16359254 MAKE:HERSEY READ:0
201701474701 | 2017-10-30 | LEAD | 3201 | BIENVILLE | N LOPEZ | WMTLK | WM- LEAK BETWEEN SIDEWALK AND STREET EXAMINE INLET AND OUTLET SERVICE FOR LEAK, METER LOCATED ON N LOPEZ /** 1) MN: A299158 SN: 0050022, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT BIENVILLE, *MB: CODE: BDH LOC: ON N LOPEZ 52FT FROM PL BIENVILLE 1ST METER ****/ | 2017-11-04 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK ALSO RAISED 5/8 INCH METER BOX BOTTOM TO GRADE BACKFILLED+ DRESSED UP AREA
201701474901 | 2017-10-30 | LEAD | 1435-37 | CRETE | LEPAGE | WMTLK | ML- METER LEAKING ACCT.# 160867-490996 MT.# A 396977 EXAMINE INLET AND OUTLET SERVICE FOR LEAK CARS ROLLING OVER METER /** AT 1437: 1) MN: A261108 SN: 0050665, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT CRETE, *MB: CODE: BDHL LOC: ON LEPAGE 73FT FROM PL CRETE 8.5' OUTSIDE PL 2.5' ****/ | 2017-11-07 | EXCAVATED 2 X 3 MUD PLOT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILL AND CLEANED THE AREA
201701475101 | 2017-10-30 | LEAD/PLASTIC | 3018 | HUDSON PL | MACARTHUR BL | WMTLK | ML- METER LEAK ACCT#229408-417307 METER#A431934 EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A326833 SN: 0131390, *TAP: SIZE: B LOC: 255 FEET FROM P LINE AT MAC ARTHUR BLVD, *MB: CODE: ADKO LOC: RES. 254FT FROM PL MAC ARTHUR ****/ | 2017-11-14 | EXAMINED METER BOX OBSERVE LEAK ON INLET REPAIRED LEAK
201701479501 | 2017-10-30 | LEAD | 237 | S OLYMPIA | PALMYRA | WILK | ML-METER LEAK INLET SERVICE LEAK NEAR SIDEWALK FLOODING AREA /** 1) MN: A325009 SN: 0133501, *TAP: SIZE: B LOC: 40 FEET FROM P LINE AT PALMYRA, *MB: CODE: CE LOC: ON S OLYMPIA 39' FROM PL PALMYRA 9' OUTSIDE PL ****/ | 2017-11-01 | DUG IN MUDPLOT TO CHANGE INLET CURB COCK ONCE WE CHANGED FITTINGS THERE WERE NO OTHER LEAKS. ALSO THERE WAS LEAD ON INLET REFER TO FIRST AM TO REMOVE LEAD LJF
201701479503 | 2017-11-12 | LEAD | 237 | S OLYMPIA | PALMYRA | WSNR | THERES A PARKED VEHICLE WHERE THE JOB IS LOCATED AND IT COULDNT BE MOVED. *******************REMOVED ALL LEAD TUBING************************* /** 1) MN: A325009 SN: 0133501, *TAP: SIZE: B LOC: 40 FEET FROM P LINE AT PALMYRA, *MB: CODE: CE LOC: ON S OLYMPIA 39' FROM PL PALMYRA 9' OUTSIDE PL ****/ | 2018-11-05 | JOB WILL BE RE-SCHEDULE AT A LATER DATE DO TO PAVEMENT BACK LOG JOB CONTINUED
201701479901 | 2017-10-30 | LEAD | 2883 | ANNETTE | INDUSTRY | WMTBG | MI - METER BOX BELOW GRADE ACCT#160733-453331 METER#A301745 ADJUST METER BOX TO PROPER GRADE /** 1) MN: A301745 SN: 0099134, *TAP: SIZE: A LOC: 171 FEET FROM P LINE AT INDUSTRY, *MB: CODE: CDL LOC: ON ANNETTE 171' FROM PL INDUSTRY 8' OUTSIDE PL ****/ | 2017-11-12 | EXCAVATED IN GUTTER BOT5TOM + REPLACED BROKEN 5/8 INCH METER BOX CASING BACKFILL + DRESSED UP AREA
201701482401 | 2017-10-31 | LEAD | 2539 | ST ANN |  | WILK | ***************PICKUP************ INLET SERVICE LEAK ACC#119411-523297 MN#A424110 11/03/17 LEAK HAS GOTTEN WORSE PER SERVICE REQUEST #12819924 (FCP) /** 1) MN: A274430 SN: 0031862, *TAP: SIZE: A LOC: 124 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CFLM LOC: ON ST ANN ST 124' FROM LRPL N. DORGENOIS ST ****/ | 2017-11-14 | REPLACED 5/8 WASHERS TO STOP LEAK
201701482901 | 2017-10-31 | LEAD/PLASTIC | 1101 | SHIRLEY DR |  | WOLK | MI- CHANGE LEAD WHIP MTR# A220789 ACCT.# 225995-405198 RENEW OUTLET SERVICE /** 1) MN: A220789 SN: 0095674, *TAP: SIZE: B LOC: 44 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: ADL4 LOC: ON SHIRLEY DR., 34.5' FROM P.L. GEN. MEYER AVE., ****/ | 2017-11-13 | EXCAVATED TO PROPERTY REPLACE PLASTIC TO PROPERTY REMOVED LEAD LINE
201701485901 | 2017-10-31 | LEAD | 1414 | N CLAIBORNE AV | ESPLANADE AV | WILK | ML- METER LEAK METER# A426761 ACCT# 117751-486331 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A273086 SN: 0026252, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: BEM2 LOC: ON CLAIBORNE 82FT FORM ESPLANADE ****/ | 2017-11-13 | EXCAVATED 3 X 3 SIDEWALK REPLACED 5/8 INCH METER BOX COCK ALSO METER WAS REPLACED BACKFILLED AND CLEANED THE AREA ************OLD METER INFO ************* METER:A426761 16311773 MAKE:HERSEY READ:76
201701487201 | 2017-11-01 | LEAD/PLASTIC | 2821 | GEN COLLINS AV |  | WMRE | LOCATION: 230632 METER BOX BURIED / LOCATE AND CHANGE METER# A 413352 HOME UNDER CONSTRUCTION LOCATE, MARK AND CHANGE METER /** 1) MN: A258107 SN: 0138124, *TAP: SIZE: B LOC: 188 FEET FROM P LINE AT HERSCHEL, *MB: CODE: CDM3 LOC: ON GEN COLLINS AVE 188FT FROM P.L. HERSCHEL 7FT ****/ | 2017-11-07 | EXCAVATED TO LOCATE METER FOUND METER AND RASIE TO GRADE THERE IS COOPER ON OUTLET AND INLET BACKFILLED AND CLEANED JOB SITE ALSO HAD TO BREAK SIDEWALK TO FIND METER BOX
201701488201 | 2017-11-01 | LEAD | 3308 | BURGUNDY |  | WMEX | LOCATIONID#301047-705542 METER#C034597 METER FILLED WITH CEMENT /** 1) MN: A302041 SN: 0032458, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT PIETY, *MB: CODE: AEHM LOC: ON BURGUNDY ST 63' P.L. PIETY ST ****/ | 2017-11-09 | REMOVED CONCRETE + DEBRIS FROM METER BOX AT ABOVE LOCATION
201701488301 | 2017-11-01 | LEAD | 3500 | ST CLAUDE AV | GALLIER | WMEX | LOCATIONID#182760-601057 METER#C008570 METER FILLED WITH CEMENT /** 1) MN: C008570 SN: 0173079, *TAP: SIZE: C LOC: 45 FEET FROM P LINE AT GALLIER, *MB: CODE: AEIM LOC: ON N RAMPART 45FT PL GALLIER 6' OUTSIDE 2' IN- ** 2) MN: D006959 SN: 0000000, *TAP: SIZE: D LOC: 55 FEET FROM P LINE AT GALLIER, *MB: CODE: BDLP LOC: IN MH 55FT FROM PL GALLIER ON ST CLAUDE ****/ | 2017-11-14 | REMOVED CONCRETE + DEBRIS FROM MANHOLE AT ABOVE LOCATION
201701489001 | 2017-11-01 | LEAD | 2344 | MAZANT | N ROCHEBLAVE | WMLK | WM LEAK BETWEEN THE SIDEWALK AND THE STREET EXAMINE WATER MAIN FOR LEAK NEAR CURB /** 1) MN: SN: 0099675, *TAP: SIZE: B LOC: 36 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: ADM LOC: ON MAZANT, 30' FROM P.L. NO. ROCHEBLAVE,7.5' OUT- ****/ | 2017-11-12 | EXCAVATED IN MUD PLOT BETWEEN SIDEWALK + STREET + EXAMINED AREA AT ABOVE LOCATION + FOUND NO LEAK
201701490001 | 2017-11-01 | LEAD | 4205 | BURGUNDY | FRANCE | WILK | MI- METER LEAK MTR# A121437 ACCT# 138407-701475 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A121437 SN: 0068972, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT FRANCE, *MB: CODE: BDE LOC: ON BURGUNDY 47FT FROM PL FRANCE ****/ | 2017-11-15 | EXCAVATED 4 X 3 SIDEWALK CUT RENEW OUTLET SERVICE UP TO PROPERTY AND REPLACED 5/8 METER BOX COCK. BACKFILLED AND CLEANED THE AREA.
201701490101 | 2017-11-01 | LEAD | 1221 | FELICIANA | MARAIS | WILK | MI-LEAK IN THE STREET LEAK IN FRONT OF 1221 INLET SERVICE LEAK @ THE MAIN IN STREET /** 1) MN: A128595 SN: 0067782, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT MARAIS, *MB: CODE: CEL1 LOC: ON FLICIANA 150' FROM PL OF MARAIS ****/ | 2017-11-12 | EXCAVATED IN ASPHALT STREET + REPLACED 3/4 INCH BEND ADAPTER ON 6 INCH WATER MAIN COMPACTED BACKFILL + DRESSED UP AREA
201701490301 | 2017-11-01 | LEAD | 2024 | TRICOU | N JOHNSON | WILK | MI METER BOX LEAKING **CONTACT MR BARNES UPON ARRIVAL @ (310)428-3856** INLET @ ABANDON LOT IN BUSHES /** 1) MN: A240880 SN: 0125647, *TAP: SIZE: A LOC: 156 FEET FROM P LINE AT JOHNSON N, *MB: CODE: ADK2 LOC: MTR ON TRICOU 156FT FROM PL JOHNSON 6FT OUTSD PL ****/ | 2017-11-10 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK ON 5/8 INLET ABANDON INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201701491601 | 2017-11-01 | LEAD | 2722 | TOULOUSE | N WHITE | WMTLK | ML - METER LEAK ACCOUNT NUMBER - 193555-709121 METER NUMBER - C032962 EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER FLOODING CURB/STREET /** 1) MN: C021361 SN: 0153299, *TAP: SIZE: C LOC: 253 FEET FROM P LINE AT WHITE N, *MB: CODE: CDL LOC: ON TOULOUSE 253FT FROM WHITE 10FT OUTSIDE ****/ | 2017-11-08 | PUMPED DOWN METER BOX + REPLACED 1 INCH HANDWHEEL + GUTS IN METER BOX
201701492001 | 2017-11-01 | LEAD | 1112 | N ROCHEBLAVE | GOV NICHOLLS | WMTLK | WM LEAK ON THE SIDEWALK EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER FLOODING CURB/STREET /** 1) MN: C024479 SN: 0045013, *TAP: SIZE: C LOC: 95 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: BD LOC: 95FT PL URSULINES 8FT OUTSD PL N ROCHEBLAVE ** 2) MN: SN: 0045013, *TAP: SIZE: A LOC: 96 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: CD LOC: ON ROCHEBLAVE 95.5FT FROM URSULINES ****/ | 2017-11-14 | EXCAVATED 3 X 3 MUD PLOT PUMPED FLOODED AREA DOWN MADE REPAIR ON OUTLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201701492101 | 2017-11-01 | LEAD | 2901 | HAVANA PL | AGRICULTURE | WILK | WM LEAK BETWEEN STREET & SIDEWALK IN GRASSY AREA ON AGRICULTURE STREET SIDE INLET SERVICE LEAK BETWEEN SIDEWALK/STREET FLOODING SIDEWALK/STREET ON AGRICULTURE /** 1) MN: A248311 SN: 0093213, *TAP: SIZE: B LOC: 24 FEET FROM P LINE AT HAVANA, *MB: CODE: CD LOC: ON AGRICULTURE 24FT FROM HAVANA ****/ | 2017-11-08 | EXCAVATED IN MUD PLOT + REPLACED 1 INCH CORPORATION COCK ON 6 INCH WATER MAIN BACKFILL + DRESSED UP AREA
201701492501 | 2017-11-01 | LEAD/PLASTIC | 2353 | ST THOMAS | SORAPARU | WILK | MI- LEAK IN THE STREET , FLOODING THE AREA *************1ST AM************** CHANGED FROM 2354 ST THOMAS INET SERVICE LAK @ SIDEWALK CAUSING POOR PRESSURE, FLOODING AREA GETTING OFF IN DCB, FOUND 1 BARREL ON SITE /** 1) MN: SN: 0045407, *TAP: SIZE: A LOC: 84 FEET FROM P LINE AT SORAPARU, *MB: CODE: BENO LOC: ON ST THOMAS 83.6FT FROM SORAPARU ****/ | 2017-11-02 | BROKE THE DRIVEWAY AND EXCAVATED ON THE INLET AND OUTLET SERVICE AND REPAIR LEAK AND ALSO FOUND A JUMPER IN METERBOX AND I REPORT IT THEN WE BACKFILL AND CLEAN UP JOB SITE AND WE LEFT THE WATER OFF
201701492801 | 2017-11-01 | LEAD/PLASTIC | 1605 | AUDUBON | BIRCH | WILK | ***********PICKUP*********** INLET SERVICE LEAK IN ASPHALT STREET /** 1) MN: B023513 SN: 0065830, *TAP: SIZE: B LOC: 28 FEET FROM P LINE AT BIRCH, *MB: CODE: BDL1 LOC: FRONT BY CATCH BASIN 28' P.L. BIRCH ****/ DOTTIE READY 11-7-17 EXP11-27-17 | 2017-11-09 | ARRIVED ON SITE FOUND LEAK ON LEAD 1 1/2 CONTROLLING LINE IN ASPHALT STREET EXCAVATED IN CUT TO MAKE REPAIR BACKFILLED AND DRESSED 8 X 5 FT STREET CUT.
201701493701 | 2017-11-02 | LEAD | 636 | POLAND AV | CHARTRES | WILK | **************PICKUP*************** INLET SERVICE LEAK ACC#221892-714055 MN#A422791 /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-11-15 | EXCAVATED 3 X 2 GUTTER BOTTOM REPLACED 5/8 METER BOX COCK TO STOP LEAK. BACKFILLED AND CLEANED THE AREA.
201701494201 | 2017-11-02 | LEAD | 1713 | ST CLAUDE AV | ANNETTE | WILK | *****************PICKUP***************** ******DAMAGE CLLAIM******** (J. GILLIAM @ 9:06AM) CUT INLET SERVICE BY HARDROCK CONSTRUCTION, CAUSING POOR PRESSURE /** 1) MN: A338902 SN: 0060235, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT ANNETTE, *MB: CODE: AD6 LOC: ON ST CLAUDE AVE 118' FROM LSPL ANNETTE ****/ | 2017-11-02 | .MADE REPAIRS INLET SERVICE 1 INCH AT 6 INCH WATER MAIN FORCE ACCOUNT HARDROCK CONSTRUCTION COMPANY FOR REPAIRS
201701497201 | 2017-11-02 | LEAD | 2035 | FELICIANA | N GALVEZ | WMTLK | ML METER LEAK METER# A325905 ACCT#161257-433452 EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A232136 SN: 0099760, *TAP: SIZE: C LOC: 82 FEET FROM P LINE AT GALVEZ N, *MB: CODE: CD LOC: ON FELICIANA, 81.5' FROM P.L. NO. GALVEZ, 6' OUT- ****/ | 2017-11-29 | EXCAVATED 3 X 3 GUTTER BOTTOM THROUGH LIMESTONE AND MUD MADE REPAIR ON INLET SERVICE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201701497701 | 2017-11-02 | LEAD | 2908 | BANKS | S DUPRE | WILK | WM LEAK BETWEEN STREET & SIDEWALK INLET SERVICE LEAK IN MUDPLOT FLOODING SIDEWALK AND CURB /** 1) MN: A255137 SN: 0021972, *TAP: SIZE: B LOC: 126 FEET FROM P LINE AT DUPRE S, *MB: CODE: AFL LOC: INSIDE AT 2908 126' P.L. S DUPRE ****/ | 2017-11-14 | EXCAVATED 3 X 3 MUD PLOT RENEWD OUTLET SERVICE TO PROPERTY BACKFILLED AND CLEANED THE AREA
201701498701 | 2017-11-02 | LEAD/PLASTIC | 1529 | MITHRA | PARIS AV | WILK | ML - METER LEAK MTR # A413031 ACCT # 167529-505995 INLET SERVICE LEAK IN MUDPLOT FLOODING SIDEWALK /** 1) MN: A320859 SN: 0114314, *TAP: SIZE: A LOC: 415 FEET FROM P LINE AT PERLITA, *MB: CODE: BD LOC: ON MITHRA, 415' FROM P.L. PERLITA, 7' OUTSIDE P.L. ****/ | 2017-11-30 | EXAMINED AND FOUND LEAK ON INLET SERVICE. USED MAUL TO BREAK UP CONCRETE IN DRIVEWAY. EXCAVATED MUDPLOT BY HAND , MADE ALL REPAIRS AND BACKFILLED WITH RIVER SAND AND COLD MILL (JOB IN TREET ROOTS) CREW FOUND METER A413031 AT ABOVE LOCATION LJF
201701502001 | 2017-11-03 | LEAD | 8219 | PANOLA |  | WOLK | MI- LEAK BETWEEN S/WALK & CURB OUTLET SERVICE LEAKING BEHIND HANDWHEEL 11/15/17 LEAK GETTING WORSE (KSW) 02/20/18 CUST STATES RAW SEWERAGE COMING THRU METER BOX (NLD) /** 1) MN: A258704 SN: 0069068, *TAP: SIZE: A LOC: 148 FEET FROM P LINE AT DUBLIN, *MB: CODE: ADM LOC: ON PANOLA 149' FROM PL OF DUBLIN ****/ | 2018-03-11 | EXCAVATED IN MUDPLOT REPAIR 5/8 STOP AND WASTE 5/8 HANDWHEEL. DRESS UP WITH RIVERSAND. JOBREFERRED TO ZONE 1 TOTAKE LEAD LINE FROM WATER MAIN TO METER BOX
201701503801 | 2017-11-03 | LEAD/PLASTIC | 912 | 4TH | CONSTANCE | WILK | MI- LEAK IN THE STREET INLET SERVICE LEAK BEHIND CURB COCK ON BOTH METERS /** 1) MN: SN: 0004584, *TAP: SIZE: D LOC: 122 FEET FROM P LINE AT LAUREL, *MB: CODE: BEKP LOC: 122FT FROM PL LAUREL ** 2) MN: A247725 SN: 0004584, *TAP: SIZE: B LOC: 112 FEET FROM P LINE AT LAUREL, *MB: CODE: OOO LOC: ON FOURTH, 118' FROM C.P.L. LAUREL, 15' OUTSIDE, THERE ARE 7 MORE NOT LISTED. ****/ | 2017-11-30 | BROKE CONCRETE WITH MAUL EXAMINED METER FOR LEAK LEAK OBSERVED ON INLET SERVICE COCK REPAIRED LEAK BACKFILLED WITH SAND AND COLD MILL CLEANED AREA
201701504301 | 2017-11-03 | LEAD/PLASTIC | 2415 | MEXICO |  | WILK | ML METER LEAK ACCOUNT #176402473140 METER #B024721 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: B024721 SN: 0120268, *TAP: SIZE: B LOC: 164 FEET FROM P LINE AT MUSIC, *MB: CODE: ADKO LOC: MTR ON MEXICO 164FT FRM PL MUSIC 8FT OUTSD PL 2FT ****/ | 2017-11-22 | EXCAVATED IN MUDPLOT/ GRAVEL OVER 3/4 INLET SERVICE LEAK LEAD ON BOTH CHANGED THE COCK RAISED METERBOX UP TO GRADE AND REPLACED 8 FT OF LEAD WITH 3/4 PVC PIPE FROM METERBOX TO PROPERTY BACKFILLED AND DRESS UP. JEG
201701504302 | 2017-11-27 | LEAD | 2415 | MEXICO |  | WSNR | REPLACE ALL LEAD ON INLET SERVICE /** 1) MN: B024721 SN: 0120268, *TAP: SIZE: B LOC: 164 FEET FROM P LINE AT MUSIC, *MB: CODE: ADKO LOC: MTR ON MEXICO 164FT FRM PL MUSIC 8FT OUTSD PL 2FT ****/ | 2018-11-05 | JOB WILL BE RE-SCHEDULE AT A LATER DATE DO TO PAVEMENT BACK LOG. JOB CONTINUED
201701504401 | 2017-11-03 | LEAD | 226 | S GAYOSO | PALMYRA | WILK | ML-METER LEAK ACCT#117140-531340 METER#A398395 INLET SERVICE LEAK /** 1) MN: A309988 SN: 0024132, *TAP: SIZE: B LOC: 112 FEET FROM P LINE AT PALMYRA, *MB: CODE: CFL LOC: IN GARDEN 113' P.L. PALMYRA ****/ | 2017-11-11 | EXCAVATED 4 X 4 MUD PLOT IN GARDEN FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND
201701504701 | 2017-11-03 | LEAD | 2900 | GRAND RTE ST JOHN | N WHITE | WILK | MI- LEAK IN THE SIDEWALK INLET SERVICE LEAK INSDE TREEROOT FLOODING CURB/STREET /** 1) MN: A294939 SN: 0050548, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT WHITE N, *MB: CODE: BD5 LOC: 2ND METER,ON GRAND RTE ST JOHN 45 FT FROM N WHITE ****/ | 2017-11-11 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAKON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET REPLACED 5/8 INCH HANDWHEEL BACKFILL JOB WITH RIVERSAND JOB IS COMPLETE
201701505101 | 2017-11-03 | LEAD/PLASTIC | 1019 | OPELOUSAS AV | ATLANTIC AV | WILK | WM- LEAK IN THE STREET *******B LEAVE IN SYSTEM******* LEAK ON WATER MAIN IN NEUTRAL GROUND FLOWING INTO STREET CAUSING A DANGEROUS SITUATION **B** 11/20/17 CUST STATES LEAST HAS GOTTEN WORST (KSW) /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-12-11 | BROKE THE STREET AND EXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOB SITE INLET SERVICE NEED TO BE REROUTE AND RENEW FROM THE WATER MAIN BECAUSE ITS A LEAD LINE GOING INTO A TREE
201701505401 | 2017-11-03 | LEAD/PLASTIC | 2350 | CAMP | 1ST | WILK | ML-METER LEAK ****WATER SHOOTING UP INSIDE BOX**** BAD BLEEDER VALVE INSIDE METER BOX 01/10/18 PER S/R 12826805 METER LEAK FLOODING SIDEWALK (KSW) /** 1) MN: A214745 SN: 0046614, *TAP: SIZE: B LOC: 95 FEET FROM P LINE AT FIRST, *MB: CODE: CEL LOC: ON CAMP,95.7' FROM L.P.L. FIRST ****/ DOTTIE READY 4-17-18 EXP 5-7-18 | 2018-04-26 | ARRIVED AT THE ABOVE LOCATION CHANGED METER WASHER AND MADE REPAIRS ON THE INLET IN A 3 X 3 SIDEWALK CUT .THEN BACKFILLED AND DRESSED UP THE JOB .THE INLET IS LEAD LINE REFER TO CREW TO RENEW FROM THE METER BOX TO THE MAIN.
201701506301 | 2017-11-04 | LEAD | 3917 | ODIN | PROVIDENCE PL | WILK | MI- LEAK IN THE STREET INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: B029688 SN: 0128710, *TAP: SIZE: B LOC: 135 FEET FROM P LINE AT PROVIDENCE PL, *MB: CODE: CDLM LOC: ON ODIN, 135' FROM P.L. PROVIDENCE PL., 8' OUTSIDE ****/ | 2017-12-06 | EXAMINED LOCATION FOUND METER BOX COCK LEAKING. EXCAVATED DOWN ON INLET SERVICE FROM METER TO CURB. FOUND LEAD SERVICE. MADE REPAIRS BY REPLACING WASHERS & COCK. BACKFILLED DRESSED UP.
201701510001 | 2017-11-06 | LEAD | 3201 | BIENVILLE | N LOPEZ | WILK | WM- LEAK BETWEEN SIDEWALK AND STREET EXAMINE INLET SERVICE FOR A LEAK , LEAKING AGAIN ON A PREVIOUS CUT /** 1) MN: A299158 SN: 0050022, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT BIENVILLE, *MB: CODE: BDH LOC: ON N LOPEZ 52FT FROM PL BIENVILLE 1ST METER ****/ | 2017-11-16 | EXCAVATED 4 X 3 SIDEWALK CUT MOVED METER BOX FROM GUTTER TO SIDEWALK BACKFILLED AND CLEANED THE AREA
201701511501 | 2017-11-06 | LEAD | 921 | ST PETER |  | WILK | LOCATION: 107056 MTR# A 113349 UNABLE TO EXAMINE METER, BAD BLEEDER VALVE LEAK PLEASE MAKE REPAIRS BAD BLEEDR VALVE PASSING IN ON POSITION /** 1) MN: A256312 SN: 0008647, *TAP: SIZE: B LOC: 144 FEET FROM P LINE AT DAUPHINE, *MB: CODE: CEM1 LOC: ON ST PETER 143.6 FT FROM PL DAUPHINE ****/ | 2017-11-30 | REPLACE INLET/OUTLET WASHERS AT ABOVE LOCATION ALSO REMOVE CEMENT FROM INSIDE OF BOX
201701511801 | 2017-11-06 | LEAD/PLASTIC | 3465 | WALL BL |  | WMRE | ML METER# A428812 ACCT# 235999-407297 LOCATE, RAISE & MAKE REPAIRS ON METER UNDER WATER. ***SIGNS OF VEHICLES ROOLING OVER METER /** 1) MN: A198264 SN: 0165926, *TAP: SIZE: A LOC: 12 FEET FROM P LINE AT CYPRESS ACRES DR, *MB: CODE: OOOO LOC: ON WALL 25FT FROM PL CYPRESS ACRES 9FT OUTSD PL ****/ | 2017-12-01 | EXCAVATED METER EXAMINED INLET AND OUTLET SERVICE FOR LEAK OBSERVED LEAK ON WASHER ON INLET SERVICE SIDE REPAIRED LEAK BACKFILLED AND DRESSED UP THE JOB
201701512701 | 2017-11-06 | LEAD | 1855 | ROSIERE | SERANTINE | WILK | ML- METER LEAK METER# A428409 ACCT# 154151-482493 INLET SERVICE LEAK NEAR METER BOX, CARS ROLLING OVER METER BOX /** 1) MN: A285366 SN: 0090255, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT CASTIGLIONE, *MB: CODE: CD LOC: ON ROSIERE,132' FROM P.L. CASTIGLIONE,8.5' OUTSIDE ****/ | 2017-11-22 | EXCAVATED IN MUD PLOT + CONCRETE SIDEWALK + RELOCATED 5/8 INLET METER BOX COMPLETE FROM MUD PLOT TO SIDEWALK BACKFILLED + DRESSED UP AREA
201701515101 | 2017-11-06 | LEAD | 7708 | MAPLE | ADAMS | WLPR | PP- POOR PRESSURE ACCT# 111059-584292 METER#A414749 EXAMINE INLET SERVICE FOR POOR PRESSURE /** 1) MN: A315328 SN: 0012819, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT ADAMS, *MB: CODE: ADK7 LOC: ON MAPLE 64.5 FT FROM ADAMS ****/ | 2017-11-08 | MADE A 2 X 2 BRICK CUT EXCAVATED AND MADE REPAIRS ON A 3/4 INLET SERVICE LEAK, LEAD LINE HAVE TO COME BACK AND TAKE THE LEAD OUT FROM THE PROPERTY TO THE WATER MAIN THE AREA IS REAL TIGHT AND BUSY AREA. CUSTOMER HAS GOOD PRESSURE JOB CONTINUED JEG
201701518201 | 2017-11-07 | LEAD | 819 | UPPERLINE |  | WILK | MI LEAK ON THE SIDEWALK BAD BLEEDER VALVE /** 1) MN: A287552 SN: 0042078, *TAP: SIZE: A LOC: 121 FEET FROM P LINE AT CONSTANCE, *MB: CODE: BFO2 LOC: ON UPPERLINE 121FT FROM SPL CONSTANCE ****/ DOTTIE READY 4-16-18 EXP 5-6-18 | 2018-04-19 | ARRIVED ON JOB SITE FOR INLET SERVICE LEAK EXCAVATED ON SIDEWALK MADE A 4 X4 CUT ON SIDEWALK AND MADE REPAIRS TO BAD METER COCK REPLACE WITH NEW METER COCK ,BACKFILLED AND DRESSED CUT UP,ALSO LEAD NEED TO BE REMOVED FROM WATER MAIN SOC 4 FT X 4 FT S/W.
201701519801 | 2017-11-07 | LEAD | 331 | DECATUR | CONTI | WILK | ML- METER LEAK MTR# D 005841 ACCT# 183214-527102 INLET SERVICE LEAK ON ABANDON SERVICE *****NO METER***** /** 1) MN: D005841 SN: 0027988, *TAP: SIZE: D LOC: 240 FEET FROM P LINE AT BIENVILLE, *MB: CODE: AEMD LOC: IN MH 240' PL BIENVILLE 6' OUTSIDE 2' INSIDE CURB ** 2) MN: SN: 0027988, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT CONTI, *MB: CODE: __ LOC: 82' P.L. CONTI THERE IS 1 MORE NOT LISTED. ****/ | 2017-11-17 | EXCAVATED 3 X 2 SIDEWALK CUT MADE REPAIR ON ABANDON INLET SERVICE LINE BACK
201701519901 | 2017-11-07 | LEAD | 919 | ROYAL | DUMAINE | WILK | ML METER LEAK METER # A398290 ACCOUNT # 106058-527880 EXAMINE INLET SERVICE NEAR CURB /** 1) MN: A215972 SN: 0028771, *TAP: SIZE: B LOC: 144 FEET FROM P LINE AT DUMAINE, *MB: CODE: AFL6 LOC: 4 APTS ON ROYAL 143 FT FROM PL DUMAINE ** 2) MN: A348141 SN: 0000000, *TAP: SIZE: G LOC: 190 FEET FROM P LINE AT PHILIP, *MB: CODE: CD LOC: ON ROYAL 190FT FROM ST PHILIP (INSIDE PROPERTY) 10 THERE IS 1 MORE NOT LISTED. ****/ | 2017-12-08 | EXCAVATED 4 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK AND MADE REPAIR ON 1 1/2 INCH OUTLET SERVICE LINE TO STOP LEAK BACKFILL AND CLEANED THE AREA LEAK IN THE STREET REFER BACK TO ZONE 4 *ROCKWELL FACTORY 50064959 TAG D7137 READING 16293000*
201701521501 | 2017-11-07 | LEAD | 2417 | ALMONASTER AV | N DORGENOIS | WILK | WM LEAK ON THE SIDEWALK EXAMINE INLET SERVICE FOR A LEAK SOMEONE PARKING ON SERVICE /** 1) MN: A287463 SN: 0087551, *TAP: SIZE: C LOC: 202 FEET FROM P LINE AT N. ROCHEBLAVE, *MB: CODE: OOO LOC: ON ALMONASTER 202' FORM PL N ROCHEBLAVE 9' OUTSIDE ** 2) MN: SN: 0087551, *TAP: SIZE: B LOC: 200 FEET FROM P LINE AT N ROCHEBLAVE, *MB: CODE: OOO LOC: ON ALMONASTER AVE 201' FROM PL N ROCHEBLAVE 9' OUT ****/ | 2017-11-22 | EXCAVATED 4 X 2 SIDEWALK CUT RELOCATED METER BOX FROM GUTTER TO SIDEWALK BACKFILLED AND CLEANED THE AREA
201701522101 | 2017-11-07 | LEAD | 1023 | N DORGENOIS |  | WILK | MI METER BOX LEAK EXAMINE INLET SERVICE FOR A LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-11-20 | EXCAVATED 2 X 2 MU DPLOT REPLACED 5/8 HANDWHEEL TO STOP LEAK BACKFILLED NA DCLEANED THE AREA
201701533001 | 2017-11-08 | LEAD | 2541 | CLEVELAND AV | S ROCHEBLAVE | WILK | MI- LEAK AT THE SIDEWALK CHANGED FROM 2500BLK CLEVELAND AV INLET SERVICE LEAK ON ABANDON SERVICE IN FRONT PARKING LOT. NO ADDRESS/NO METER IN BOX /** 1) MN: SN: 0005360, *TAP: SIZE: B LOC: 31 FEET FROM P LINE AT DORGENOIS S LRPL, *MB: CODE: AEL LOC: 30.5' FROM LRPL DORGENOIS ****/ | 2017-11-22 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 1 INCH ABANDON INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201701533101 | 2017-11-08 | LEAD | 1129 | ELYSIAN FIELDS AV | ST CLAUDE AV | WILK | **********PICK UP********** INLET SERVICE LEAK ON ABANDON SERVICE INTERFERING WITH CONTRACTORS WORK /** 1) MN: A316160 SN: 0017969, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT ELYSIAN FIELDS AVE, *MB: CODE: AFHM LOC: ON MARAIS 64FT FORM ELYS FIELDS ****/ | 2017-11-11 | FOUND INLET LINE EXPOSED MADE REPAIRS TO STOP LEAK
201701535801 | 2017-11-08 | LEAD | 241 | AUDUBON |  | WMBK | LOCATIONID#136138-585541 METER#A275976 TREE ROOTS INSIDE METERBOX TREEROOTS IMPACTING METER BOX RE-ROUTE METER BOX /** 1) MN: A275976 SN: 0066746, *TAP: SIZE: A LOC: 101 FEET FROM P LINE AT MEADOWBANK DR, *MB: CODE: AD LOC: ON AUDUBON 102FT FROM PL OF MEADOWBANK DR 2FT FROM ****/ DOTTIE READY 1-2-18 EXP 1-22-18 | 2018-01-18 | ARRIVED AT ABOVE LOCATION REMOVED ROOTS AND MUD OUT OF METER BOX METER IS NOW OPERATE AND READABLE
201701536001 | 2017-11-08 | LEAD | 2001 | FRENCHMEN | N JOHNSON | WILK | ML--METER LEAK ACCT# 131121-495050 METER# A237644 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A237644 SN: 0061519, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT FRENCHMEN, *MB: CODE: __ LOC: ON N JOHNSON ST 43' FROM LPL FRENCHMEN ****/ | 2017-11-22 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INLET CURB COCK BACKFILLED + DRESSED UP AREA
201701537201 | 2017-11-08 | LEAD | 3310 | LAWRENCE RD | HORACE | WILK | ***********PICKUP********** INLET SERVICE LEAK IN ASPHALT STREET /** 1) MN: A123246 SN: 0148675, *TAP: SIZE: B LOC: 89 FEET FROM P LINE AT HORACE, *MB: CODE: CDL2 LOC: ON LAWRENCE 89FT FROM P.L. HORACE 7FT OUTSDE PL ****/ | 2018-03-03 | EXCAVTED IN STREET AT SITE OF LEAK OBSERVED LEAK ON INLET LINE AT MAIN REPAIRED LEAK BACKFILLED WITH SAND + COLDMILL CLEAN METER BOX REPLACED WASHER
201701538601 | 2017-11-09 | LEAD | 2816 | REPUBLIC | INDUSTRY | WILK | ML- METER LEAK AT METER # A 409498 ACCT# 222464-492712 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A130874 SN: 0065124, *TAP: SIZE: A LOC: 141 FEET FROM P LINE AT INDUSTRY, *MB: CODE: DL LOC: ON REPUBLIC ST 141' FROM USPL INDUSTRY ****/ | 2017-12-08 | EXCAVATED IN GUTTER BOTTOM + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201701541401 | 2017-11-09 | LEAD | 1715 | FELICIANA |  | WMTLK | BAD BLEEDER VALVE LEAK. METER A430920 NEEDS TO BE REPAIRED ASAP. CUSTOMER IS WITHOUT WATER. LOC ID 146509 EXAMINE INLET & OUTLET SERVICE FOR A LEAK BAD BLEEDER VALVE, METER UNDER WATER ON VACANT LOT, CURB COCK OFF /** 1) MN: 000000 SN: 0084909, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BDL LOC: 112FT FROM DERBIGNY METER ON FELICIANA ****/ | 2017-12-06 | EXCAVATED IN MUD PLOT + MADE REPAIR BY REPLACING 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201701542501 | 2017-11-09 | LEAD/PLASTIC | 8222 | COHN | DANTE | WILK | ML METER LEAK ACCT# 114787-589887 METER# A249112 INLET SERVICE LAEK IN GRASS INFRONT METER FLOODING AREA GETTING OFF IN DCB 10/27/17 S/R 12822230 METER LEAK /** 1) MN: A249112 SN: 0017767, *TAP: SIZE: A LOC: 164 FEET FROM P LINE AT DUBLIN, *MB: CODE: CDN1 LOC: ON COHN 164.5FT FROM PL OF DUBLIN ****/ | 2018-02-20 | EXCAVATED AND MADE REAPIRS ON A 5/8' INLET LEAK PLASTIC ON THE OUTLET JOB COMPLETE
201701542502 | 2018-02-21 | LEAD | 8222 | COHN | DANTE | WSNR | REPLACE SERVICE LEAD SERVICE FROM MAIN TO METER BOX /** 1) MN: A249112 SN: 0017767, *TAP: SIZE: A LOC: 164 FEET FROM P LINE AT DUBLIN, *MB: CODE: CDN1 LOC: ON COHN 164.5FT FROM PL OF DUBLIN ****/ | 2018-11-05 | JOB WILL BE RE-SCHEDULE AT A LATER DATE DO TO PAVEMENT BACK LOG
201701542901 | 2017-11-09 | LEAD/PLASTIC | 200 | 12TH |  | WMRE | SERVICE BURIED, UNABLE TO SET METER. PLEASE LOCATE AND SET 3/4" METER. LOC ID 302573 LOCATE, RAISE TO GRADE, MARK & SET 3/4 METER /** 1) MN: B014610 SN: 0127701, *TAP: SIZE: B LOC: 302 FEET FROM P LINE AT FLEUR DE LIS DR., *MB: CODE: CFN LOC: ON 12TH, 302' FROM P.L. FLEUR DE LIS DR., 7' OUT- ****/ | 2017-12-02 | EXCAVATED LOCATED AND RAISED A 3/4 METER TO GRADE ALSO RENEWED THE OUTLET AND SET A 3/4 METER. LEAD ON THE INLET. PLASTIC ON THE OUTLET. JOB COMPLETE JEG
201701543701 | 2017-11-09 | LEAD | 1450 | MOSS | ESPLANADE AV | WILK | ML- METER LEAK ACCT#103233-521914 METER#A428771 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A226007 SN: 0024453, *TAP: SIZE: B LOC: 579 FEET FROM P LINE AT ESPLANADE AVE LRPL, *MB: CODE: BFK2 LOC: 578.8' FROM URPL ESPLANADE ****/ | 2017-11-27 | EXCAVATED IN BED OF LIMESTONES + REPLACED 5/8 INCH CURB COCK BACKFILL + DRESSED UP AREA
201701543801 | 2017-11-09 | LEAD | 1600BLK | TUPELO | N CLAIBORNE AV | WMTLK | WM LEAK BETWEEN STREET AND CURB EXAMINE INLET/OUTLET SERVICE FOR A LEAK, AREA FLOODED /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-12-05 | EXCAVATED 4 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH ABANDON INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201701544601 | 2017-11-09 | LEAD | 1820 | GOV NICHOLLS | N DERBIGNY | WILK | ML- METER LEAK METER#A217182 ACCT#167339-525405 INLET SERCIVE LEAK IN SIDEWALK /** 1) MN: A217182 SN: 0108257, *TAP: SIZE: A LOC: 154 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BDNO LOC: 154FT FROM PL N DERBIGNY ON GOV NICHOLLS 9.5FT OUT ****/ | 2017-11-27 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201701545801 | 2017-11-10 | LEAD | 3138 | ST ANN | N RENDON | WMLK | WATER LEAK -MAIN. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A315450 SN: 0079694, *TAP: SIZE: B LOC: 68 FEET FROM P LINE AT ST ANN, *MB: CODE: BDOK LOC: SIDE ST OP XXX ON FENS CRB END OF HSE ****/ | 2017-11-20 | EXCAVATED IN ASPHALT STREET + STOPPED LEK ON 1 INCH CORPORATION COCK COMPACTED BACKFILL + DRESSED UP AREA
201701547301 | 2017-11-10 | LEAD/PLASTIC | 734 | JACKSON AV | ANNUNCIATION | WILK | ML METER LEAK METER# A302767 ACCT# 118575-541931 CHANGED FROM 736 JACKSON AV CURB COCK PASSING IN OFF POSITION NO METER IN BOX /** 1) MN: A123232 SN: 0031117, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT ANNUNCIATION, *MB: CODE: CFLM LOC: 48FT FROM PL ANNUNCIATION ON JACKSON ****/ | 2017-11-28 | EXAMINED LEAK IN METER BOX AND FOUND THAT THE COCK WAS BAD BROKE CONCRETE BY EXCAVATED LEAK ON INLET SIDE REPLACED BOX COCK WITH ANTHER NEED TO RETURN WITH MACHINE TO EREMOVE LEAD
201701547501 | 2017-11-10 | LEAD | 3530 | TOULOUSE |  | WMLK | MI- LEAK IN THE STREET CHANGED FROM 3534 TOULOUSE LEAK ON THE WATER MAIN IN RURAL AREA NEXT TO ABOVE ADDRESS IN GRASSY AREA 10/13/17 LEAK GETTING WORS PER SR#12820859 (AJR) /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-12-18 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 2 INCH CONTROLLING LINE BACKFILLED + DRESSEDUP AREA
201701548801 | 2017-11-10 | LEAD/PLASTIC | 1339 | RIVIERA AV |  | WILK | METER LEAK/METER BOX OVER FLOWING INLET SERVICE LEAK IN MUDPLOT 2/7/18 METER BOX OVERFLOWING PER S/R # 12831221 (PET). /** 1) MN: C018654 SN: 0115611, *TAP: SIZE: C LOC: 150 FEET FROM P LINE AT CARTIER AVE, *MB: CODE: CDL LOC: 150' P/L CARTIER 8' OUTSIDE 5' INSIDE CURB ****/ | 2018-03-06 | EXCAVATED A N 8 X 13 MUDPLOT CUT IN TREE ROOTS TO MAKE REPAIR ON A 6' WATER MAIN WITH A 6 " FCC REPAIRED INLET SERVICE RAISED 1" MEETR BOX TO GRADE , AND RENEWED OUTLET SERVICE FROM METER TO P.L ALSO REMOVED / REPLACED DAMAGED WATER METER FOUIND LEAD ON INLET SERVICE *********OLD METER INFO*************** METER:C028685 FAC:62101264 MAKE:SENSUS READ:6086
201701549001 | 2017-11-10 | LEAD | 3337-39 | ST ANN | HAGAN AV | WILK | ML- METER LEAK METER# A 425923 ACCT#149346-520484 INLET SERVICE LEAK IN THE MUD PLOT /** AT 3337: 1) MN: A268798 SN: 0026730, *TAP: SIZE: B LOC: 284 FEET FROM P LINE AT HAGAN AVE, *MB: CODE: CDLM LOC: HAGAN/MOSS METER ON ST ANN 284 FT FROM PL N HAGAN ****/ | 2017-11-20 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201701549401 | 2017-11-10 | LEAD | 1330 | POLAND AV | VILLERE | WMTLK | MI-LEAK AT THE SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-11-21 | EXCAVATED 3 X 2 MUD PLOT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILL AND CLEANED THE AREA
201701550401 | 2017-11-10 | LEAD | 528 | GOV NICHOLLS | CHARTRES | WILK | ML - METER LEAK ACCOUNT NUMBER - 104927-528700 METER NUMBER - A256380 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A256380 SN: 0040942, *TAP: SIZE: A LOC: 123 FEET FROM P LINE AT CHARTRES, *MB: CODE: CEN1 LOC: 128 FT FROM URPL CHARTRES ****/ | 2017-11-30 | REPLACED INLET AND OUTLET WASHERS AT ABOVE LOCATION
201701550501 | 2017-11-10 | LEAD | 1467 | MOSS |  | WMRE | SERVICE BURIED. PLEASE LOCATE AND CHANGE METER C028636. LOC ID 148783 LOCATE WATER METER AND MARK /** 1) MN: E006245 SN: 0069690, *TAP: SIZE: G LOC: 166 FEET FROM P LINE AT CANAL, *MB: CODE: AE LOC: ON MOSS ST 169.6' FROM URPL CARROLLTON AVE ****/ | 2017-11-27 | REMOVED SAND OUT OF MANHOLE + REPLACED METER....OLD METER C028636 FACT:62101215 MAKE:SENSUS READ:10895
201701551001 | 2017-11-10 | LEAD/PLASTIC | 711 | BEHRMAN AV | OPELOUSAS AV | WILK | ML- METER LEAK METER# A431903 ACCT# 225576-403788 INLET SERVICE LEAK /** 1) MN: A310870 SN: 0098604, *TAP: SIZE: A LOC: 71 FEET FROM P LINE AT OPELOUSAS AVE, *MB: CODE: BD LOC: RES ON BEHRMAN AVE 71' FROM PL OPELOUSAS 6' OUTSID ****/ | 2017-11-29 | EXAMINED METER CLEANED METER BOX OUT REPLACED WASHERS ON METER TESTED METER METER WORKING IN ORDER
201701551501 | 2017-11-11 | LEAD | 220 | S GAYOSO | PALMYRA | WMTLK | ML METER LEAK ACCT# 113528-531264 METER# A133672 METER BOX "OVER FLOODING" INSIDE YARD (C) /** 1) MN: A133672 SN: 0048838, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT CLEVELAND AVE, *MB: CODE: AFL7 LOC: IN GARDEN AT PLON S GAYOSO 149.6' FROM URPL CLEVEL ****/ | 2017-11-22 | R5EPLACE INLET /OUTLET WASHERS AT ABOVE LOCATION
201701551701 | 2017-11-11 | LEAD/PLASTIC | 148 | W BROOKS | PONTCHARTRAIN BL | WOLK | CHANGE LEAD WHIP HOLE EXPOSED ACCT # 303307-714144 METER # B-41130 CHANGE LEAD WHIP, THE HOLE IS EXPOSED (C) /** 1) MN: B013827 SN: 0128508, *TAP: SIZE: B LOC: 341 FEET FROM P LINE AT PONTCHARTRAIN BLVD, *MB: CODE: CDN1 LOC: ON BROOKS 341FT FROM PL PONTCHARTRAIN ****/ | 2017-11-21 | EXCAVATED A 4 X 8 TRENCH IN MUDPLOT OVER 3/4' SERVICE LEAD ON BOTH REPLACED LEAD ON OUTLET WITH 8 FT OF PVC PIPE BACKFILLED AND DRESS UP JOB CONT-- TO REPLACE LEAD SERVICE FROM MAIN TO METER BOX
201701551702 | 2017-11-27 | LEAD | 148 | W BROOKS | PONTCHARTRAIN BL | WSNR | EXCAVATED A 4 X 8 TRENCH IN MUDPLOT OVER 3/4' SERVICE LEAD ON BOTH REPLACED LEAD ON OUTLET WITH 8 FT OF PVC PIPE BACKFILLED AND DRESS UP JOB CONT-- TO REPLACE LEAD SERVICE FROM MAIN TO METER BOX /** 1) MN: B013827 SN: 0128508, *TAP: SIZE: B LOC: 341 FEET FROM P LINE AT PONTCHARTRAIN BLVD, *MB: CODE: CDN1 LOC: ON BROOKS 341FT FROM PL PONTCHARTRAIN ****/ | 2018-11-05 | JOB WILL BE RE-SCHEDULE AT A LATER DATE DO TO PAVEMENT BACK LOG
201701552001 | 2017-11-11 | LEAD | 1665 | DUELS | BRUXELLES | WILK | WM- LEAK ON THE SIDEWALK INLET LEAK IN THE METER BOX, FLOODING THE SIDEWALK (C) /** 1) MN: A325257 SN: 0069621, *TAP: SIZE: B LOC: 176 FEET FROM P LINE AT BRUXELLES, *MB: CODE: CD1 LOC: ON DUELS 176' FROM PL OF BRUXELLES ****/ | 2017-11-22 | EXCAVATED 4 X 4 SIDEWALK CUT RELOCATED METER BOX FROM THE GUTTER BOTTOM TO SIDEWALK TO PREVENT FUTURE ROLL ON BY CARS BACKFILLED AND CLEANED THE AREA *OUTLET RENEWED TO PROPERTY ALSO FOR 1663 + 1665* DUELS
201701552601 | 2017-11-11 | LEAD | 631 | CHARTRES | ST PETER | WMLK | WM- LEAK IN THE STREET LEAK ON THE MAIN IN THE STREET (C) 12/01/17 LEAK NOQW CAUSING A DEEP HOLE IN STREET PER INSPC K GRIFFIN/ SR#12822869 (AJR) 12/16/17 JOB GIVEN TO J. CLARK (BY INSP K. GRIFFIN). WILL ATTEMPT TO MAKE THE REPAIRS SUNDAY 12/17/17. ALSO /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-12-17 | ARRIVE AT ABOVE LOCATION EXCAVATED IN STREET OVER 12" WATER MAIN ON LEAD LINE MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVER SAND AND COLD MILL LJF
201701555102 | 2017-11-14 | LEAD | 2403 | CARONDELET | 1ST | WILK | /** 1) MN: A211946 SN: 0004255, *TAP: SIZE: C LOC: 84 FEET FROM P LINE AT CARONDELET, *MB: CODE: BDHM LOC: ON FIRST, 83.5' FROM P.L. CARONDELET ** 2) MN: A295243 SN: 0004255, *TAP: SIZE: A LOC: 85 FEET FROM P LINE AT CARONDELET, *MB: CODE: BDHM LOC: ON FIRST, 85' FROM P.L. CARONDELET THERE ARE 3 MORE NOT LISTED. ****/ | 2017-11-12 | EXAMINED JOB TO FIND NO WATER ON THE INLET EXCAVATED 7 X 3 MUD PLOT MADE REPLACED ON INLET SERVICE LINE TO RESTORE WATER TO INLET BACKFILL AND CLEANED THE AREA
201701558201 | 2017-11-12 | LEAD | 2528 | S MIRO | 3RD | WMTLK | METER LEAK METER# A421916 LOC.# 206746-551043 EXAMINE INLET AND OUTLET SERVICE FOR LEAK INSIDE BOX /** 1) MN: A276355 SN: 0077478, *TAP: SIZE: B LOC: 61 FEET FROM P LINE AT THIRD, *MB: CODE: __ LOC: ON S MIRO 62FT FROM PL THIRD ****/ | 2017-11-13 | EXAMINED METER NEEDS NEW COCK LEAKING FROM COCK.WHEN ARRIVED METER WAS IN OFF POSITION LEAFT IT THE SAME AS I FOUND IT.JOB CONTINUED
201701559502 | 2017-11-12 | LEAD | 1135 | ROYAL |  | WMRE | LOCATE AND RAISE TO GRADE /** 1) MN: B030628 SN: 0004770, *TAP: SIZE: B LOC: 71 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: AFK6 LOC: ON ROYAL,71' FROM U.S.P.L. GOV. NICHOLLS ** 2) MN: A264794 SN: 0004770, *TAP: SIZE: A LOC: 71 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: AFR6 LOC: 72FT FROM PL GOV NICHOLLS ****/ | 2017-12-12 | FOUND BOTH METERS ALREADY TO GRADE REMOVED MUD OUT OF METER CASING TO EXPOSE METER
201701559702 | 2017-11-12 | LEAD | 925 | N ROCHEBLAVE |  | WMRE | UNABLE TO LOCATE BY MEASUREMENTS REFER TO ZONE /** 1) MN: A196592 SN: 0020601, *TAP: SIZE: A LOC: 163 FEET FROM P LINE AT ST PHILIP, *MB: CODE: AFLM LOC: INS OF WLK BY HSE SW 163' P.L. ST PHILIP ****/ | 2017-12-12 | CUSTOMER BUILT FLOWER ON TOP OF METER BOX LOCATION JOB WAS ALREADY COMPLETED BY TRUCK 408
201701559902 | 2017-11-12 | LEAD | 853 | OLGA | DUMAINE | WMRE | METER FOUND BUT NEEDS TO RAISED /** 1) MN: A322938 SN: 0033601, *TAP: SIZE: A LOC: 200 FEET FROM P LINE AT DUMAINE, *MB: CODE: BD LOC: 200FT FROM USPL DUMAINE ****/ | 2017-12-08 | EXCAVATED 3 X 3 MUD PLOT THROUGH LIMESTONE AND BRICKS REPLACED 5/8 INCHMETER BOX COCK AND RAISED METER BOX TO GRADE BACK FILLED AND CLEANED THE LEFT TWO SAFETY ON JOB DUE TO WETTNESS OF MATERIAL170545552
201701560902 | 2017-11-12 | LEAD/PLASTIC | 8734 | PEAR |  | WMRE | RELOCATE METER /** 1) MN: A329996 SN: 0081580, *TAP: SIZE: B LOC: 247 FEET FROM P LINE AT MONROE, *MB: CODE: CDLN LOC: 247FT FROM PL MONROE ****/ | 2018-08-05 | EXCAVATED IN MUDPLOT. REPAIR INLET & OUTLET SERVICE LEAD & COOPER LINES ALSO RAISE TO GRADE DRESSED UP WITH RIVERSAND. JOB REFERRED TO ZONE2 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METERBOX.
201701561504 | 2018-01-14 | LEAD/PLASTIC | 2528 | ST THOMAS | 3RD | WMRE | /** 1) MN: A303821 SN: 0034710, *TAP: SIZE: A LOC: 70 FEET FROM P LINE AT ST THOMAS, *MB: CODE: BFHM LOC: ON THIRD 72FT FROM PL ST THOMAS 2' OUTSIDE PL 9' I ****/ | 2018-01-14 | EXCAVATED AND RASIE METERBOX TO GRADE WE BACKFILL AND CLEAN UP JOB SITE
201701566301 | 2017-11-12 | LEAD/PLASTIC | 2353 | ANNUNCIATION | SORAPARU | WMTLK | MI- LEAK IN CURB FLOODING STREET EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: A340011 SN: 0010973, *TAP: SIZE: B LOC: 25 FEET FROM P LINE AT SORAPARU, *MB: CODE: OOOO LOC: ON ANNUNCIATION, 24' FROM P.L. SORAPARU, 8' OUT- ****/ | 2017-11-17 | EXAMINED LEAK IN METER BOX EXCAVATED METER BOX EXPOSED INLET AND OUTLET OBSERVED LEAK ON INLET SERVICE COCK AND ON INLET SERVICE LINE REPARED AND REPLACED BACKFILLED
201701569401 | 2017-11-13 | LEAD | 1008 | ST PETER |  | WILK | LOCATION: 201010 MTR# A 355486 FRONT APT UNABLE TO CHANGE METER, BAD UNDER GROUND LEAK / PLEASE REPAIR AND CHANGE METER INLET SERVICE LEAKK IN BOX /** 1) MN: A278519 SN: 0026940, *TAP: SIZE: A LOC: 52 FEET FROM P LINE AT BURGUNDY, *MB: CODE: OOOO LOC: 58' P/L BURGUNDY 4' OUTSIDE 4' INSIDE CURB ****/ | 2017-12-07 | ARRIVED AT ABOVE LOCATION + FOUND 4 METER REPLACED 5/8 INCH CURB COCK ON ONE METER + REPLACED 5/8 INCH HANDWHEEL ON A SECOND METER ALSO REPLACED 5/8 INCH WATER METER AT ABOVE LOCATION BACKFILLED +DRESSED UP AREA OLD METER A355486 FACT:69295907 MAKE: SENSUS READ:6854
201701569801 | 2017-11-13 | LEAD | 2901 | LAFITTE |  | WMBK | UNABLE TO CHANGE METER. METER IS IN CEMENT. PLEASE REPAIR AND CHANGE METER A331846 LOC ID 191291 BROKEN METER BOX CASING, METER IS SITTING IN DIRT /** 1) MN: A331846 SN: 0149956, *TAP: SIZE: B LOC: 7 FEET FROM P LINE AT LAFITTE AVE, *MB: CODE: F LOC: ON N GAYOSO 20' P/L LAFITTE 5' OUTSIDE 7' INSIDE ****/ | 2017-12-06 | EXCAVATED 2 X 2 AROUND METER BOX RENEWED CEMENT AND CHANGE OUT DAMAGE METER SET 1 NEW HERSEY METER AND CASING BACK FILLEDE AND CLEANED THE AREA,,, OLD METER A331846 FACT:56042436 MAKE: SENSUS READ:11255
201701571601 | 2017-11-13 | LEAD | 2326 | N VILLERE | SPAIN | WILK | ML- METER LEAK METER # A240398 ACCT # 130089-481896 BAD BLEEDER VALVE PASSING IN ON POSITION /** 1) MN: A240398 SN: 0045113, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT SPAIN, *MB: CODE: AE2 LOC: ON NO. VILLERE,101' FROM U.R.P.L. SPAIN ****/ | 2017-12-07 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201701572701 | 2017-11-13 | LEAD | 1251 | RIVIERA AV | ST BERNARD AV | WILK | ML METER LEAK METER # A377179 ACCOUNT # 171622-475960 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A326281 SN: 0114548, *TAP: SIZE: B LOC: 360 FEET FROM P LINE AT ST BERNARD AVE, *MB: CODE: AKO LOC: 360FT FROM PL ST BERNARD OPP 2ND WINDOW 8' OUTSIDE ****/ | 2017-12-13 | EXCAVATED IN MUDPLOT ON INLET LEAK MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVER SAND. LJF
201701573001 | 2017-11-13 | LEAD | 3105 | N CLAIBORNE AV | CLOUET | WMLK | ************PICKUP************ LEAK ON THE MAIN /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-12-18 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH ABANDON INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201701573101 | 2017-11-13 | LEAD | 41 | EGRET | ROBERT E LEE BL | WILK | ML METER LEAK METER# A343146 ACCT# 170767-513665 INLET SERVIC LEAK IN MUDPLOT /** 1) MN: A324844 SN: 0116563, *TAP: SIZE: A LOC: 613 FEET FROM P LINE AT ROBERT E LEE BLVD, *MB: CODE: AF LOC: ON EGRET, 613' FROMP.L. ROBERT E. LEE BLVD., 4' ****/ | 2017-12-27 | EXCAVATED A 3 X 4 CUT IN CONCRETE DRIVEWAY OVER A 5/8 INLET SERVICE LEAK. LEAD ON INLET CHANGED THE COCK RAISE METERBOX UP TO GRADE REPLACED 8 FT OF LEAD OUTLET WITH 3/4 PVC PLASTIC TO PROPERTY BACKFILLED WITH RIVERSAND & COLDMILL JOB COMPLETE PAVING 3 X 4 CUT S/W JEG
201701575001 | 2017-11-13 | LEAD | 3203 | BIENVILLE | N LOPEZ | WMTLK | ML - METER LEAK ACCOUNT NUMBER - 126367-5189251 METER NUMBER - A414445 EXAMINE INLET/OUTLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: A345767 SN: 0050022, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT BIENVILLE, *MB: CODE: ADH LOC: 2ND METER BY 2ND TREE SIDE GUTTER ON N LOPEZ 53.5 ****/ | 2017-12-08 | EXCAVATED 3 X 3 MUD PLOT UNABLE TO FIND LEAK
201701575101 | 2017-11-13 | LEAD | 4779 | BACCICH |  | WILK | METER LEAK INLET SERVICE LEAK BEHND CURBCOCK /** 1) MN: A296812 SN: 0091728, *TAP: SIZE: A LOC: 40 FEET FROM P LINE AT MIRABEAU AVE, *MB: CODE: BDKM LOC: ON BACCICH 40' FROM PL MIRABEAU AVE 8.5' OUTSIDE P ****/ | 2017-11-15 | EXAMINE LOCATION FOUND OUTLET SERVICE LEAKING & METER WAS BELOW GRADE. EXCAVATED DOWN ON INLET & OUTLET SERVICE'S FOUND LEAD.. MADE REPAIR'S BY REPLACING COCK, WASHER, HAND WHEEL. UPPER CASING & OUTLET SERVICE FROM METER TO PROPERTY ALSO ADDED PLASTIC TUBING TO INLET TO RAISE METER TO GRADE. BACKFILLED DRESS UP.
201701575501 | 2017-11-13 | LEAD/PLASTIC | 3520 | RUE DELPHINE | LACOUR MONIQUE | WILK | ML METER LEAK ACCT# 232297-416787 METER# C033930 INLET SERVICE LEAK AT CURB CURB FLOODED LEFT ONE (1) FOR PROTECTION /** 1) MN: C026794 SN: 0145329, *TAP: SIZE: C LOC: 167 FEET FROM P LINE AT LACOUR MONIQUE, *MB: CODE: CDLM LOC: RES.ON DELPHINE 167' FROM PL LACOUR MONIQUE 8' OUT ****/ | 2018-01-04 | EXCAVATED METER BOX AND FOUND LEAK COMING FROM INSIDE BOX REPLACED METER WASHERS TO REPAIR LEAK BACKFILLED
201701577401 | 2017-11-14 | LEAD | 3227 | BELFORT AV | CRETE | WILK | ML- METER LEAK MTR# A 122966 ACCT# 144236-492819 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A122966 SN: 0090675, *TAP: SIZE: A LOC: 393 FEET FROM P LINE AT CRETE, *MB: CODE: ADKN LOC: ON BELFORT 393FT FROM PL CRETE ****/ | 2017-12-06 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH METER BOX COCK AND HANDWHEEL TO STOP LEAK BACKFILL AND CLEANED THE AREA
201701577501 | 2017-11-14 | LEAD | 2515 | EADS | N DORGENOIS | WILK | WM-LEAK IN SIDEWALK EXAMINE INLET SERVICE FOR LEAK METER UNDER WATER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-12-04 | EXCAVATED 2 X 2 MUD PLOT METER CASING IN THE CORRECT POSITION BACKFILLED AND CLEANED THE AREA
201701577701 | 2017-11-14 | LEAD | 1600 | ELYSIAN FIELDS AV | N DERBIGNY | WILK | ML - METER LEAK ACCOUNT NUMBER - 102295-493614 METER NUMBER - B039467 INLET SERVICE LEAK IN MUDPLOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-12-04 | EXCAVATED 4 X 4 SIDEWALK CUT MADE REPAIR ON ABANDON INLET SERVICE LINE BACKFILL AND CLEAN THE AREA
201701579001 | 2017-11-14 | LEAD | 1517-19 | LOUISA DR |  | WMBK | NEED CURB COCK INSTALLED CUSTOMER IS WAITING ON WATER PLEASE REPAIR LOCATION #303346 METER BOX SHIFTED OVER CURB COCK HOUSE UNDER RENOVATION /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-11-30 | RENEW OUTLET SERVICE TO PROPERTY AND SET A 5/8 INCH METER BACKFILLED JOB AREA
201701580001 | 2017-11-14 | LEAD/PLASTIC | 5029 | S PRIEUR | ROBERT | WILK | ML - METER LEAK ACCOUNT NUMBER - 161920-704631 METER NUMBER - A316515 INLET SERVICE LEAK BEHING CURB COCK FLOODING GRASSY AREA & GUTTER BOTTOM /** 1) MN: A254983 SN: 0100694, *TAP: SIZE: A LOC: 224 FEET FROM P LINE AT ROBERT, *MB: CODE: AD LOC: ON SO. PRIEUR, 221' FROM P.L. ROBERT, 5' OUTSIDE ****/ DOTTIE READY 4-16-18 EXP 5-6-18 | 2018-04-16 | UNABLE TO REMOVE LEAD DUE TO CAR PARKED TO CLOSE . REPLACED 5/8 CURB TO STOP LEAK TIED INTO LEAD.
201701580301 | 2017-11-14 | LEAD/PLASTIC | 8405 | COHN |  | WOLK | MI-LEAD WHIP NEEDS TO BE CHNAGED ACCT#302847-700823 METER# NOT AVAILABLE IS COGSDALE READY FOR TIE IN HOLE OPEN ****HOUSE UNDER RENOVATIONS*** /** 1) MN: SN: 0079609, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT CAMBRONNE, *MB: CODE: CFM LOC: ON COHN, 35' FROM P.L. CAMBRONNE, 1' OUTSIDE P.L., ****/ | 2017-11-20 | EXCAVATED IN MUDPLOT THROUGH DEBRIS TO CHANGED LEAD WHIP FROM METERBOX TO PROPERTY. ********************************NO METER********************************** JEG
201701580501 | 2017-11-14 | LEAD | 3602 | HAVANA | SERE | WILK | ML-METER LEAK ACCT#162933-496946 METER#A386832 INLET SERVICE LEAK IN THE MUD PLOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-12-21 | EXCAVATED IN MUDPLOT ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL LJF
201701582901 | 2017-11-14 | LEAD/PLASTIC | 1228 | CAMBRONNE | OAK | WOLK | MI LEAK IN GRASSY AREA BY SIDEWALK EXAMINE OUTLET SERVICE FOR A LEAK /** 1) MN: A236169 SN: 0025404, *TAP: SIZE: A LOC: 78 FEET FROM P LINE AT PLUM, *MB: CODE: CFM LOC: ON CAMBRONNE 77FT FROM PLUM ****/ | 2018-04-09 | MADE A 2 X 2 SIDEWALK BRICK CUT EXCAVATED AND RAISE A 5/8 METER TO GRADE AND RENEWED THE OUTLET FROM THE METER BOX TO PEROPERTY LEAD INLET PLASTIC OUTLET REFERRE THAT BRICK CUT TO PAVING
201701585501 | 2017-11-15 | LEAD/PLASTIC | 2610 | BEHRMAN HW | IDAHO | WILK | ***************PICKUP*************** INLET SERVICE LEAK IN MUDPLOT MN#A-390132 ACC#238710-411351 /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-01-03 | EXCAVATED INLET SERVICE TO EXPOSE LEAK FOUND LEAK BETWEEN BOX AND WATER MAIN RAN NEW LINE FROM TEE TO WATER MAIN
201701585601 | 2017-11-15 | LEAD/PLASTIC | 1029 | PHILIP | MAGAZINE | WILK | MI - METER LEAK MTR# A 118038- ACCT# 126574-542509 INLET SERVICE BAD BLEEDER VALVE FLOODING GRASS & GUTTER BOTTOM /** 1) MN: A118038 SN: 0050439, *TAP: SIZE: A LOC: 108 FEET FROM P LINE AT MAGAZINE, *MB: CODE: ADN LOC: BET CONSTANCE AND MAGAZINE 108FT FR PL MAGAZINE ****/ | 2017-12-14 | EXAMINED LEAKING AREA EXCAVATED METER BOX OBSERVED LEAK ON INLET SERVICE REPLACED INLET SERVICE UNABLE TO REMOVE DUE TO TIME
201701585701 | 2017-11-15 | LEAD | 1231 | FRANKLIN AV | URQUHART | WMEX | LOCATIONID#120418-481625 METER#A412687 CEMENT INSIDE METERBOX /** 1) MN: 000000 SN: 0036156, *TAP: SIZE: A LOC: 111 FEET FROM P LINE AT URQUHART, *MB: CODE: CDMN LOC: ON LAFAYETTE,111' FROM L.R.P.L. URQUHART ****/ | 2017-12-01 | REMOVE CEMENT FROM INSIDE OF METER BOX
201701586901 | 2017-11-15 | LEAD/PLASTIC | 3708 | PRESTON PL | BERKLEY DR | WILK | ML-METER LEAK INLET SERVICE LEAK IN BOX /** 1) MN: A321756 SN: 0145876, *TAP: SIZE: B LOC: 538 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: ADL3 LOC: 544FT FROM PL BERKLEY ****/ | 2017-12-06 | ARRIVED ON JOBSITE EXAMINED FOUND LEAK ON INLET EXCAVATED MADE REPAIRS BACKFILLED AND CLEANED JOBSITE
201701588401 | 2017-11-15 | LEAD | 2013 | NAPOLEON AV | DANNEEL | WOLK | MI CHANGE LEAD WHIP EXPOSED METER # C018262 ACCOUNT # 107638-553930 CHANGE LEAD WHIP HOLE OPEN, BAD LEAK ON LEAD LINE /** 1) MN: C018262 SN: 0009213, *TAP: SIZE: C LOC: 128 FEET FROM P LINE AT DANNEEL, *MB: CODE: ADK2 LOC: ON NAPOLEON AVE 126.5FT FROM PL OF DANNEEL 9FT OUT ****/ | 2017-11-16 | EXCAVATED IN MUDPLOT REPAIR 1' LEAD ON THE OUTLET SIDE UNABLE TO RENEW 1' LEAD LINE BECAUSE IT FEEDING OFF 1' CONTROLING LEAD LINE FEEDING 2OTHER HOUSES... JOB REFER TO ZONE 3 TO TAKE LEAD OUT THE HOLE
201701589801 | 2017-11-15 | LEAD/PLASTIC | 6361 | ESSEX CT | CUT OFF RD | WILK | ML-METER LEAK ACCT#229305-419309 METER#157533 INLET SERVICE LEAK /** 1) MN: A157533 SN: 0129222, *TAP: SIZE: B LOC: 36 FEET FROM P LINE AT CUT OFF RD, *MB: CODE: CD LOC: ON ESSEX CT., 36' FROM U.P.L. CUT OFF RD., 8' OUT- ****/ | 2017-12-07 | EXCAVATED ON METER BOX FOR LEAK FOUND LEAK INSIDE BOX MADE REPAIR BACKFILLED AND CLEANED JOB SITE
201701589901 | 2017-11-15 | LEAD | 1714 | JOLIET |  | WILK | ML- METER LEAK ACCT# 137539-589492 MTR# A372123 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A266908 SN: 0068259, *TAP: SIZE: A LOC: 129 FEET FROM P LINE AT GREEN, *MB: CODE: AD LOC: ON JOLIET ST 129' FROM PL GREEN ****/ | 2018-03-11 | EXCAVATED IN MUDPLOT,REPAIR 5/8 STOP AND WASTE LEAD LINE.DRESS UP WITH RIVERSAND. JOB REFERRED TO ZONE 1 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201701590701 | 2017-11-15 | LEAD | 6053 | WARRINGTON DR |  | WMTLK | WM- LEAK ON THE SIDEWALK EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: A250780 SN: 0107661, *TAP: SIZE: A LOC: 620 FEET FROM P LINE AT BURBANK DR, *MB: CODE: CD LOC: 622FT FROM PL BURBANK DR 7' OUTSIDE PL 4' INSIDE C ****/ | 2018-01-03 | EXCAVATED A 4 X 5 MUDPLOT CUT TO REPAIR INLET SERVICE LEAK AND RAISE METERBOX TO GRADE FOUND LEAD ON INLET SERVICE NO METER INSIDE METERBOX. JEG
201701591101 | 2017-11-15 | LEAD/PLASTIC | 4627 | FRENCHMEN | SUMPTER | WILK | ML- METER LEAK AT METER # A 414423 ACCT# 150563 - 501807 INLET SERVICE LEAK IN MUDPLOT FLOODING SIDEWALK /** 1) MN: A117716 SN: 0108516, *TAP: SIZE: B LOC: 175 FEET FROM P LINE AT SUMPTER, *MB: CODE: CD LOC: ON FRENCHMEN 175FT FROM SUMPTER ****/ | 2018-10-24 | EXCAVATED IN MUD PLOT TO REPAIR INLET SERVICE LINE AND RAISE METER TO GRADE FOUND LEAD ON INLET
201701591301 | 2017-11-15 | LEAD | 1474 | N ROMAN | COLUMBUS | WILK | ML- METER LEAK METER#A370208 ACCT#212709-487933 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A147950 SN: 0057405, *TAP: SIZE: A LOC: 93 FEET FROM P LINE AT COLUMBUS, *MB: CODE: CD LOC: ON ROMAN 93FT FROM DIV P/L COLUMBUS 6FT OUTSIDE 3' ** 2) MN: A299639 SN: 0057405, *TAP: SIZE: A LOC: 92 FEET FROM P LINE AT COLUMBUS, *MB: CODE: CD LOC: ON ROMAN 92FT FROM COLUMBUS 6FT OUTSIDE 3'INSIDE ****/ | 2017-12-08 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201701592101 | 2017-11-16 | LEAD | 23 | RAIL |  | WDSM | DECREASE EXISTING SERVICE FROM 1 1/2 INCH TO A 5/8 INCH WATER METER FOR 23 RAIL ST IN SAME LOCATION FOR THE FLAT SUM OF $100.00 SWBNO APP#122284 WFA 2513 /** 1) MN: D005199 SN: 0107169, *TAP: SIZE: CCC LOC: 335 FEET FROM P LINE AT TERN, *MB: CODE: FM4 LOC: OPP GAS METER 3FT FROM FENCE INSIDE BUSHES--ON ****/ | 2017-12-26 | DECREASED A 1 1/2 METER DOWN TO A 5/8 METER. ALSO SET A 5/8 METER. LEAD ON THE INLER & OUTLET. JOB COMPLETE REMOVED D-5199 ROCKWELL 38413512 RDG 1233500 INSTALLED A-405832 HERSHEY 14111594 RDG 0000
201701592201 | 2017-11-16 | LEAD/PLASTIC | 210 | RIVER OAKS DR | GEN MEYER AV | WILK | WM-LEAK IN THE STREET INLET SERVICE LEAK IN MUDPLOT FLOODING CURB /** 1) MN: A142776 SN: 0117687, *TAP: SIZE: A LOC: 351 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: CDL LOC: ON RIVER OAKS DR., 347' FROM P.L. GEN. MEYERS AVE. ****/ | 2017-12-10 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 INLET SERVICE BACKFILLED AREA
201701593001 | 2017-11-16 | LEAD | 1508 | BASIN | N VILLERE | WILK | MI- LEAK ON SIDEWALK **ON N.VILLERE ST ORANGE STAKE AT LEAK** INLET SERVICE LEAK ON N VILLERE INTERFERING WITH CONTRACTORS WORK /** 1) MN: A326018 SN: 0045948, *TAP: SIZE: D LOC: 64 FEET FROM P LINE AT NO. VILLERE, *MB: CODE: __ LOC: ON ST. PETER, 64' FROM P.L. NO. VILLERE ****/ | 2017-11-16 | EXCAVATED 3 X 3 MUD PLOT MADE REPAIR ON ABANDON INLET SERVICE BACKFILLED AND CLEANED UP AREA
201701593401 | 2017-11-16 | LEAD/PLASTIC | 1709 | WAGNER |  | WILK | MI LEAK ON THE SIDEWALK INLET SERVICE LEAK IN ASPHALT STREET FLOODING AREA /** 1) MN: A116691 SN: 0108991, *TAP: SIZE: A LOC: 518 FEET FROM P LINE AT BRINGIER, *MB: CODE: AGLN LOC: 522FT FROM PL. BRINGER 7' OUTSIDE PL 7' INSIDE CUR ****/ | 2017-12-13 | EXAMINED METER BOX EXCAVATED INLET SERVICE TO CURB EXPOSED INLET AND OUTLET SERVICE IN STREET MACCHINE NEEDED
201701593701 | 2017-11-16 | LEAD | 5514 | N ROMAN | CAFFIN AV | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: SN: 0129658, *TAP: SIZE: B LOC: 129 FEET FROM P LINE AT FLOOD, *MB: CODE: BDL LOC: RES ON N ROMAN 129' P.L. FLOOD ****/ | 2017-12-01 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 INCH CURB COCK FOR ABANDON SERVICE BACKFILLED AREA
201701595201 | 2017-11-16 | LEAD/PLASTIC | 414 | WHITNEY AV | ALIX | WMTLK | ML- METER LEAK METER# B026723 ACCT # 225259-403163 EXAMINE INLET AND OUTLET SERVICE FOR LEAK INSIDE BOX /** 1) MN: B026723 SN: 0091018, *TAP: SIZE: B LOC: 113 FEET FROM P LINE AT ALIX, *MB: CODE: CD LOC: ON WHITNEY 113FT FROM ALIX ****/ | 2017-12-05 | EXCAVATED METER EXPOSED INLET AND OUTLET REMOVED LEAD TO PROPERTY AND REPLACED WITH PLASTIC LEAD ON INLET NEED MACHINE TO REPLACE REPLACED OLD METER BOX WITH NEW METER BOX CONPLETE
201701595701 | 2017-11-16 | LEAD | 2540 | ST PHILIP |  | WILK | METER LEAK/METER BOX OVER FLOWING BAD BLEEDER VALVE PASSING IN ON POSITION /** 1) MN: A140589 SN: 0060202, *TAP: SIZE: A LOC: 111 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: ADN LOC: ON ST. PHILIP,109' FROM P.L. NO. DORGENOIS ****/ | 2017-12-08 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DREESED UP AREA
201701595801 | 2017-11-16 | LEAD | 928 | N RENDON | DUMAINE | WILK | ML--METER LEAK ACCT# 124838-701403 METER# A423474 BAD BLEEDER VALVE PASSING IN ON POSITION /** 1) MN: A143876 SN: 0046337, *TAP: SIZE: A LOC: 117 FEET FROM P LINE AT ST PHILIP, *MB: CODE: CE LOC: ON NO. RENDO,118' FROM U.S.P.L. ST. PHILIP ****/ | 2017-12-01 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA
201701596101 | 2017-11-16 | LEAD | 1533 | ESPLANADE AV | N CLAIBORNE AV | WMTLK | ML- METER LEAKING ****AGAIN**** FLOODING AREA METER# A426761 CHANGED FROM 1414 N CLAIBORNE AV AND ESPLANADE AV EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER N N CLAIBORNE AV 11/17/17 LEAK NOW CAUSING POOR PRESSURE PER SR#12821438 (AJR) /** 1) MN: E006847 SN: 0062634, *TAP: SIZE: __ LOC: 109 FEET FROM P LINE AT ESPLANADE AV, *MB: CODE: OOO LOC: N CLAIBORNE AV BET KERLEREC & ESPLANADE AV 109' ****/ | 2017-12-07 | SET METER WITH 2 NEW 5/8 INCH WASHER TO STOP LEAK LEFT SAFETY BARREL OVER METER TO PREVENT ROLL OVER UNTIL AREA IS CEMENTED BACK
201701596301 | 2017-11-16 | LEAD | 2220 | ST ANTHONY AV | N MIRO | WILK | BAD MTR LEAK/AREA FLOODED/GREEN ALGAE/NO MTR IN BOX INLET SERVICE LEAK NO METER IN BOX, ALSO REPLACE METER BOX COVER /** 1) MN: A227880 SN: 0063288, *TAP: SIZE: A LOC: 142 FEET FROM P LINE AT MIRO N, *MB: CODE: CFK LOC: 142' P.L. N MIRO ****/ | 2017-12-15 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILL + DRESSED UP AREA ( NO METER)
201701596501 | 2017-11-16 | LEAD | 1830 | BIENVILLE | N ROMAN | WMLK | WM LEAK ON THE SIDEWALK LEAK ON THE MAIN /** 1) MN: A276102 SN: 0021783, *TAP: SIZE: A LOC: 38 FEET FROM P LINE AT ROMAN N, *MB: CODE: BFL6 LOC: METER ON BIENVILLE 37.6 FT FROM PL N ROMAN ****/ | 2017-12-04 | EXCAVATED IN CONCRETE WALKWAY NEAR PROPERTY + MADE REPAIR ON 3/4 INCH ABANDONED INLET SERVICE LINE COMPACTED BACKFILL + DRESSED UP AREA (NO METER)
201701596901 | 2017-11-16 | LEAD | 5361 | FRANKLIN AV | FILMORE AV | WMTLK | MI- LEAK IN THE STREET, FLOODING THE AREA EXAMINE INLET & OUTLET SERVICE FOR A LEAK ON SIDEWALK FLOODING SIDEWALK & CURB /** 1) MN: C016422 SN: 0104795, *TAP: SIZE: C LOC: 129 FEET FROM P LINE AT FILLMORE AVE, *MB: CODE: ADK4 LOC: 129FT FROM PL FILLMORE 7FT OUTSD PL ****/ | 2017-12-19 | EXCAVAATED IN CONCRETE SIDEWALK. REPAIR 1 INCH STOP & WASTE LEAD LINE. DRESS UP WITH RIVER SAND & COLD MILL. REF JOB TO ZONE 5 TO TAKE LEAD LINE OUT. REF TO PAVE 3 X 3 CONCRETE S/W CUT LJF
201701597101 | 2017-11-16 | LEAD | 3102 | GEN TAYLOR |  | WMTLK | WM - LEAK ON THE SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER GRASSY AREA FLOODED, CARS ROLLING OVER METER /** 1) MN: A272452 SN: 0065961, *TAP: SIZE: B LOC: 67 FEET FROM P LINE AT GEN TAYLOR, *MB: CODE: ADHL LOC: ON S DERBIGNY 68FT PL GEN TAYLOR 7' OUTSIDE 3' ** 2) MN: A277988 SN: 0065961, *TAP: SIZE: B LOC: 66 FEET FROM P LINE AT GEN TAYLOR, *MB: CODE: DHL LOC: 65' P/L GEN TAYLOR 8' OUTSIDE 3' INSIDE CURB ****/ DOTTIE READY 2-2-18 EXP 2-22-18 | 2018-02-06 | EXAMINE JOB AND PUMP METER OUT AND FOUND BAD METER COCK AND EXCAVATED IN 5 X 5 IN MUDPLOT AND METER REPAIR TO METER COCK AND TIED ONTO LEAD LINE AND BACKFILLED JOB WITH RIVERSAND.
201701597201 | 2017-11-16 | LEAD | 3900 | CANAL | S SCOTT | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK ON SIDEWALK FLOODING AREA /** 1) MN: A253408 SN: 0011998, *TAP: SIZE: B LOC: 84 FEET FROM P LINE AT CANAL, *MB: CODE: OOO LOC: ON SCOTT 82FT FROM PL CANAL 11FT OUTSD PL SCOTT ****/ DOTTIE READY 4-16-18 EXP 5-6-18 | 2018-04-18 | ARRIVED ON JOB EXCAVATED IN DRIVEWAY FOUND LEAK ON 1" LEAD SERVICE ON ABANDON LINE MADE REPAIRS AND BACKFILLED. JOB COMPLETE.
201701597501 | 2017-11-16 | LEAD | 1542 | RIVIERA AV | PARIS AV | WMLK | WM-LEAK IN STREET LEAK ON THE WATER MAIN ON RIVIERA AV ON SIDEWALK FLOODING SIDEWALK, INTERFERING WITH CONTRACTORS WORK /** 1) MN: C024542 SN: 0110960, *TAP: SIZE: C LOC: 164 FEET FROM P LINE AT PARIS AVE, *MB: CODE: BD LOC: ON RIVIERA, 164' FROM P.L. PARIS AVE., 12' OUTSIDE ****/ | 2017-12-27 | EXCAVATED A 12 X 8 MUDPLOT CUT TO REPAIR 1'' TAILPIECE OF AN INLET SERVICE FOR 1524 RIVIERA AVE FOUND LEAD PIPE AND NEEDS TO BE REMOVED. JEG
201701598001 | 2017-11-16 | LEAD/PLASTIC | 1738 | ROBERT | DANNEEL | WILK | ML-METER LEAK ACCOUNT #103511-573633 METER #A316350 METER IS ON DANNEE INLET SERVICE LEAK 01/11/18 CUST STATED LEAK HAS GOTTEN WORSE (KSW) 05/03/18 CUST STATES LEAK HAS GOTTEN WORSE (NLD) /** 1) MN: A316350 SN: 0022288, *TAP: SIZE: B LOC: 76 FEET FROM P LINE AT ROBERT, *MB: CODE: BDHM LOC: ON DANNEEL 76FT FROM URPL OF ROBERT ****/ DOTTIE READY 5-7-18 EXP 5-27-18 | 2018-06-06 | EXAMINE WATER LEAK IN TREE ROOTS FOUND 3/4 LEAD LEAKING REPLACED 6FT. OF 3/4 TUBING UNABLE TO REMOVE LEAD DUE TO CAR PARKED OVER WATER MAIN.
201701598801 | 2017-11-16 | LEAD | 4023 | N CLAIBORNE AV | MAZANT | WOLK | ML- METER LEAK AT METER# A 383171 ACCT# 207678-703774 EXAMINE OUTLET SERVICE UP TO PROPERTY LINE FOR LEAK /** 1) MN: A321552 SN: 0076667, *TAP: SIZE: B LOC: 11 FEET FROM P LINE AT MAZANT, *MB: CODE: __ LOC: ON N CLAIBORNE AVE 10FT FROM D.P.L. MAZANT 3FT OUT ****/ | 2017-12-22 | EXCAVATED 5 X 3 MUD PLOT RAISED METER BOX TO GRADE AND REMOVED LEAD TO PROPERTY BACKFILL AND CLEANED THE AREA 4021 N CLAIBORN METER BOX WAS ALSO RAISED TO GRADE
201701599601 | 2017-11-17 | LEAD | 719 | DUMAINE | ROYAL | WOLK | 148580-528055 METER# D004205 CONSTANT REGISTRATION ON METER PLEASE REPAIR. /** 1) MN: D004205 SN: 0017389, *TAP: SIZE: C LOC: 48 FEET FROM P LINE AT ROYAL, *MB: CODE: BER5 LOC: ON DUMAINE ST 146.5' FROM PL ROYAL ST ****/ | 2017-12-13 | ARRIVED AT ABOVE LOCATED CALL PROPERTY MANAGER TO MAINTENCE WORK TO PERFORM STOP + WASTE TEST FOUND NO CONSTANT REGISTRATION ON METER ANY LEAK
201701602601 | 2017-11-17 | LEAD | 2037 | ALLEN | S GALVEZ | WMBK | MI METER BOX BROKEN REPLACE MISSING METER BOX CASING AND COVER /** 1) MN: A197678 SN: 0047040, *TAP: SIZE: A LOC: 32 FEET FROM P LINE AT GALVEZ N, *MB: CODE: ADK LOC: 34' P.L. N GALVEZ ****/ | 2017-11-28 | REPLACED BROKEN METER BOX CASING AND COVER
201701603201 | 2017-11-17 | LEAD | 2654 | N GALVEZ | ALMONASTER AV | WILK | ML- METER LEAK MTR# B041939 ACCT# 133204-479336 INLET SERVICE LEAK CARS ROLLING OVER METER /** 1) MN: B030423 SN: 0076619, *TAP: SIZE: B LOC: 136 FEET FROM P LINE AT ALMONASTER, *MB: CODE: OOO LOC: ON GALVEZ 135FT FROM ALMONASTER ****/ | 2017-11-28 | EXCAVATED 3 X 2 SIDEWALK CUT MOVED METER BOX FROM THE GUTTER TO SIDEWALK BACKFILLED AND CLEANED THE AREA
201701605401 | 2017-11-17 | LEAD/PLASTIC | 2719 | BRISTOL PL | HERSCHEL | WMBK | **********PICKUP JOB********** METER BOX CASING SHIFTED OVER CURB COCK, LEFT ONE CONE /** 1) MN: B019061 SN: 0122110, *TAP: SIZE: B LOC: 172 FEET FROM P LINE AT HERSCHEL, *MB: CODE: CDLM LOC: ON BRISTOL PL., 172' FROM P.L. HERSCHEL, 9' OUT- ****/ | 2018-02-27 | LOCATED METER BOX AND EXCAVATED METER BOX SET TO PROPER GRADE
201701607301 | 2017-11-18 | LEAD | 2217 | PIETY | N MIRO | WILK | WM-LEAK IN BETWEEN STREET AND SIDEWALK INLET SERVICE LEAK AT THE CURB /** 1) MN: SN: 0084328, *TAP: SIZE: A LOC: 139 FEET FROM P LINE AT MIRO N, *MB: CODE: CEN1 LOC: ON PIETY 139' FROM PL OF MIRO N ****/ | 2017-11-28 | EXCAVATED 2 X 2 SIDEWALK CUT ALSO 3 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE TO STOP LEAK BACKFILL AND CLEANED THE AREA
201701607401 | 2017-11-18 | LEAD/PLASTIC | 5916 | LAUREL | ELEONORE | WILK | WM-LEAK IN SIDEWALK BLEEDER VALVE LEAKING (FLOODING THE GRASS) C 01/22/18 UPGRADE TO B LEAVE IN SYSTEM PER C PLAINS (NLD) /** 1) MN: A280333 SN: 0019068, *TAP: SIZE: A LOC: 140 FEET FROM P LINE AT ELEONORE, *MB: CODE: CDLM LOC: ON LAUREL 139.7' FROM UPL ELEONORE ****/ | 2018-02-23 | ARRIVED ON JOB SITE AND CURB COCK LEAKING .MADE A 4 X 4 CUT ON SIDEWALK AND EXCAVATED ON SIDEWALK AND MADE REPAIRS AND TIED ONTO LEAD LINE .LEAD NEED TO BE REMOVE AND REPLACE WITH PLASTIC.BACKFILLED JOB COMPLETE.
201701607801 | 2017-11-18 | LEAD | 264 | HILLARY | BENJAMIN | WILK | ML- METER LEAK METER#A376778 ACCT#122069586438 CURB COCK LEAKING. LEAKING IN THE GRASSY AREA & SIDEWALK. GETTING OFF IN DCB 03/07/18 CALLER STATES LEAK HAS GOTTEN WORSE (KSW) /** 1) MN: A317868 SN: 0033014, *TAP: SIZE: A LOC: 39 FEET FROM P LINE AT HILLARY, *MB: CODE: __ LOC: ON BENJAMIN 33.4' FROM UPL HILLARY ST ****/ | 2018-03-13 | EXCAVATED IN SIDEWALK ON INLET ON LEAD MADE ALL REPAIRS TO STOP BACKFILL WITH RIVERSAND.REFER TO ZONE 1 TO REMOVE LEAD.
201701610601 | 2017-11-19 | LEAD/PLASTIC | 8931-33 | NELSON | HOLLYGROVE | WMRE | **********PICKUP JOB*********** ******B LEAVE IN SYSTEM****** LOCATE WATER SERVICE AND MARK METER COVERED WITH CONCRETE REFER CUSTOMER TO CLAIMS DEPARTMENT ALSO SPOKE WITH CUSTOMER /** AT 8931: 1) MN: A307297 SN: 0069933, *TAP: SIZE: B LOC: 73 FEET FROM P LINE AT HOLLYGROVE, *MB: CODE: ADL4 LOC: ON NELSON, 73' FROM P.L. HOLLYGROVE ****/ | 2017-12-07 | EXCAVATED A 3 X 6 CUT IN CONCRETE SIDEWALK TO EXPOSED A 5/8 SERVICE PLASTIC INLET REPLACED 8 FT WITH 3/4 PVC PIPE TO PROPERTY BACKFILLED AND DRESSUP
201701620002 | 2017-11-20 | LEAD/PLASTIC | 1330 | ORIOLE | PERLITA | WMRE | LOCATE AND RAISE TO GRAD METER CANT BE READ FOR REVENUE 12/05/17 PER SR#12823223 METER SHIFTED, CASING SITTNG IN TREE ROOTS, REPAIR AND CHANGE METER (AJR) /** 1) MN: C025970 SN: 0121050, *TAP: SIZE: C LOC: 72 FEET FROM P LINE AT ORIOLE, *MB: CODE: CFHL LOC: ON PERLITA 75FT FROM PL ORIOLE 3FT OUTSD PL 9FT IN ** 2) MN: 000000 SN: 0000000, *TAP: SIZE: __ LOC: 0 FEET FROM P LINE AT , *MB: CODE: __ LOC: ****/ | 2018-05-27 | EXCAVATED REMOVED TREE ROOTS AND METER BOX, REPLACED ONE INCH METER BOX COMPLEE AND REMOVED MORE TREE ROOTS AND SET ONE INCH METER. FOUND PLASTIC ON INLET AND LEAD ON OUTLET IN TREE REFER BACK TO ZONE TO REROUTE LEAD OUT OF TREE.
201701620003 | 2018-05-29 | LEAD/PLASTIC | 1330 | ORIOLE | PERLITA | WRMS | RELOCATE METER OUT OF OAK TREE. FOUND LEAD ON OUTLET IN TREE. /** 1) MN: C025970 SN: 0121050, *TAP: SIZE: C LOC: 72 FEET FROM P LINE AT ORIOLE, *MB: CODE: CFHL LOC: ON PERLITA 75FT FROM PL ORIOLE 3FT OUTSD PL 9FT IN ** 2) MN: 000000 SN: 0000000, *TAP: SIZE: __ LOC: 0 FEET FROM P LINE AT , *MB: CODE: __ LOC: ****/ | 2019-03-04 | MADE A 4 X 8 MUD CUT IN TREE ROOTS EXCAVATED RELOCATED A 1" METER FROM OUT OF A TRE AND RENEWED OUTLET FROM LEAD TO PLASTIC IT'S ALSO PLASTIC ON THE INLET
201701621401 | 2017-11-20 | LEAD/PLASTIC | 4944 | DESIRE | MIRABEAU AV | WILK | MI- LEAK BETWEEN THE SIDEWALK AND THE STREET ****************W.BLAKE @ 12:07PM*************** INLET SERVICE LEAK IN MUDPLOT FLOODING SIDEWALK CUSTOMER OUT OF WATER, NO ANSWER @ DOOR /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-11-20 | EXAMINE LOCATION FOUND LEAK COMING FROM INLET SERVICE. EXCAVATED DOWN ON INLET & OUTLET SERVICES. FOUND LEAD & PLASTIC TUBING. MADE REPAIR'S BY REPLACING COCK, WASHER'S, HAND WHEEL & 2 FT OF INLET ALSO OUT FROM METER TO PROPERTY.
201701626201 | 2017-11-20 | LEAD | 728 | MOSS | ORLEANS AV | WILK | WM LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET FLOODING STREET /** 1) MN: A187947 SN: 0089120, *TAP: SIZE: Y LOC: 102 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: CDLN LOC: ON MOSS,100' FROM P.L. ORLEANS AVE.,8' OUTSIDE ****/ | 2017-12-12 | EXCAVATED IN MUD PLOT + REPLACED 1 1/4 X 3/4 INCH TEE BACKFILLED + DRESSED UP AREA
201701630102 | 2017-11-21 | LEAD/PLASTIC | 1022 | DANTE | FRERET | WMRE | LOCATE AND RASIE TO GRADE NED MACHINE /** 1) MN: A333412 SN: 0043993, *TAP: SIZE: B LOC: 166 FEET FROM P LINE AT FRERET, *MB: CODE: CDK1 LOC: ON DANTE 166FT FROM FRERET ****/ | 2017-12-25 | EXCAVATED LOCATED AND RAISED A 5/8 METER TO GRADE ALSO RENEWED THE OUTLET LEAD INLET PLASTIC OUTLET. JOB COMPLETE JEG
201701634801 | 2017-11-21 | LEAD | 1829 | LAPEYROUSE |  | WILK | MI - LEAK INSTREET. INLET SERVICE LEAK ON ABANDON SERVICE. SOME TYPE OF HEAVY UTILITY CRUSH SERVICE /** 1) MN: A304620 SN: 0053824, *TAP: SIZE: A LOC: 92 FEET FROM P LINE AT PRIEUR N, *MB: CODE: BDE LOC: ON LAPEYROUSE,92' FROM L.R.P.L. NO. PRIEUR ****/ | 2017-12-13 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON ABANDON INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND
201701636301 | 2017-11-21 | LEAD | 8921 | NELSON | GEN OGDEN | WILK | MI-LEAK IN THE STREET ***********J. GATLIN @ 12:46PM************ INLET SERVICE LEAK IN ASPHAT STREET FLOODING AREA /** 1) MN: A331657 SN: 0078526, *TAP: SIZE: A LOC: 160 FEET FROM P LINE AT GEN OGDEN, *MB: CODE: BDL4 LOC: 160FT FROM PL GEN OGDEN CURB BY GARAGE ON NELSON ****/ | 2017-11-21 | EXCAVATED IN STREET OVER 6" WATER MAIN ON LEAD LINE MADE ALL REPAIR TO STOP LEAK BACKFILL WITH RIVESAND AND COLDMILL REFER TO ZONE 1 TO REMOVE LAEAD
201701638602 | 2017-11-21 | LEAD/PLASTIC | 7737 | PANOLA | BURDETTE | WMRE | ACCT#043271122 METER#A307940 METER BURIED,LOCATE & RAISE /** 1) MN: A307940 SN: 0044771, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT PANOLA, *MB: CODE: ADHL LOC: 130FT FROM /** 1) MN: A307940 SN: 0044771, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT PANOLA, *MB: CODE: ADHL LOC: 130FT FROM SPL PANOLA 2ND TREE ON SIDE ST ****/ | 2017-12-31 | EXCAVATED AND LOCATED AND RAISED A 5/8 METER TO GRADE AND RENEWED THE OUTLET LEAD ON THE INLET PLASTIC ON THE OUTLET. JOB COMPLETE JEG
201701639101 | 2017-11-21 | LEAD | 1820-22 | POLAND AV | N ROMAN | WMTLK | WM METER BOX LEAKING EXAMINE INLET/OUTLET SERVICE FOR A LEAK AREA SATURATED LEAK ON SIDE OF SUNSHINE CAR WASH /** AT 1820: 1) MN: SN: 0085740, *TAP: SIZE: C LOC: 188 FEET FROM P LINE AT ROMAN N, *MB: CODE: DL6 LOC: ON E POLAND-172'FROM P.L. N ROMAN 8FT OUTSIDE PL ****/ | 2017-12-20 | EXCAVATED 4 X 3 SIDEWALK CUT 4 FT DEEP MADE REPAIR ON ABANDON 1 INCH SERVICE LINE TO STOP LEAKBACKFILLED AND CLEANED THE AREA
201701639401 | 2017-11-21 | LEAD | 5756 | WARRINGTON DR | PRENTISS AV | WOLK | PLEASE REPAIR INLET AND OUTLET AND SET 5/8 METER. CUSTOMER IS WAITING ON WATER TO MOVE IN. LOC ID 303200 RENEW OUTLET SERVICE ALSO SET 5/8 METER /** 1) MN: 000000 SN: 0107525, *TAP: SIZE: A LOC: 573 FEET FROM P LINE AT PRENTISS AVE, *MB: CODE: ADL2 LOC: ON WARRINGTON DR., 573' FROM P.L. PRENTISS AVE.,8' ****/ | 2017-11-27 | EXCAVATED A 3 X 3 MUDPLOT CUT TO LOCATE / RAISE METERBOX TO GRADE AND SET A 5/8 WATERMETER. FOUND LEAD ON INLET SERVICE. LEAD LINE NEEDS TO BE REMOVED. JOB CONTINUED JEG
201701641201 | 2017-11-21 | LEAD | 2215 | ST ANN | N GALVEZ | WILK | ML - METER LEAK ACCT#120829-486448 METER#A420790 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A256288 SN: 0175292, *TAP: SIZE: A LOC: 1146 FEET FROM P LINE AT GALVEZ N, *MB: CODE: CFL1 LOC: ON ST. ANN,116' FROM L.S.P.L. NO. GALVEZ ****/ | 2017-12-11 | EXAMINED AND FOUND JOB ALREADY COMPLETED
201701641701 | 2017-11-21 | LEAD | 1718 | ELYSIAN FIELDS AV | N ROMAN | WOLK | MI-LEAK IN THE SIDEWALK AREA IS FLOODED IN FRONT LOC EXAMINE OUTLET SERVICE UP TO PROPERTY LINE, LEAK COMING ACROSS BY CVS /** 1) MN: A262097 SN: 0046773, *TAP: SIZE: A LOC: 144 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: CDL1 LOC: ON ELYSIAN FIELDS 144FT FROM USPL DERBIGNY ****/ | 2017-12-14 | REPLACED 5/8 WASHERS TO STOP LEAK
201701641801 | 2017-11-21 | LEAD | 137 | S RENDON | CLEVELAND AV | WILK | ML: METER LEAK ACCT# 101481-701507 METER# A413717 PLEASE REPAIR ASAP INLET SERVICE LEAK AT METER FLOODING AREA /** 1) MN: SN: 0004048, *TAP: SIZE: B LOC: 175 FEET FROM P LINE AT CLEVELAND AVE, *MB: CODE: CDM4 LOC: ON S RENDON 175FT FROM PL CLEVELAND AVE ****/ | 2017-12-11 | EXCAVATED 4 X 2 MUD PLOT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK 135 S RENDON REPLACED 5/8 INCH WASHERS TO STOP LEAK BACKFILL AND CLEANED THE AREA
201701642301 | 2017-11-21 | LEAD/PLASTIC | 2211 | LAURADALE DR | SHIRLEY DR | WILK | ML METER LEAK METER# A298869 ACCT# 229635-405573 INLET SERVICE LEAK IN SIDEWALK /** 1) MN: A298869 SN: 0131146, *TAP: SIZE: B LOC: 657 FEET FROM P LINE AT COPERNICUS, *MB: CODE: CDM LOC: ON LAURADALE DR., 657' FROM P.L. COPERNICUS, 7' ****/ | 2017-12-08 | EXAMINED METER EXCAVATED INLET OUTLET SERVICE OBSERVED LEAK ON INLET REPAIRED LEAK NO LEAK OBSERVED
201701642501 | 2017-11-21 | LEAD/PLASTIC | 1025 | S CLARK | EUPHROSINE | WILK | MI- LEAK IN SIDEWALK EXAMINE INLET SERVICE FOR LEAK ON SIDEWALK /** 1) MN: A315172 SN: 0092620, *TAP: SIZE: A LOC: 188 FEET FROM P LINE AT PALMETTO, *MB: CODE: ADK2 LOC: 188FT FR PL PALMETTO 7'OUTSD 1' INSDE CURB ****/ DOTTIE READY 5-24-18 EXP 6-13-18 | 2018-05-26 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 CURB COCK BACKFILLED AREA
201701647601 | 2017-11-22 | LEAD | 2227 | ARTS | N MIRO | WMRE | ML- METER LEAK METER#A349510 ACCT#152288-713710 LOCATE, MARK AND RAISE METER TO GRADE /** 1) MN: A317154 SN: 0088024, *TAP: SIZE: A LOC: 221 FEET FROM P LINE AT MIRO N, *MB: CODE: ADMO LOC: ON ARTS, 220.7' FROM P.L. NO. MIRO,8' OUTSIDE P.L. ****/ | 2017-12-22 | LOCATED METER BOX BURIED 1 FT UNDER MUD AND LIMESTONE EXCAVATED 4 X 2 SIDEWALK CUT ALSO 2 X 2 MUD PLOT RELOCATED METER BOX TO SIDEWALK RAISED TO GRADE WITH SIDEWALK ALSO RENEWED OUTLET SERVICE TO PROPERTYBACKFILLED AND CLEANED THE AREA
201701652501 | 2017-11-24 | LEAD/PLASTIC | 1522 | CHIPPEWA | RACE | WILK | MI- LEAK IN SIDEWALK INLET SERVICE LEAK AT CURB /** 1) MN: E005136 SN: 0006248, *TAP: SIZE: E LOC: 116 FEET FROM P LINE AT RACE, *MB: CODE: EIR6 LOC: ON ST. THOMAS, 116' FROM P.L. RACE, 5' OUTSIDE, ****/ | 2017-12-10 | EXAMINED LEAK REMOVED BRICKS FROM AROUND METER BOX EXCAVATED INLET SERVICE REPAIRED LEAK ON BOX COCK BACKFILLED WITH SAND AND REPLACED BRICK
201701654001 | 2017-11-25 | LEAD | 1901 | ELYSIAN FIELDS AV | N PRIEUR | WMRE | MI- CLOSE FOR REPAIRS BROKEN OUTSIDE METER# A396362 ACCT# 189845-483693 REPAIRS WERE MADE INSIDE PROPERTY LINE ***CUSTOMER WANT METER LOCATED AND RAISE TO GRADE*** /** 1) MN: A141110 SN: 0037474, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT ELYSIAN FIELDS AVE, *MB: CODE: BF LOC: ON N PRIEUR 99FT PL ELYSIAN FIELDS AV 2' OUTSIDE ****/ | 2017-12-19 | EXCAVATED IN GUTTER BOTTOM + LOACTED 5/8 INCH METER BOX REPLACED METER BOX CASING +MARKED WITH BLUE PAINT
201701654601 | 2017-11-25 | LEAD/PLASTIC | 331 | FAIRWAY DR | HEDWIGE LN | WILK | MI- LEAK IN CURB INLET SERVICE LEAK IN DRIVEWAY /** 1) MN: A331748 SN: 0102956, *TAP: SIZE: A LOC: 355 FEET FROM P LINE AT ETHEL LANE, *MB: CODE: CFLM LOC: 355FT EXTENDED PL ETHEL LANE 6' OUTSIDE 6' INSIDE ****/ | 2017-12-25 | EXCAVATED A 5 X 3 BRICK CUT IN DRIVEWAY TO REPAIR INLET SERVICE LEAK AND RAISED METER BOX TO GRADE. FOUND PVC ON OUTLET SERVICE & LEAD ON INLET SERVICE. JEG
201701656301 | 2017-11-26 | LEAD | 1311 | ST MAURICE AV | URQUHART | WILK | MI- LEAK IN SIDEWALK INLET SERVICE LEAK INSIDE METER BOX CAUSING POOR PRESSURE 11/27/17 CUSTOMER NOW OUT OF WATER PER INSPC K GRIFFIN, UPGRADE AND GIVE OUT **J.GILLIAM @ 9:28AM** /** 1) MN: A263317 SN: 0170779, *TAP: SIZE: A LOC: 79 FEET FROM P LINE AT URQUHART, *MB: CODE: CD2 LOC: ON ST MAURICE,78FT FROM LSPL URGUHART ****/ | 2017-11-27 | REPLACED 5/8 INCH WASHERS TO STOP LEAK
201701657901 | 2017-11-27 | LEAD | 5901 | MARAIS | ALABO | WILK | ML-- METER LEAK METER # A271679 ACCT # 139085-VACANT INET SERVICE LEAK BEHIND BOX /** 1) MN: A271679 SN: 0094569, *TAP: SIZE: A LOC: 5 FEET FROM P LINE AT MARAIS, *MB: CODE: AE LOC: ON ALABO ST 9' FROM PL MARAIS ****/ | 2017-12-27 | EXCAVATED 3 X 3 SIDEWALK CUT MADE REPAIR ON INLET SERVICE LINE TO STOP LEAK BACKFILL AND CLEANED THE AREA
201701658201 | 2017-11-27 | LEAD/PLASTIC | 1708 | FLANDERS | GEN MEYER AV | WILK | ML- METER LEAK ACCT # 236136-407989 METER# A243327 INLET SERVICE LEAK IN BOX /** 1) MN: A243327 SN: 0165262, *TAP: SIZE: A LOC: 17 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: __ LOC: ON FLANDERS, 17' FROM D.P.L. GEN. MEYER AVE., 9'OU ****/ | 2017-12-07 | EXAMINED LEAK EXCAVATED METER BOX OBSERVED LEAK ON INLET REPAIRED LEAK
201701658901 | 2017-11-27 | LEAD/PLASTIC | 2454 | PRANCER |  | WILK | MI- LEAK BETWEEN S/WALK & STREET. INLET SERVICE LEAK /** 1) MN: A125841 SN: 0136036, *TAP: SIZE: B LOC: 188 FEET FROM P LINE AT FIESTA DR, *MB: CODE: B LOC: ON PRANCER 187' FROM PL FIESTA 7' OUTSIDE PL 4' IN ****/ | 2017-12-08 | EXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOB SITE
201701659001 | 2017-11-27 | LEAD/PLASTIC | 2611 | PRANCER | VIXEN | WILK | MI- LEAK IN THE STREET EXAMINE INLET SERVICE FOR LEAK IN STREET FLOODING INFRONT OF ADDRESS 02/23/18 CUST STATES LEAK HAS GOTTEN WORSE AND AFFECTING FOUNDATION OF HER HOME (NLD) 03/23/18 LEAK FLOODING AREA PER SR#12836199 (AJR) /** 1) MN: A227081 SN: 0133483, *TAP: SIZE: B LOC: 647 FEET FROM P LINE AT VIXEN, *MB: CODE: B LOC: 649FT FROM P.L. VIXEN ****/ | 2018-04-11 | CUT OUT JOB WITH AIR GUN START EXCAVATING BY HAND STARTED USING MACHINE TO DIG UP TREE ROOTS FOUND LEAK ON OUTLET SERVICE ALSO FOUND LEAD ON OUTLET REPLACED LEAD LINE WITH PLASTIC NEED PICK UP DRESS UP AND BACKFILL
201701659201 | 2017-11-27 | LEAD/PLASTIC | 8921 | DIXON | GEN OGDEN | WILK | ML-METER LEAK ACCT#156615-553659 METER#A431867 CHANGED FROM 8927 DIXON INLET SERVICE LEAK IN BOX /** 1) MN: A249338 SN: 0093833, *TAP: SIZE: B LOC: 170 FEET FROM P LINE AT GEN OGDEN, *MB: CODE: CDL1 LOC: 170FT FROM PL GEN OGDEN ON DIXON ****/ | 2017-11-27 | EXAMINED AND FOUND LEAK ON INLET. EXCAVATED MUD PLOT BY HAND, MADE ALL REPAIRS AND BACKFILLED WITH SAND. CREW FOUND METER A379315 AT ABOVE LOCATION LJF
201701659501 | 2017-11-27 | LEAD | 6004 | BURGUNDY |  | WILK | INLET SERVICE NEED TO BE REPAIRED NO WATER COMING FORM THE MAIN CUSTOMER IS WAITING ON WATER LOCATION #303462 INSPECTOR SET A-426975 DRY INLET SERVICE, CONTRACTORS WAITING ON WATER HOUSE UNDER RENOVATION /** 1) MN: SN: 0079844, *TAP: SIZE: B LOC: 37 FEET FROM P LINE AT GORDON, *MB: CODE: CD LOC: ON BURGUNDY 37FT FROM PL GORDON ****/ | 2017-12-06 | EXAMINED AND FOUND NO WATER ON WATER ON INLET RENEW INLET SERVICE FROM CONTROLLING LINE TO METER BOX WAS UNABLE TO PROPERTY OWNER GRASS WATER ON INLET NOW LEFT OFF IN METER BOX BACKFILL JOB WITH RIVERSAND
201701660701 | 2017-11-27 | LEAD/PLASTIC | 109 | LARCHMONT PL | GEN MEYER AV | WILK | ML - METER LEAK ACCOUNT NUMBER - 226817-419594 METER NUMBER - A338209 INLET SERVICE LEAK INSIDE BOX /** 1) MN: A289478 SN: 0118983, *TAP: SIZE: A LOC: 122 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: BD LOC: ON LARCHMONT 122FT FROM GEN MEYER 10FT OUTSIDE ****/ | 2017-12-14 | EXCAVATED METER BOX AND FOUND LEAK ON OUTLET REMOVED LEAD FROM OUTLET AND REPLACED WITH PLASTIC TO PROPERTY DUG BY HAND AND CHOPPED THROUGH TREE ROOTS BACKFILLED WITH RIVER SAND
201701661001 | 2017-11-27 | LEAD | 430 | N GALVEZ | ST LOUIS | WMTLK | MI LEAK IN THE STREET EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A315573 SN: 0051592, *TAP: SIZE: A LOC: 33 FEET FROM P LINE AT ST LOUIS, *MB: CODE: ADK LOC: ON NO. GALVEZ,32' FROM U.R.P.L. ST. LOUIS ****/ | 2017-12-15 | EXCAVATED 3 X 3 GUTTER BOTTOM REPLACED 5/8 INCH METER BOX TO STOP LEAK BACKFILL AND CLEANTHE AREA
201701663101 | 2017-11-27 | LEAD | 3214 | PAUGER |  | WILK | MI-LEAK AT THE SIDEWALK INLET LEAK ON THE SIDEWALK. FLOODING THE SIDEWALK & CURB /** 1) MN: A310696 SN: 0072787, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CK LOC: ON PAUGER, 111' FROM P.L. NO. DORGENOIS ****/ | 2017-12-21 | EXCAVATED 3 X 2 SIDEWALK CUT ALSO AN ADDITIONAL 3 X 3 GUTTER BOTTOM MUD PLOT MOVED METER BOX FROM GUTTER TO SIDEWALK ALSO RENEWED TO PROPERTY BACKFILLED AND CLEANED THE AREA
201701663201 | 2017-11-27 | LEAD | 410 | WARRINGTON DR | MANDOLIN | WILK | WM-LEAK IN SIDEWALK INLET LEAK ON THE SIDEWALK. FLOODING. /** 1) MN: A134171 SN: 0107704, *TAP: SIZE: A LOC: 225 FEET FROM P LINE AT MANDOLIN, *MB: CODE: CDL5 LOC: 225FT FROM PL MANDOLIN MTR ON WARRINGTON 8FT OUTSD ****/ | 2017-12-20 | EXCAVATED IN MUDPLOT ON INLET LEAK MADE ALL REPAIRS TO STOP LEAK ON LEAD BACKFILL LJF
201701664501 | 2017-11-27 | LEAD | 7602 | SYCAMORE | LOWERLINE | WILK | ML METER LEAK METER# A256012 ACCT# 131016-580448 INLET SERVICE LEAK /** 1) MN: A256012 SN: 0061209, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT SYCAMORE, *MB: CODE: ADH3 LOC: ON LOWERLINE,62' FROM P.L. SYCAMORE ****/ | 2017-12-19 | EXCAVATED IN MUDPLOT ON OUTLET LEAK MADE ALL REPAIR TO STOP LEAK BACKFILL WITH RIVER SAND LJF
201701665801 | 2017-11-28 | LEAD | 4736 | CORONADO DR | PRESSBURG | WILK | MI- LEAK IN SIDEWALK INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A325180 SN: 0129429, *TAP: SIZE: B LOC: 5 FEET FROM P LINE AT HYDT #4, *MB: CODE: BDM1 LOC: ON CORONADO DR 5' FROM PL HYDT #4 8'OUTSIDE PL 2' ****/ | 2017-12-16 | EXCAVATED IN MUDPLOT. REPAIR 5/8 STOP & WASTE LEAD LINE. DRESS UP WITH RIVER SAND. JOB REF TO ZONE 5 TO TAKE LEAD LINE OUT THE GROUND LJF
201701666901 | 2017-11-28 | LEAD/PLASTIC | 1339 | NUNEZ |  | WOLK | ML-- METER LEAK METER # A352552 ACCT# 232502-401668 OUTLET SERVICE LEAK CON REG /** 1) MN: A278006 SN: 0051857, *TAP: SIZE: A LOC: 23 FEET FROM P LINE AT SOCRATES, *MB: CODE: CF LOC: ON NUNEZ 25FT FROM SOCRATES 4FT OUTSIDE ****/ | 2017-12-04 | EXCAVATED METER AND FOUND LEAK ON PROPERTY SIDE REPLACED LINE FROM PROPERTY TO METER BOX TO REPAIR LEAK BACKFILLED WITH RIVER SAND
201701668801 | 2017-11-28 | LEAD/PLASTIC | 5830 | ALBANY CT | ABBEY DR | WILK | ML METER LEAK METER # A137942 ACCOUNT # 231600-418052 INLET SERVICE LEAK IN BOX /** 1) MN: A137942 SN: 0142552, *TAP: SIZE: B LOC: 30 FEET FROM P LINE AT CHELSEA DR, *MB: CODE: AD5 LOC: ON ALBANY CT 30' FROM DPL CHELSEA DR 1' INSIDE CUR ****/ | 2017-12-07 | EXCAVATED ON METERBOX FOR LEAK FOUND LEAK ON INLET INSIDE BOX MADE REPAIR BACKFILLED AND CLEANED JOB SITE
201701671301 | 2017-11-28 | LEAD/PLASTIC | 8326-28 | FORSHEY | CAMBRONNE | WMTLK | ML- METER LEAK METER# A393237 ACCT# 141833-593926 EXAMINE INLET & OUTLET SERVICE METER UNDER WATER GRASSY AREA FLOODED /** AT 8326: 1) MN: A338912 SN: 0073260, *TAP: SIZE: B LOC: 240 FEET FROM P LINE AT DANTE, *MB: CODE: CDN3 LOC: ON FORSHEY 239' FROM PL OF DANTE ** AT 8328: 2) MN: A345684 SN: 0073260, *TAP: SIZE: B LOC: 63 FEET FROM P LINE AT CAMBRONNE, *MB: CODE: CDN3 LOC: 62FT FROM PL CAMBRONNE 8FT OUTSIDE PL ON FORSHEY ****/ | 2017-11-29 | EXAMINED AND FOUND LEAK ON OUTLET EXCAVATED 4 X 4 HOLE IN MUDPLOT MADE ALL REPAIRS AND BACKFILLED WITH RIVER SAND. LJF
201701674301 | 2017-11-28 | LEAD/PLASTIC | 1724 | BROADWAY |  | WILK | MI- LEAK BETWEEN THE STREET AND THE SIDEWALK INLET SERVICE LEAK /** 1) MN: C025745 SN: 0069258, *TAP: SIZE: C LOC: 204 FEET FROM P LINE AT GREEN, *MB: CODE: CDL LOC: ON BROADWAY 205.5FT FROM GREEN ****/ | 2018-05-03 | EXCAVATED IN TREE ROOTS AND MADE REPAIRS ON A 1" INLET SERVICE LEAK LEAD LINE PLASTIC ON THE OUTLET
201701674601 | 2017-11-28 | LEAD | 2123 | PINE |  | WILK | INLET SERVICE LEAK /** 1) MN: A242032 SN: 0066908, *TAP: SIZE: A LOC: 218 FEET FROM P LINE AT PANOLA, *MB: CODE: CDMN LOC: 219' P.L. PANOLA ****/ | 2017-11-28 | EXAMINED AND FOUND LEAK ON CURB COCK. EXCAVATED BY HAND, FOUND BOTTOM BROKEN ALSO MADE REPAIRS (METER BOX COMPLETE) BACKFILLED WITH RIVER SAND. LJF
201701675101 | 2017-11-28 | LEAD | 2933 | SERANTINE | N GAYOSO | WILK | MI- LEAK AT THE SIDEWALK CUST STATES AREA IS LEAKING AGAIN INLET SERVICE LEAK ON SIDEWALK, FLOODING SIDEWALK /** 1) MN: A300793 SN: 0073658, *TAP: SIZE: B LOC: 257 FEET FROM P LINE AT GAYOSO N, *MB: CODE: CEL LOC: ON SERANTINE, 257' FROM P.L. NO. GAYOSO ****/ | 2017-12-07 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201701675401 | 2017-11-28 | LEAD | 4819 | N ROCHEBLAVE | JOURDAN AV | WILK | MI: LEAK BTW STREET AND SIDEWALK LOCATION # 177831 NO METER AT LOCATION INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A319546 SN: 0130370, *TAP: SIZE: B LOC: 152 FEET FROM P LINE AT JOURDAN AVE, *MB: CODE: ADL LOC: RES ON N.ROCHEBLAVE 152FT P.L. JOURDAN AV 6' OUT- ****/ | 2017-12-27 | EXCVATED 3 X 3 MUD PLOT REPLACED 5/8 INCH METER BOX COCK AND METER BOX CASING BACKFILLED AND CLEANED THE AREA,,,UNABLE TO GET READING
201701675701 | 2017-11-28 | LEAD/PLASTIC | 2307 | GEN MEYER AV | FARRAGUT | WMTLK | ML- METER LEAK METER# A401111 ACCT # 238547-703887 ******LEAVE IN SYSTEM****** EXAMINE INLET/OUTLET SERVICE AT CURB FOR A LEAK CURB FLOODED LEFT ONE (1) CONE FOR PROTECTION /** 1) MN: A343537 SN: 0177048, *TAP: SIZE: A LOC: 61 FEET FROM P LINE AT FARAGUT, *MB: CODE: CD LOC: ON GEN MEYER 29FT FROM FARRAGUT 7FT OUTSIDE ****/ | 2017-12-13 | EXAMINED METER BOX FOR LEAK EXCAVATED METER EXPOSED INLET AND OUTLET LINE OBSERVED LEAK ON INLET REPAIRED LEAK BACKFILLED
201701676301 | 2017-11-29 | LEAD | 2903 | ST CLAUDE AV | PRESS DR | WMRE | LOCATION ID# 127873 MTR# A364769 PLEASE LOCATE AND RAISE TO GRADE /** 1) MN: A148478 SN: 0054427, *TAP: SIZE: A LOC: 52 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: CDL1 LOC: SIDE ST 7FT FROM CORNER OF GARAGE FENCE ON PRESS ****/ | 2017-12-18 | EXCAVATED 4 X 2 TRENCH THROUGH LIMESTONE BRICK AND SHALLS RAISED METER BOX TO GRADE BACKFILLED AND CLEANED THE AREA,,,,,UNABLE TO READ
201701676401 | 2017-11-29 | LEAD | 3001 | LAW | MONTEGUT | WMRE | LOCATION ID# 211381 MTR# A413043 PLEASE LOCATE AND RAISE TO GRADE /** 1) MN: A275042 SN: 0172066, *TAP: SIZE: B LOC: 8 FEET FROM P LINE AT MONTEGUT, *MB: CODE: CD LOC: ON LAW 8' FROM P.L. MONTEGUT 9' OUTSIDE PL 3' INSI ****/ | 2017-12-18 | EXCAVATED 4 X 4 SIDEWALK RELOCATED METER FROM THE GUTTER TO MUD PLOT BESIDE FENCE METER BOX IS UP TO GRADE BACKFILL AND CLEAN ED THE AREA
201701678901 | 2017-11-29 | LEAD/PLASTIC | 933 | EUTERPE | CONSTANCE | WILK | ML-METER BOX LEAKING INLET SERVICE LEAK IN METER BOX. CURB COCK IN OFF POSITION WATER PASSING THROUGH, FLOODING SIDEWALK & GUTTER BOTTOM, ***HOUSE UNDER RENOVATIONS*** /** 1) MN: A251530 SN: 0050701, *TAP: SIZE: A LOC: 138 FEET FROM P LINE AT CONSTANCE, *MB: CODE: CEL1 LOC: 134FT FROM LRPL CONSTANCE ****/ | 2017-12-07 | EXAMINED FOR LEAK EXCAVATED METER BOX OBSERVED LEAK ON INLET REPAIED LEAK BACKFILLED NO METER PRESENT IN METER BOX
201701681901 | 2017-11-29 | LEAD | 2643 | DELERY | FLORIDA BL | WILK | WM LEAK BETWEEN STREET & SIDEWALK CHANGED FROM 2601 DELERY INLET ON ABANDON SERVICE ON VACANT LOT FLOODING AREA GETTING OFF N DCB /** 1) MN: A270077 SN: 0092929, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT FLORIDA AVE, *MB: CODE: __ LOC: ON DELERY 39' FROM PL FLORIDA 7' OUTSIDE PL 3' INS ****/ | 2017-12-14 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON ABANDON INLET SERCIVE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201701682301 | 2017-11-29 | LEAD/PLASTIC | 6469 | LOUIS XIV |  | WOLK | UNABLE TO CHANGE METER. CONCRETE AND WHEEL BEHIND CASING. PLEASE REPAIR AND CHANGE METER A139362 LOC ID 184359 CEMENT COVERING HANDWHEEL, ALSO CHANGE METER /** 1) MN: A139362 SN: 0137035, *TAP: SIZE: C LOC: 76 FEET FROM P LINE AT LANE, *MB: CODE: OOO LOC: ON LOUIS FOURTEENTH, 76' FROM P.L. LANE, 8' OUT- ****/ | 2018-05-27 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 CURB COCK REPLACED OUTLET TO PROPERTY AND SET 5/8 METER BACKFILLED AREA MADE 4X4 SIDEWALK CUT ***********OLD METER INFO************* METER:A419264 FAC:15485510 MAKE:HERSEY READ:105
201701682502 | 2017-12-22 | LEAD | 1870 | N ROMAN | PAUGER | WILK | EXAMINED JOB FOUND LEAK COMING FROM THE STREET REFER BACK TO ZONE 4 /** 1) MN: A345903 SN: 0140883, *TAP: SIZE: B LOC: 128 FEET FROM P LINE AT PAUGER, *MB: CODE: CDL LOC: ON NO. ROMAN, 127.5' FROM P.L. PAUGER,8' OUTSIDE ****/ | 2017-12-27 | EXCAVATED IN ASPHALT STREET + MADE TWO REPAIRS IN CUT REPLACED 3/4 INCH BEND ADAPTER ON ABANDONED SERVICE ACROSS FROM ABOVE LOCATED + CAULKED JOINT ON WATER MAIN IN SAMD CUT COMPACTED BACKFILLED + DRESSED UP AREA
201701682801 | 2017-11-29 | LEAD/PLASTIC | 701 | FELICITY | ST THOMAS | WILK | WM LEAK IN THE STREET **********S SLACK 14:03********** INLET SERVICE LEAK IN AN ASPHALT STREET WATER COMING UP OUT HOLE IN THE STREET AREA FLOODED, LEAK ON ST THOMAS/FELICITY. LEFT 1 COR FOR SAFETY /** 1) MN: A335201 SN: 0011908, *TAP: SIZE: B LOC: 35 FEET FROM P LINE AT ST THOMAS, *MB: CODE: BEK4 LOC: FRONT 35' P.L. ST THOMAS ****/ | 2017-11-29 | BROKE THE STREET AND EXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOB SITE
201701684401 | 2017-11-29 | LEAD/PLASTIC | 4225 | HAMBURG |  | WILK | LOCATION ID-302444 MTR-A430827 MTR ON/STOP & WASTE OPEN/CUST NOT GETTING WATER **************L FREEMAN************ DRY INLET CUSTOMER OUT OF WATER /** 1) MN: A154695 SN: 0107465, *TAP: SIZE: A LOC: 143 FEET FROM P LINE AT PELOPIDAS, *MB: CODE: BKO LOC: 143FT FROM PL PELOPIDAS MTR ON HAMBURG 7FT OUTSD ****/ | 2017-11-29 | EXAMINED AND FOUND DRY INLET. EXCAVATEDMUDPLOT WITH BACKHOE, FOUND ABANDONED INLET. RAN LINE TO CURB COCK, SET METER AND BACKFILLED WITH SAND. CREW FOUND METER A430827 AT ABOVE LOCATION LJF
201701685301 | 2017-11-29 | LEAD | 2401 | CANAL | N TONTI | WMTLK | LOCATION ID-223027 MTR-C033809 BAD MTR LEAK/AREA FLOODED EXAMINE INLET/OUTLET SERVICE FOR LEAK AREA SATURATED /** 1) MN: 000000 SN: 0015175, *TAP: SIZE: A LOC: 0 FEET FROM P LINE AT , *MB: CODE: AFH2 LOC: INS WLK SIDE ST DR ****/ | 2017-12-15 | EXCAVATED 2 X 2 MUD PLOT REPLACED METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA ALSO REPLACED MISSING METER BOX CASING ON THE METER NEXT TO IT
201701688101 | 2017-11-30 | LEAD/PLASTIC | 116 | ROSELYN PARK PL |  | WILK | MI LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET FLOODING AREA 04/12/18 LEAK HAS GOTTEN WORSE PER INSP B BOURNES UPGRADED TO 1ST AM SENT TO ZONE 6 PRINTER LEFT ONE (1) CONE (FCP) 04/30/18 LEAK HAS GOTTEN WORSE NOW CAUSING A LARGE SINK HOLE TO FORM PER SR#12839627 (AJR) /** 1) MN: B029346 SN: 0116341, *TAP: SIZE: B LOC: 173 FEET FROM P LINE AT PATTERSON DR, *MB: CODE: CDN2 LOC: ON ROSELYN PARK PL., 173' FROM P.L. PATTERSON DR., ****/ | 2018-05-18 | BROKE THE STREET EXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND UP JOB SITE
201701688201 | 2017-11-30 | LEAD | 3022 | CLEVELAND AV |  | WMTLK | ML METER LEAK ACCOUNT #104343531115 METER #A291000 EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN BOX /** 1) MN: A292384 SN: 0015826, *TAP: SIZE: A LOC: 114 FEET FROM P LINE AT GAYOSO S PL, *MB: CODE: CDL LOC: 114' FROM USPL GAYOSO S PL ****/ | 2017-12-21 | REPLACED 5/8 INCH WASHERS IN METER BOX
201701688601 | 2017-11-30 | LEAD | 3158 | TOULOUSE | N RENDON | WMTLK | ML- METER LEAK ACCT# 149250-711845 MTR# A423951 EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A260808 SN: 0074385, *TAP: SIZE: B LOC: 172 FEET FROM P LINE AT LOPEZ N, *MB: CODE: CDLN LOC: ON TOULOUSE ST 172' FROM PL N LOPEZ ****/ | 2017-12-21 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201701688901 | 2017-11-30 | LEAD | 2456 | N ROBERTSON | MUSIC | WOLK | ML METERLEAK MTR#A346908 ACCT#102151-482084 CONS REG ON METER /** 1) MN: SN: 0004858, *TAP: SIZE: B LOC: 139 FEET FROM P LINE AT MUSIC LSPL, *MB: CODE: CEM1 LOC: 139' FROM LSPL MUSIC ****/ | 2017-12-27 | EXAMINED BOTH METER AT ABOVE LOCATION + FOUND NO LEAK + NO CONSTRANT REGISTRATION
201701689101 | 2017-11-30 | LEAD/PLASTIC | 5914 | HURST | STATE | WILK | ML METERLEAK MTR#A263516 ACCT#105863-563990 LEAK AT THE CURBCOCK INSIDE METERBOX /** 1) MN: A263516 SN: 0007873, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT STATE, *MB: CODE: BE26 LOC: ON HURST 45' FROM LRP STATE ** 2) MN: A135972 SN: 0007849, *TAP: SIZE: A LOC: 92 FEET FROM P LINE AT ELEONORE, *MB: CODE: BE26 LOC: ON HURST, 91.7' FROM P.L. ELEONORE, 6' INSIDE THERE IS 1 MORE NOT LISTED. ****/ DOTTIE READY 5-14-18 EXP 6-3-18 | 2018-05-26 | REPLACED 5/8 CURB COCK TIED INTO LEAD UNABLE TO REMOVE LEAD DUE CAR PARKED OVER WATER MAIN
201701694501 | 2017-12-01 | LEAD | 1045 | JOURDAN AV |  | WILK | ML METER LEAK ACCOUNT #155614424546 METER #A310251 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A242459 SN: 0092455, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: CDM7 LOC: ON JOURDAN AVE.,93.5' FROM P.L. ST. CLAUDE AVE., ****/ | 2018-01-04 | EXCAVATED 3 X 2 GUTTER BOTTOM ALSO 4 X 2 MUD PLOT AT PROPERTY RENEWED OUTLET SERVICE LINE TO PROPERTY AND REPLACED 5/8 INCH METER BOX COCK ALSO RAISED METER BOX TO GRADE BACKFILLED AND CLEANED THE AREA
201701694901 | 2017-12-01 | LEAD/PLASTIC | 2765 | HUDSON PL | RAMSEY DR | WILK | ML- METER LEAK ACCT#230918-417697 METER# C033165 INLET SERVICE LEAK IN BOX /** 1) MN: C007300 SN: 0139337, *TAP: SIZE: __ LOC: 0 FEET FROM P LINE AT HUDSON PL, *MB: CODE: AL LOC: ON HUDSON PL., 23' FROM D.P.L. RAMSEY DR., 2' IN- ****/ | 2017-12-15 | EXAMINED LEAK EXCAVATED THROUGH ROOTS EXPOSED COPPER ON INLET AND OUTLET REPAIRED LEAK
201701696601 | 2017-12-01 | LEAD | 2221 | N PRIEUR | ELYSIAN FIELDS AV | WMTLK | ML- METER LEAK METER# A317062 ACCT# 208398-486900 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: A327402 SN: 0089183, *TAP: SIZE: A LOC: 16 FEET FROM P LINE AT DPL ELYSIAN FIELDS AVE, *MB: CODE: OOO LOC: ON N PRIEUR 4' FROM DPL ELYSIAN FIELDS AVE 9' OUTS ****/ | 2017-12-27 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201701696801 | 2017-12-01 | LEAD | 3829 | LAUREL | GEN TAYLOR | WILK | WM- LEAK ON THE SIDEWALK ****** ON THE SIDE OF THE HOME**** INLET SERVICE LEAK BAD BLEEDER VALVE, FLOODING SIDEWALK 04/23/18 LEAK HAS GOTTEN WORSE PER SR#12838936 (AJR) 05/04/18 CUST STATED LEAK FETTING WORSE DAMAGING PROPERTY (KSW) /** 1) MN: A158672 SN: 0030815, *TAP: SIZE: __ LOC: 80 FEET FROM P LINE AT LAUREL, *MB: CODE: AFHK LOC: ON GEN TAYLOR 79FT FROM PL OF LAUREL ****/ DOTTIE READY 6-6-18 EXP 6-26-18 | 2018-06-08 | REPLACED 5/8 METER BOX COCK TIED BACK INTO LEAD . OUTLET PLASTIC ALREADY
201701697901 | 2017-12-01 | LEAD | 5437 | ROYAL |  | WILK | METER A 426873 IS LEAKING FROM CURB COCK. PLEASE REPAIR. LOC ID 303526 BAD BLEEDER VALVE /** 1) MN: SN: 0068176, *TAP: SIZE: B LOC: 190 FEET FROM P LINE AT ANDRY, *MB: CODE: BD LOC: ON ROYAL 190FT FROM PL OF ANDRY ****/ | 2018-01-04 | FOUND METER BOX 3 CASING DEEP EXCAVATED3 X 3 GUTTER BOTTOM ALSO 3 X2 MUD PLOT RAISED METER BOX TO GRADE RENEWED OUTLET SERVICE TO PROPERTY BACKFILLED AND CLEANED THE AREA
201701698301 | 2017-12-01 | LEAD | 1023 | LOUISA DR | N RAMPART | WILK | WM- LEAK AT THE CURB INLET SERVICE LEAK AT CURB /** 1) MN: A295304 SN: 0045812, *TAP: SIZE: A LOC: 170 FEET FROM P LINE AT RAMPART N, *MB: CODE: __ LOC: 167' P.L. N RAMPART ****/ | 2017-12-22 | EXCAVATED 4X 10 CUT CONCRETE DRIVEWAY FOUND LEAK ON 5/8 INLET SERVICE MADE REPAIRS ON INLET FROM CURB TO METER BOX UNABLE TO GO TO WATER MAIN CAUSE CARS PARKED ON JOB BACKFILL JOB WITH RIVERSAND AND COLD MILL
201701700001 | 2017-12-02 | LEAD | 2934 | BANKS | S GAYOSO | WILK | ML- METER LEAK METER# A386849 ACCT# 161984-531576 ***** ON THE SIDE OF THE PROPERTY ***** INLET SERVICE LEAK IN BOX /** 1) MN: A257681 SN: 0100824, *TAP: SIZE: A LOC: 30 FEET FROM P LINE AT BANKS, *MB: CODE: CDHL LOC: ON GAYOSO 30' FROM PL BANKS 7' OUTSIDE PL 2' INSID ****/ | 2018-01-03 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND
201701700301 | 2017-12-02 | LEAD | 1803 | URSULINES AV | DERBY PL | WILK | PP- POOR PRESSURE METER# A351025 ACCT# 101202-525078 INLET SERVICE LEAK IN BOX CAUSING POOR PRESSURE /** 1) MN: A225315 SN: 0017222, *TAP: SIZE: A LOC: 42 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: AFLK LOC: ON URSULINES AVE.,42' FROM S.P.L. NO. DERBIGNY ****/ | 2017-12-21 | EXCAVATED 4 X 3 SIDEWALK CUT MADE REPAIR ON INELT SERVICE AND RENEWED OUTLET SERVICE TO PROPERTY BACKFILL AND CLEANED THE AREA
201701707702 | 2017-12-03 | LEAD/PLASTIC | 201 | POLK | CATINA | WMRE | LOCATE AND RAISE TO GRADE NEED MACHINE /** 1) MN: A187799 SN: 0175672, *TAP: SIZE: B LOC: 27 FEET FROM P LINE AT CATINA, *MB: CODE: CDL LOC: ON POLK AVE 27' FROM PL OF CATINA ****/ | 2018-08-18 | EXCAVATED LOCATED AND RAISED A 5/8 METER TO GRADE AND MARK THE METER PLASTIC INLET LEAD OUTLET CUSTOMER DID NOT WANT TO EXCAVATE ANY MORE ON LAWN. JOB COMPLETE
201701708302 | 2017-12-03 | LEAD/PLASTIC | 8618 | PLUM | LEONIDAS | WOLK | METER BURIED,LOCATE & RAISE /** 1) MN: A299850 SN: 0049969, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT LEONIDAS, *MB: CODE: CDLM LOC: 131FT FROM UPL LEONIDAS METER ON PLUM ****/ /** 1) MN: A299850 SN: 0049969, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT LEONIDAS, *MB: CODE: CDLM LOC: 131FT FROM UPL LEONIDAS METER ON PLUM ****/ | 2017-12-29 | EXCAVATED LOCATED AND RAISED A 5/8 METER TO GRADE. ALSO RENEWED THE OUTLET PLASTIC ON THE OUTLET. LEAD ON THE INLET JOB COMPLETE. JEG
201701710601 | 2017-12-03 | LEAD | 717 | ORLEANS AV | BOURBON | WOLK | ACCT# 186457-528273 METER# G002086 CONSTANT REGISTRATION ON METER. PLEASE REPAIR. /** 1) MN: C023486 SN: 0000000, *TAP: SIZE: G LOC: 131 FEET FROM P LINE AT BOURBON, *MB: CODE: ARP LOC: ON ORLEANS AV 139' PL BOURBON METER IN STREET ** 2) MN: G001384 SN: 0005260, *TAP: SIZE: Y LOC: 104 FEET FROM P LINE AT BOURBON, *MB: CODE: OOOO LOC: IN MH ON ST. ANN 134FT PL BOURBON ON SIDEWALK THERE ARE 2 MORE NOT LISTED. ****/ | 2017-12-28 | REFER JOB TO METER SHOP
201701718601 | 2017-12-04 | LEAD | 2921 | ST PETER | N DUPRE | WILK | ML- METER LEAK ACCT# 134535-714708 METER# A426419 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A208923 SN: 0071677, *TAP: SIZE: A LOC: 171 FEET FROM P LINE AT DUPRE N, *MB: CODE: CD LOC: ON ST.PETER, 171' FROM P.L. NO. DUPRE ****/ | 2017-12-22 | ARRIVED AT ABOVE LOCATED FOUND INLET ON METER EXCAVATED 5 X 2 GUTTER THROUGH LIMESTONE AND MUD ALSO 4 X 3 SIDEWALK CUT REPAIR INLET SERVICE LINE LEAK AND REPLACED BROKEN METER BOTTON RELOCATED METER FROM GUTTER BOTTOM TO SIDEWALK UP TO GRADE OUTLET SERVICE LINE RENEWED TO PROPERTY BACKFILL AND CLEANED THE AREA
201701718701 | 2017-12-04 | LEAD | 2313 | LAHARPE | TONTI | WILK | ML - METER LEAK MTR # A395600 ACCT # 186119 -488962 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A299685 SN: 0015632, *TAP: SIZE: A LOC: 120 FEET FROM P LINE AT TONTI N, *MB: CODE: AFK LOC: 122FT FROM PL N TONTI 3' OUTSIDE PL 8' INSIDE CURB ** 2) MN: A263657 SN: 0015632, *TAP: SIZE: A LOC: 99 FEET FROM P LINE AT TONTI N, *MB: CODE: BD LOC: INSIDE BY RIVER SIDE OF STEPS 100' P.L. N TONTI ****/ | 2017-12-19 | REPLACED 5/8 INCH WASHERS TO STOP LEAK
201701723502 | 2017-12-04 | LEAD | 113 | WINTHROP PL | DESAIX BL | WMRE | ACCT#099894034 METER#A365596 METER BURIED,LOCATE & RAISE /** 1) MN: A275263 SN: 0095913, *TAP: SIZE: B LOC: 152 FEET FROM P LINE AT DE SAIX BLVD, *MB: CODE: ADM2 LOC: ON /** 1) MN: A275263 SN: 0095913, *TAP: SIZE: B LOC: 152 FEET FROM P LINE AT DE SAIX BLVD, *MB: CODE: ADM2 LOC: ON WINTRHOP PL 153' FROM PL DE SAIX BLVD 6.5' OUTS ****/ | 2018-05-30 | EXCAVATED IN MUDPLOT. REPAIR 5/8 STOP & WASTE LEAD LINE. DRESS UP WITH RIVERSAND JOB REFER TO ZONE 1 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201701723801 | 2017-12-04 | LEAD | 3303 | TULANE AV |  | WILK | MI LEAK ON SIDEALK IN BACK OF BUILDING ,ON DE'HEMCOURT STREET INLET SERVICE LEAK /** 1) MN: A344988 SN: 0111155, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT RENDON S, *MB: CODE: CD LOC: 63'FRM PL S RENDON 7'OUTSD PL 3'INSD.CURB. ** 2) MN: D006712 SN: 0111155, *TAP: SIZE: D LOC: 58 FEET FROM P LINE AT RENDON S, *MB: CODE: CDL2 LOC: IN MH ON DHEMECOURT 50FT PL S RENDON 5' OUTSIDE ****/ | 2017-12-21 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201701724402 | 2017-12-04 | LEAD/PLASTIC | 38 | WREN |  | WMRE | METER BURIED,LOCATE & RAISE /** 1) MN: A333384 SN: 0110826, *TAP: SIZE: A LOC: 420 FEET FROM P LINE AT MARCONI DR, *MB: CODE: AFK LOC: ON WREN 421FT FROM PL MARCONI DR 5' OUTSIDE PL 10' ****/ /** 1) MN: D005792 SN: 0104289, *TAP: SIZE: D LOC: 550 FEET FROM P LINE AT MARCONI DR, *MB: CODE: BFK LOC: ON WREN, 550' FROM P.L. MARCONI DR., 5' OUTSIDE ****/ | 2018-05-20 | EXCAVATED & RAISED 5/8 METER BOTTOM TO BRADE ALSO RENEWED 5/8 OUTLET FROM METERBOX TO PROPERTY. FOUND LEAD ON INLET REFER BACK TO ZONE TO REMOVE LEAD ON INLET.
201701724702 | 2017-12-04 | LEAD/PLASTIC | 981 | WALKER | GEN HAIG | WMRE | ACCT#125986047 METER#B036493 METER BELOW GRADE,RAISE /** 1) MN: B018966 SN: 0117843, *TAP: SIZE: B LOC: 15 FEET FROM P LINE AT WALKER, *MB: CODE: BDH5 LOC: ON GEN HAIG /** 1) MN: B018966 SN: 0117843, *TAP: SIZE: B LOC: 15 FEET FROM P LINE AT WALKER, *MB: CODE: BDH5 LOC: ON GEN HAIG 15FT FROM PL WALKER 9' OUTSIDE PL ****/ | 2018-05-19 | EXCAVATED IN MUD PLOT IN TREE ROOTS 3/4 METER RAISED TO GRADE TO PROPERTY FOUND LEAD ON INLET AND RENEWED ON OUTLET.
201701725201 | 2017-12-04 | LEAD | 1009 | ST ANN | BURGUNDY | WILK | PP-POOR PRESSURE ACCOUNT #104887-528259 METER #B032837 CONTRACTOR STATING ONLY 22LBS OF PRESSURE FOR THIS 4 STORY BUILDING EXAMINE INLET FOR POOR PRESSURE /** 1) MN: B032837 SN: 0007098, *TAP: SIZE: A LOC: 60 FEET FROM P LINE AT BURGUNDY, *MB: CODE: BEN1 LOC: 60FT FROM PL BURGUNDY ****/ | 2017-12-06 | REMOVED DEBRIS FROM METER BOX + REPLACED DAMAGE 3/4 INCH WATER METER ,,,, OLD METER B032837 FACT:59814027 MAKE: SENSUS READ:7356
201701725902 | 2017-12-04 | LEAD/PLASTIC | 2534 | MISTLETOE | APPLE | WMRE | ACCT#054024060 METER#A389295 METER BURIED,LOCATE & RAISE /** 1) MN: A259609 SN: 0078222, *TAP: SIZE: A LOC: 133 FEET FROM P LINE AT APPLE, *MB: CODE: CDM1 LOC: ON /** 1) MN: A259609 SN: 0078222, *TAP: SIZE: A LOC: 133 FEET FROM P LINE AT APPLE, *MB: CODE: CDM1 LOC: ON MISTLETOE,134' FROM U.R.P.L. APPLE ****/ | 2018-03-14 | EXCAVATED AND RAISED A 5/8" METER TO GRADE ALSAO RENEWED THE OUT LET PLASTIC ON THE ON THE LEAD ON INLET (JOB COMPLETE)
201701726701 | 2017-12-04 | LEAD | 526 | ST PETER | DECATUR | WILK | WM- LEAK ON THE SIDEWALK EXAMINE INLET SERVICE FOR UNDER GROUND LEAK /** 1) MN: A296957 SN: 0029254, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT CHARTRES, *MB: CODE: CEL1 LOC: 2ND METER ** 2) MN: A316961 SN: 0029254, *TAP: SIZE: B LOC: 207 FEET FROM P LINE AT DECATUR, *MB: CODE: CEL1 LOC: ON ST PETER 207' FROM PL OF DECATUR THERE ARE 2 MORE NOT LISTED. ****/ | 2017-12-22 | REPLACED 5/8 INCH WASHERS IN METER BOX
201701729901 | 2017-12-04 | LEAD/PLASTIC | 2111 | EASTER LN |  | WILK | ML- METER LEAK METER#A350864 ACCT#231004-409386 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A271985 SN: 0139526, *TAP: SIZE: B LOC: 562 FEET FROM P LINE AT VALENTINE CT., *MB: CODE: BDK LOC: ON EASTER LN., 10' FROM D.P.L. VALENTINE CT., 1' ****/ | 2017-12-15 | EXAMINED METER BOX EXCAVATED METER CHOPPED THROUGH ROOTS EXPOSED INLET AND OUTLET SERVICE MADE REPAIR TO INLET SERVICE AND OUTLET SERVICE COPPER FOUND ON INLET AND OUTLET SERVICE NEED COAL MILL AND SAND DRESS UP
201701732501 | 2017-12-05 | LEAD | 2820 | ST ANN |  | WMRE | LOCATION: 183250 MTR# A 399223 METER BOX BURIED, PLEASE LOCATE AND CHANGE METER LOCATE/RAISE/CHANGE METER /** 1) MN: A227631 SN: 0053960, *TAP: SIZE: A LOC: 111 FEET FROM P LINE AT DUPRE N, *MB: CODE: D LOC: 111FT PL N DUPRE 8' OUTSIDE 2' INSIDE CURB ****/ | 2018-01-03 | EXCAVATED IN 4 X 4 GUTTER BOTTOM LIMESTONES RAISE METER BOX UP TO GRADE BACKFILL JOB WITH RIVERSAND /LIMESTONES
201701732601 | 2017-12-05 | LEAD | 2832 | ST ANN |  | WMRE | LOCATION: 178817 MTR# A 403879 METER BOX BURIED, LOCATE AND CHANGE METER LOCATE/RAISE/CHANGE METER /** 1) MN: A272836 SN: 0054345, *TAP: SIZE: B LOC: 63 FEET FROM P LINE AT ST ANN, *MB: CODE: BDH LOC: 64FT P/L ST ANN 7' OUTSIDE ****/ | 2017-12-12 | EXCAVATED 3 X 2 MUD PLOT REPLACED 5/8 INCH METER BOX COCK AND SET 5/8 INCH METER BACKFILLED AND CLEANED THE AREA ***********OLD METER INFO*************** METER:A403879 FAC:14109641 MAKE:HERSEY READ:969
201701733101 | 2017-12-05 | LEAD/PLASTIC | 7810 | GREEN |  | WMTLK | MI-LEAK BETWEEN S/WALK & STREET. 01/10/18 CUSTOMER STATES LEAK IS FLOWING AND CAN'T GET INTO CAR (NLD) EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER BOX UNDER WATER, SIDEWALK AND MUDPLOT FLOODED 02/08/18 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER FLOODING AREA GUTTER BOTTOM & 2 HOUSE DOWN. (KSW) /** 1) MN: A258722 SN: 0062304, *TAP: SIZE: A LOC: 83 FEET FROM P LINE AT BURDETTE, *MB: CODE: CDL LOC: ON GREEN, 83' FROM P.L. BURDETTE,8' OUTSIDE P.L., ****/ | 2018-02-24 | EXCAVATED AND MADE REPAIRS ON A 5/8 INLET LEAD LINE. PLASTIC ON THE OUTLET JOB COMPLETE. JEG
201701734701 | 2017-12-05 | LEAD | 1424 | N DERBIGNY |  | WMRE | LOCATION ID-107973 MTR-B042106 UNABLE TO LOCATE MTR PLEASE LOCATE AND RAISE TO GRADE LOCATE/RAISE METER BOX TO GRADE /** 1) MN: SN: 0038929, *TAP: SIZE: B LOC: 167 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: CDK LOC: 167FT FROM PL ESPLANADE AVE ON N DERBIGNY ****/ | 2018-01-03 | EXCAVATED 4 X 3 GUTTER BOTTOM THROUGH LIMESTONE ,BRICKS,TILEAND MUD RAISED METER BOX TO GRADE BACKFILLED AND CLEANED THE AREA
201701735101 | 2017-12-05 | LEAD/PLASTIC | 2411 | PRANCER | FIESTA | WILK | ML METER LEAK ACCT# 230602-410489 METER# A231159 INLET SERVICE LEAK CAUSING METER BOX TO OVERFLOW /** 1) MN: A231159 SN: 0137777, *TAP: SIZE: B LOC: 463 FEET FROM P LINE AT FIESTA DR, *MB: CODE: A LOC: ON PRANCER 463FT FROM P.L. FIESTA DR 7FT OUTSIDE ****/ | 2017-12-11 | OBSERVED LEAK ON INLET EXPOSED OUTLET LINE OBSERVED COPPER ON OUTLET REPAIRED LEAK BACKFILLED
201701735501 | 2017-12-05 | LEAD | 3350 | DUMAINE | MOSS | WOLK | ML METER LEAK ACCT# 118904-521502 METER# A118980 EXAMINE OUTLET SERVICE FOR LEAK /** 1) MN: A118980 SN: 0029700, *TAP: SIZE: A LOC: 67 FEET FROM P LINE AT MOSS, *MB: CODE: CFLM LOC: ON DUMAINE ST 66.6' FROM LRPL MOSS ST ****/ | 2017-12-21 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201701736501 | 2017-12-05 | LEAD | 6030 | ANNUNCIATION | STATE | WMTLK | MI-LEAK ON THE SIDEWALKI ***********L.THOMPSON @ 14:20PM********* EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER BOX UNDER WATER FLOODING AREA /** 1) MN: A120239 SN: 0011419, *TAP: SIZE: A LOC: 241 FEET FROM P LINE AT STATE, *MB: CODE: BDLM LOC: 242' P.L. STATE ****/ | 2017-12-05 | EXCAVATED IN MUDPLOT ON INLET LEAK ON LEAD LINE MADE ALL REPAIR TO STOP LEAK BACKFILL WITH RIIVERSAND
201701738701 | 2017-12-05 | LEAD | 20 | VIVIAN CT |  | WILK | ML-METER LEAK ACCT#227099-415993 METER#A303445 INLET SERVICE LEAK ON SIDEWALK /** 1) MN: A303445 SN: 0115388, *TAP: SIZE: A LOC: 416 FEET FROM P LINE AT HUNTLEE DR, *MB: CODE: CFL LOC: ON VIVIAN CT., 416' FROM P.L. HUNTLEE DR., 4' OUT- ****/ | 2017-12-06 | EXCAVATED IN CONCRETE DRIVEWAY. REPAIR 5/8" STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND. ALSO TAKE 3/4" LEAD LINE OUT FROM WATER MAIN TO METER BOX. JOB REFER TO ZONE 6. JOB REFER TO PAVE 3X3 CONCRETE D/W
201701739201 | 2017-12-05 | LEAD | 837 | ORLEANS AV | DAUPHINE | WILK | ML METER LEAK ACCT# 108021-527944 METER# A333289 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A310526 SN: 0009050, *TAP: SIZE: B LOC: 47 FEET FROM P LINE AT DAUPHINE, *MB: CODE: CEM3 LOC: 47' P.L. DAUPHINE ****/ | 2017-12-28 | EXCAVATED 3 X 2 BRICK SIDEWALK REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILL AND CLEANED THE AREA
201701739701 | 2017-12-05 | LEAD | 2909 | PAUGER | N MIRO | WILK | ML- METER LEAK METER#A223862 ACCT# 143205-495145 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A223892 SN: 0074714, *TAP: SIZE: A LOC: 61 FEET FROM P LINE AT MIRO N, *MB: CODE: BDKM LOC: ON PAUGER 61' FROM PL OF MIRO N ****/ | 2017-12-21 | EXCAVATED 4 X 3 SIDEWALK CUT ALSO 2 X 2 GUTTER BOTTOM MOVED METER TO SIDEWALK TO PREVENT CUSTOMER FROM PARKING ON METER AGAIN RENEWED OUTLET SERVICE TO PROPERTY BACKFILLED AND CLEANED THE AREA
201701740101 | 2017-12-05 | LEAD/PLASTIC | 1624 | ERIE | WAGNER | WILK | MI- LEAK IN SIDEWALK CAUSING POOR PRESSURE TO PROPERTY ACCT#227375-405755 METER#A344142 BROKEN WATER MAIN IN ASPHALT STREET FLOODING AREA CAUSING POOR PRESSURE TO RESIDENT **1ST AM** /** 1) MN: A344142 SN: 0147692, *TAP: SIZE: B LOC: 182 FEET FROM P LINE AT WHITNEY AVE, *MB: CODE: CDL LOC: ON ERIE, 172' FROM P.L. WHITNEY AVE., 3' OUTSIDE ****/ | 2017-12-06 | BROKE THE STREET AND EXCAVATED ON THE 6" WATER MAIN AND REPAIR LEAK THEN BACKFILL AND CLEAN UP JOB SITE
201701741201 | 2017-12-06 | LEAD | 1212 | FORSTALL |  | WMRE | LOCATION: 140862 MTR# A 414242 METER BOX BURIED, UNABLE TO CHANGE METER REPAIR & CHANGE METER LOCATE & RAISE TO GRADE /** 1) MN: A294659 SN: 0083214, *TAP: SIZE: B LOC: 124 FEET FROM P LINE AT MARAIS, *MB: CODE: BDK LOC: ON FORSTALL 123' FROM PL OF MARAIS ****/ | 2018-01-12 | EXCAVATED TO LOCATE A 5/8 INCH METER BOTTOM DID SO AND SET TO GRADE AND SET A 5/8 INCH METER,,, MADE A 4X4 MUD CUT BACKFILLED AMD DRESS UP CUT,,OLD METER A414242 FACT:14120004 MAKE:HERSEY READ: 729
201701744001 | 2017-12-06 | LEAD | 2721 | N PRIEUR |  | WILK | INLET SERVICE /** 1) MN: A139361 SN: 0072703, *TAP: SIZE: A LOC: 105 FEET FROM P LINE AT ST FERDINAND, *MB: CODE: CFM LOC: ON N PRIEUR 104FT FROM PL OF ST FERDNINAND ****/ | 2017-11-30 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH METER BOX TO STOP LEAK ALSO REMOVED DAMAGE METER BACK FILL AND CLEANED THE AREA **************OLD METER INFO********* METER:A359563 FAC:70687002 MAKE:SENSUS READ:5686
201701744501 | 2017-12-06 | LEAD/PLASTIC | 5387 | PRATT DR |  | WMBK | UNABLE TO CHANGE, CURB COCK FROZEN, CANNOT TURN WATER OFF. PLEASE REPAIR AND CHANGE METER C033319 LOC ID 191406 METER BOX CASING SHIFTED OVER CURB COCK, REPAIR METER /** 1) MN: C008023 SN: 0150850, *TAP: SIZE: C LOC: 301 FEET FROM P LINE AT FILMORE AVE, *MB: CODE: AD LOC: ON PRATT DR 298' FROM PL FILMORE AVE 8' OUTSIDE PL ****/ | 2017-12-26 | EXCAVATED IN MUDPLOT THROUGH TREE ROOTS OVER A 1'' INLET SERVICE LEAK. LEAD ON INLET CHANGED THE COCK RAISE THE METERBOX UP TO GRADE AND REPLACED 10 FT OF LEAD OUTLET WITH 1'' PVC PIPE FROM THE BOX TO PROPERTY BACKFILLED AND DRESSED WIT RIVERSAND. OLD METER INFO C-36027 HERSHEY 15551613 RDG 35
201701744901 | 2017-12-06 | LEAD | 1018 | N JOHNSON |  | WILK | LOCATION: 302798 UNABLE TO SET METER, INLET SERVICE NEED TO BE REPAIRED REPAIR & SET 5/8 METER CUSTOMER WAITING INLET SERVICE LEAK INSIDE METER BOX ALSO SET 5/8 METER, HOUSE UNDER RENOVATION /** 1) MN: SN: 0005450, *TAP: SIZE: C LOC: 125 FEET FROM P LINE AT DUMAINE, *MB: CODE: OOOO LOC: ON N JOHNSON 125FT FROM RUPL DUMAINE ****/ | 2018-01-03 | EXCAVATED IN CONCRETE SIDEWALK + MUD PLOT + REPLACED 5/8 INCH METER BOX COMPLETE ALSO SET 5/8 INCH WATER METER + ALSO FOUND DEAD INLET .NEDD BACK HOE TO REPLACE INLET FROM WATER MAIN TO PROPERTY REFER BACK TO ZOE 4 FOR REPAIR
201701745801 | 2017-12-06 | LEAD | 1414 | N CLAIBORNE AV | ESPLANADE AV | WILK | C Y NO WATER METER#426761 ACCT#117751-486331 *******1ST AM****** INLET SERVICE LEAK BEHIND METER BOX CAUSING CUSTOMER TO HAVE VERY LOW WATER PRESSURE /** 1) MN: A273086 SN: 0026252, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: BEM2 LOC: ON CLAIBORNE 82FT FORM ESPLANADE ****/ | 2017-12-07 | SET METER WITH 2 NEW 5/8 INCH WASHERS TO STOP LEAK LEFT SAFETY BARREL OVER METER TO PREVENT ROLL OVER UNTIL AREA IS CEMENTED BACK
201701745902 | 2017-12-21 | LEAD/PLASTIC | 6100 | PONTCHARTRAIN BL |  | WSNR | REPLACE WATER SERVICE FROM WATER MAIN TO METER BOX /** 1) MN: C018961 SN: 0126993, *TAP: SIZE: C LOC: 50 FEET FROM P LINE AT FOURTEENTH, *MB: CODE: CFN LOC: ON PONTCHARTRAIN 50' FROM PL OF FOURTEENTH ****/ | 2018-11-06 | JOB WILL BE RE- SCHEDULE AT A LATER DATE DO TO PAVEMENT BACK LOG
201701747001 | 2017-12-07 | LEAD/PLASTIC | 1012 | BARTHOLOMEW |  | WILK | ML METER LEAK ACCOUNT #149789428102 METER #A408881 EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A129253 SN: 0051439, *TAP: SIZE: B LOC: 107 FEET FROM P LINE AT RAMPART N, *MB: CODE: BELK LOC: 102FT FROM PL N RAMPART ON BARTHOLOMEW ****/ | 2018-02-25 | EXCAVATED AND MADE REPAIR ON 3/4 INLET SERVICE LEAK MADE 4X4 SIDEWALK AT BACKFILL HOLE
201701747901 | 2017-12-07 | LEAD | 2429 | BARONNE | 2ND | WILK | ML METER LEAK ACCT# 180185-548817 METER# E007879 INLET LEAK, (NO METER IN THE BOX & CURB COCK IN OFF POSITION, BUT WATER STILL PASSING THROUGH) C /** 1) MN: E004676 SN: 0021248, *TAP: SIZE: CCCC LOC: 16 FEET FROM P LINE AT BARONNE, *MB: CODE: CDHN LOC: METR ON SECOND 15' FROM PL BARONNE 6' OUTSIDE PL ****/ | 2018-01-19 | EXCAVATED IN THE 4 X 4 SIDEWALK OVER 5/8 INCH METER BOX FOUND METER BOX STOP COCK LEAKING REOPLACE 5/8 INCH METER BOX STOP COCK BACKFILLJOB COMPLETE
201701749001 | 2017-12-07 | LEAD/PLASTIC | 3522 | RIVER OAKS DR | GEN DE GAULLE DR | WMTLK | ML- METER LEAK ACCT# 230605-415617 MTR# A326050 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A326050 SN: 0137756, *TAP: SIZE: B LOC: 196 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: BDL1 LOC: ON RIVER OAKS DR 197FT FROM P.L. BERKLEY DR 7FT ****/ | 2017-12-28 | EXAMINED METER EXCAVATED EXCAVATED METER OBSERVED LEAK ON OUTLET SERVICE REPAIRED LEAK BACKFILLED CLEANED AREA
201701752401 | 2017-12-09 | LEAD/PLASTIC | 5711 | ALBANY CT | CHELSEA DR | WMTLK | ML-METER LEAK ACCT#231358-417987 METER#A273795 EXAMINE INLET & OULET SERVICE FOR A LEAK METER BOX OVERFLOWING FLOODING CURB & STREET 12/18/17 CUSTOMER STATES LEAK IS GETTING WORSE (KSW) /** 1) MN: A273795 SN: 0142422, *TAP: SIZE: B LOC: 32 FEET FROM P LINE AT CHELSEA DR, *MB: CODE: BDN5 LOC: ON ALBANY CT 32' FROM DPL CHELSEA 2' INSIDE CURB ****/ | 2017-12-22 | EXAMAINED METER OBSERVED LEAKING WATER POURING UP FROM GASS AREA EXCAVATED METER AND AT LEAK EXPOSED LEAK ON OUTLET SERVICE REPAIRED LEAK BACKFILLED
201701752801 | 2017-12-09 | LEAD/PLASTIC | 4457 | FRANCIS DR | RANSOM | WILK | WM-LEAK IN SIDEWALK **********S SLACK 11:54********** INLET SERVICE LEAK IN THE MUD PLOT FLOODING SIDEWALK & CURB. ***CUSTOMER @ 4459 FRANCIS IS ****OUT OF WATER****, *****4457 HAS EXTREMELY LOW PRESSURE,***** UNBALE TO PUMP METER BOX DOWN WATER COMING IN TO FAST /** 1) MN: A329572 SN: 0139998, *TAP: SIZE: B LOC: 10 FEET FROM P LINE AT RANSOM, *MB: CODE: ADL LOC: RES 10FT FROM RANSOM 10FT FROM H.P.L. CURB ****/ | 2017-12-09 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 INLET SERVICE BACKFILLED AREA
201701773401 | 2017-12-10 | LEAD | 7725 | OAK | ADAMS | WILK | ML- METER LEAK ACCT# 126773-583209 MTR# A321307 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A321307 SN: 0051145, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT BURDETTE, *MB: CODE: CDL LOC: ON OAK,110' FROM L.P.L. BURDETTE ****/ | 2018-01-05 | EXCAVATED IN TREE ROOTS AND MADE REPAIRS ON A 5/8 INLET SERVICE LEAK BY HAND. LEAD ON THE INLET AND OUTLET JOB COMPLETE. JEG
201701775801 | 2017-12-11 | LEAD | 2437 | MUSIC | N DORGENOIS | WILK | ***************PICKUP************* EXAMINE INLET SERVICE FOR LEAK METER UNDER WATER MACC#209751-48517 MN#A-401943 /** 1) MN: A267633 SN: 0083038, *TAP: SIZE: B LOC: 74 FEET FROM P LINE AT MUSIC, *MB: CODE: ADHL LOC: SIDE ST/N DORGENOIS 74 FT FROM PL MUSIC ****/ | 2018-01-03 | EXCAVATED 3 X 3 MUD PLOT RENEWED OUTLET SERVICE TO PROPERTY AND REPLACED 5/8 INCH METER BOX COCK METER HAS BEEN RAISED TO GRADE BACK FILLED AND CLEANED THE AREA METER WAS RELOCATED FROM GUTTER AND PUT INTO MUD PLOT CLOSER TO HOUSE
201701775901 | 2017-12-11 | LEAD | 2439 | MUSIC | N DORGENOIS | WILK | ************PICKUP************** EXAMINE INLET SERVICE FOR LEAK METER UNDER WATER ACC#150263-485151 MN#A-419844 /** 1) MN: A324774 SN: 0080838, *TAP: SIZE: B LOC: 73 FEET FROM P LINE AT MUISC, *MB: CODE: HDL1 LOC: ON N DORGENOIS 74FT FROM P.L. MUSIC 8FT OUTSIDE P. ****/ | 2018-01-03 | EXCAVATED 3 X 3 MUD PLOT RENEWED OUTLET SERVICE TO PROPERTY AND 5/8 INCHMETER BOX COCK REPLACED RELOCATED METER FROM GUTTER AND PUT INTO MUD PLOT CLOSER TO HOUSE BACKFILLED AND CLEANED THE AREA
201701779601 | 2017-12-11 | LEAD/PLASTIC | 6324 | S JOHNSON | CALHOUN | WILK | ML METER LEAK METER # A413687 ACCOUNT # 148679-564659 INLET SERVICE LEAK BAD CURB COCK FLOODING SIDEWALK & GUTTER BOTOM /** 1) MN: A218806 SN: 0080917, *TAP: SIZE: B LOC: 106 FEET FROM P LINE AT CALHOUN, *MB: CODE: CDLN LOC: ON JOHNSON 106FT FROM CALHOUN ****/ | 2018-05-21 | ARRIVED ON JOB SITE FOR LEAK INSIDE OF METER BOX MAD EA 5 X 5 CUT ON SIDEWALK EXCAVTED ON SIDEWALK AND MADE REPAIR TO BAD METER COCK EXCHANGE METER COCK WITH NEW METR COCK BACKFILLED AND DRESSED CUT UP.TIED INTO LEAD NEED TO BE REMOVED FROM MAIN TO PROPERTY.
201701787502 | 2017-12-12 | LEAD | 3312 | NAPOLEON AV |  | WMRE | METER BURIED,LOCATE & RAISE /** 1) MN: A340165 SN: 0070567, *TAP: SIZE: B LOC: 105 FEET FROM P LINE AT PRIEUR S, *MB: CODE: ADL1 LOC: ON NAPOLEON AVE 105' FROM PL S PRIEUR ****/ /** 1) MN: A340165 SN: 0070567, *TAP: SIZE: B LOC: 105 FEET FROM P LINE AT PRIEUR S, *MB: CODE: ADL1 LOC: ON NAPOLEON AVE 105' FROM PL S PRIEUR ****/ | 2018-01-19 | FOUND METER 1 FT FROM THE EDGE OF SIDEWALK COVER WITH MUD + CONCRETE REMOVE ALL CONCRETE + MUD OFF METER BOX MARKED METER BOX WITH BLUE MARKING PAINT
201701787902 | 2017-12-12 | LEAD | 3308 | MAGAZINE | TOLEDANO | WMRE | LOCATION ID# 217049 MTR# A347966 PLEASE LOCATE AND RAISE TO GRADE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-01-19 | EXAMINED JOB FOUND METER LOCATION BEHIND THE BUILDING 60 FT FROM TOLEDANO PROPERTY LINE METR TOP MARKED WITH BLUE PAINT AND METER IS UP GRADE
201701792101 | 2017-12-12 | LEAD | 3034 | URSULINES AV | N LOPEZ | WMRE | LOCATION ID# 115006 MTR# A283279 PLEASE LOCATE AND RAISE TO GRADE /** 1) MN: A283279 SN: 0072342, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT LOPEZ N, *MB: CODE: BG LOC: ON URUSLINES 94.6FT FROM LOPEZ N IN YARD ****/ | 2018-01-26 | EXAMINED AREA AT ABOVE LOCATION + LOCATED METER ON PROPERTY CUSTOMER STATES THE METER HAS BEEN IN SAME LOCATION FOR OVER 19 YEARS + DOES NOT WANT METER MOVED MARKED WITH BLUE PAINT
201701795301 | 2017-12-12 | LEAD | 2133 | DUMAINE | N GALVEZ | WILK | PP-POOR PRESSURE ACCT# 303046-713120 METER# A417972 INLET SERVICE LEAK @ CURB UNDERGROUNG CAUSING POOR PRESURE GETTING OFF IN DCB, RENOVATED PROPERTY /** 1) MN: SN: 0052150, *TAP: SIZE: A LOC: 38 FEET FROM P LINE AT GALVEZ N, *MB: CODE: ADL1 LOC: 35FT FROM RPL N GALVEZ ****/ | 2018-01-10 | ARRIVED AT ABOVE LOCATION TO FIND A 3/4 LEAD INLET SERVICE LEAKING. REPAIRED BY REPLACING WITH 3/4 PLASTIC TUBING FROM A 4'' WATER MAIN TO METER . MADE A 6X6X3X3 CONCRETE CUT AND A 3X3 SIDEWALK CUT BACKFILLED AND DRESS UP CUT .
201701798401 | 2017-12-12 | LEAD | 330 | JANE AL | PALMYRA | WILK | MI--LEAK IN THE STREET CHANGED FROM 300 BLK JANE PL **********1ST AM******** ***********DAMAGE CLAIM************ CUT INLET SERVICE BY "TWIN SHORES LANDSCAPING" 701 S. ALEXANDER, NEW ORLEANS LA 70119 NOT SURE IF ANYONE OUT OF WATER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-12-14 | ECAVATED 3 X 3 MUD PLOTTHROUGH BRICK + CONCRETE MADE REPAIR ON INLET SERVICE LINE TO STOP LEAK BACKFILL AND CLEANED THE AREA
201701798601 | 2017-12-12 | LEAD/PLASTIC | 2431 | MENDEZ | MUSIC | WOLK | MI- NEED LEAD WHIP CHANGED OUT HOLE EXPOSED ACCT#303666-478090 NO METER # CHANGE LEAD WHIP HOUSE UNDER RENOVATIONS /** 1) MN: C027715 SN: 0110031, *TAP: SIZE: C LOC: 21 FEET FROM P LINE AT MENDEZ, *MB: CODE: ADHL LOC: MTR ON MUSIC 21FT FRM PL MENDEZ 7FT OUTSD PL ****/ | 2017-12-30 | EXCAVATED A 5 X 5 MUDPLOT CUT TO RENEW OUTLET SERVICE FROM METERBOX TO P.L. FOUND LEAD ON INLET SERVICE. NO METER IN METERBOX. RAISED METER BOX TO GRADE. JEG
201701800002 | 2017-12-13 | LEAD | 1828 | ROBERT | DANNEEL | WMRE | ACCT#053182220 METER#A282923 METER BURIED,LOCATE & RAISE /** 1) MN: A282923 SN: 0058938, *TAP: SIZE: A LOC: 216 FEET FROM P LINE AT DANNEEL, *MB: CODE: CDN4 LOC: ON ROBERT,215' FROM S.P.L. DANNEEL ****/ DOTTIE READY 9-6-18 EXP 9-26-18 | 2018-09-29 | EXCAVATED AND MADE REPAIRS ON 3/4 INCH INLET SERVICE ALSO RAISE METER BOX UP TO GRADE MADE 4 X 4 MUD PLOT CUT BACKFILLED AND CLEANED THE AREA
201701801701 | 2017-12-13 | LEAD | 2700 | N RAMPART |  | WILK | WM-LEAK BETWEEN SIDEWALK & STREET CHANGED FROM 927 PORT INLET SERVICE LEAK IN BOX /** 1) MN: A213854 SN: 0047106, *TAP: SIZE: A LOC: 74 FEET FROM P LINE AT RAMPART N, *MB: CODE: BEHK LOC: SIDE ST 76' P.L. N RAMPART ****/ | 2018-05-31 | EXCAVATED 3 X 2 SIDEWALK CUT RENEWED OUTLET TO PROPERTY ALSO REPLACED 5/8 INCH METER COCK BACKFILLED + CLEAN THE AREA
201701802801 | 2017-12-13 | LEAD | 814 | CANAL | CARONDELET | WMLK | WM-LEAK IN CURB **********J. GILLIAM @ 9:25AM*********** CHANGED FROM 800 CANAL LEAK ON THE MAIN FLOODING SIDEWALK AND INSIDE OF BUSINESS /** 1) MN: E005642 SN: 0002722, *TAP: SIZE: CCCC LOC: 124 FEET FROM P LINE AT CARONDELET, *MB: CODE: OOOO LOC: ON CANAL 124'FROM P.L. CARONDELET ** 2) MN: SN: 0000000, *TAP: SIZE: H LOC: 125 FEET FROM P LINE AT CARONDELET, *MB: CODE: __ LOC: ****/ | 2017-12-13 | SHUT OFF 6 INCH FIRE SERVICE YO ABOVE LOCATION
201701803101 | 2017-12-13 | LEAD/PLASTIC | 3770 | INWOOD AV | TALL OAKS DR | WILK | WM-LEAK IN STREET INLET SERVICE LEAK @ CURB LEFT 1 CONE FOR SAFTY /** 1) MN: A258083 SN: 0149047, *TAP: SIZE: A LOC: 49 FEET FROM P LINE AT TALL OAK, *MB: CODE: DN1 LOC: ON INWOOD AVE 49' FROM DPL TALL OAK 2.5' INSIDE CU ****/ | 2018-02-22 | EXCAVATED INLET AND OUTLET SERVICE EXAMINE INLET AND OUTLET SERVICE OBSERVED LEAKING ONINLET SERVICE MADE REPAIRS BACKFILLED AND CLEAN AREA
201701805301 | 2017-12-13 | LEAD/PLASTIC | 4132 | POLK | HWY 406 | WOLK | ML- METER LEAK METER#A426865 ACCT#238796-715334 (PLUMBER TURN OFF METER DUE TO FLOODING FROM LEAK) **********B LEAVE IN SYSTEM*********** OUTLET DISCONNECTED FROM FITTING CUSTOMER OUT OF WATER LEFT 1 CONE ON SITE , FOUND OFF LEFT OFF, HOUSE IS VACANT **METER IS MARKED WITH BLUE PAINT** /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-12-21 | EXAMINE JOB FOUND TUBING DISCONNECTED AT JOINT REPLACED PACK JOINT 1" WITH 3/4 REDUCER REPLAC UPPERCASING
201701807101 | 2017-12-13 | LEAD/PLASTIC | 601 | PARK BL | HERMOSA | WMTLK | ML-METER LEAK METER#A382463 EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A118593 SN: 0091306, *TAP: SIZE: A LOC: 85 FEET FROM P LINE AT HERMOSA, *MB: CODE: AD LOC: ON PARK BLVD 84.5FT FROM P.L. HERMOSA 10FT OUTSIDE ****/ | 2017-12-29 | EXAMINED METER OBSERVED LEAK EXCAVATED METER BOX REPLACED LEAD FROM OUTLET SIDE WITH PLASTIC TO PROPERTY CONNECTION BACKFILLED CLEAN SITE
201701808101 | 2017-12-13 | LEAD | 5436 | MARAIS | FLOOD | WILK | RPML-METER LEAK ACCT 303668-715668 ( METER INSTALLED TODAY PER METER SHOP) INLET SERVICE LEAK /** 1) MN: A255143 SN: 0075416, *TAP: SIZE: A LOC: 183 FEET FROM P LINE AT FLOOD, *MB: CODE: DK LOC: ON MARAIS, 183' FROM U.R.P.L. FLOOD,3' FROM CURB ****/ | 2018-01-05 | EXCAVATED 3 X 3 GUTTER BOTTOM ALSO 4 X 2 SIDEWALK CUT MOVED METER BOX FROM GUTTER BOTTOM TO SIDEWALK AND RENEWED TO PROPERTY BACKFILLED AND CLEANED THE AREA
201701808201 | 2017-12-13 | LEAD | 819 | FRANKLIN AV |  | WMBK | CASING IS BROKEN AND NEEDS TO BE REPAIRED. METER A427738 LOC ID 303511 BROKEN UPPER METER BOX CASING /** 1) MN: A114262 SN: 0046910, *TAP: SIZE: A LOC: 98 FEET FROM P LINE AT DAUPHINE, *MB: CODE: BLM LOC: ON ALMONASTER AVE.,98' FROM U.S.P.L. DAUPHINE ****/ | 2017-12-27 | REPLACED 5/8 INCH METER BOX CASING IN A PREVIOUS CUT
201701811601 | 2017-12-14 | LEAD/PLASTIC | 2101 | ADAMS |  | WMRE | LOCATION: 138513 MTR# A 251584 LID STUCK IN CASING, REPAIR AND CHANGE METER LOCATE & MARK METER /** 1) MN: A251584 SN: 0098595, *TAP: SIZE: B LOC: 46 FEET FROM P LINE AT ADAMS, *MB: CODE: BDH1 LOC: ON PANOLA ST 46' FROM PL ADAMS ****/ | 2018-03-06 | EXCAVATED AROUND A 5/8 METER MARK METER AND RAISED IT COULD NOT RENEWED THE OUT LET DUE TO A CAR WAS NEXT TO THE METER JOB COMPLETE
201701813401 | 2017-12-14 | LEAD/PLASTIC | 3711 | RUE DELPHINE | CARLISLE CT | WILK | ML- METER LEAK ACCT# 232609-416953 METER# A400105 INLET SERVICE LEAK /** 1) MN: A320932 SN: 0146699, *TAP: SIZE: B LOC: 445 FEET FROM P LINE AT CARLISLE CT, *MB: CODE: BDL2 LOC: RES. 446FT FROM PL CARLISLE ****/ | 2017-12-27 | EXAMINED METER EXCAVATED THROUGH ROOTS EXPOSED INLET OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK NEED SAND FOR BACKFILL PLACED 5 CONES ON HOLE AND FLAG ALSO NEED FLUSH TRUCK FOR GROUND
201701814501 | 2017-12-14 | LEAD/PLASTIC | 2300 | HOLIDAY DR |  | WILK | ML METER LEAK ACCOUNT #231454408839 METER#C017426 INLET SERVICE LEAK AT CURB /** 1) MN: C017426 SN: 0141908, *TAP: SIZE: C LOC: 352 FEET FROM P LINE AT COPERNICUS, *MB: CODE: BDK LOC: 352FT FROM P.L. COPERNICUS ****/ | 2017-12-27 | EXAMINED METER EXPOSED INLET OUTLET OBSERVED LEAK ON OUTLET SERVICE REPAIRED LEAK
201701814601 | 2017-12-14 | LEAD | 1202 | FORSTALL |  | WILK | MI- LEAK BETWEEN S/WALK & CURB. EXAMINE INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A281288 SN: 0079782, *TAP: SIZE: B LOC: 13 FEET FROM P LINE AT MARAIS, *MB: CODE: CD LOC: ON FORSTALL 15' FROM P.L. MARAIS 8' OUTSIDE 4' ****/ | 2018-01-22 | EXCAVATED 3 X 3 AT EDGE OF SIDEWALK ALSO 6 X 1 TREACH TO PROPERTY RENEWED OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILLED AND CLEANED THE AREA METER BOX WAS RAISED TO GRADE
201701815101 | 2017-12-14 | LEAD | 3005-07 | DUMAINE | N GAYOSO | WILK | MI- LEAK IN THE SIDEWALK INLET SERVICE LEAK INSIDE METER BOX, REPAIRS WAS PREVIOUS MADE /** AT 3005: 1) MN: A245321 SN: 0034065, *TAP: SIZE: B LOC: 52 FEET FROM P LINE AT GAYOSO N, *MB: CODE: OOO LOC: 52' P.L. N GAYOSO ****/ | 2017-12-19 | REPLACED 5/8 INCH WSHER TO STOP LEAK
201701815201 | 2017-12-14 | LEAD | 1805 | PORT | N ROMAN | WMTLK | ML-- METER LEAK METER # A410314 ACCT# 174076-479967 EXAMINE INLET/OUTLET SERVICE FOR A LEAK, RESDIENCE PARKING ON TOP OF METER /** 1) MN: A317653 SN: 0117565, *TAP: SIZE: B LOC: 62 FEET FROM P LINE AT ROMAN N, *MB: CODE: C LOC: POST BET.PRIEUR & ROMAN 60' FROM P.L.N ROMAN 7' O ****/ | 2017-12-15 | EXCAVATED 4 X 4 SIDEWALK CUT MOVED METER BOX TO SIDEWALK BACKFILL AND CLEANED THE AREA
201701816301 | 2017-12-14 | LEAD | 1315 | GORDON |  | WILK | ML-- METER LEAK METER# A299072 ACCT# 172689-422570 INLET SERVICE LEAK NEAR BOX /** 1) MN: A338365 SN: 0116130, *TAP: SIZE: A LOC: 104 FEET FROM P LINE AT URQUHART, *MB: CODE: BDL LOC: RES ON GORDON 104FT FROM PL URQUHART 8' OUTSIDE P ****/ | 2018-01-12 | EXCAVATED 3 X 3 GUTTER ALSO 3 X 2 MUD PLOT RELOCATED METER FROM GUTTER TO MUD PLOT ALSO RENEWED OUTLET SERVICE TO PROPERTY BACKFILLED AND CLEANED THE AREA
201701818601 | 2017-12-14 | LEAD | 1909 | DUELS |  | WILK | LOCATION ID-143445 MTR-A408301 BAD METER LEAK INLET SERVICE LEAK IN MUDPLOT FLOODING CURB/STREET /** 1) MN: A304063 SN: 0077643, *TAP: SIZE: A LOC: 81 FEET FROM P LINE AT ALLEN, *MB: CODE: BDL LOC: ON DUELS 80' FROM PL OF ALLEN ****/ | 2018-01-16 | EXCAVATED 3 X 3 GUTTER BOTTOM THROUGH SEND + LIMESTONE RENEWED OUTLET TO PROPERTY TO STOP LEAK ***********OLD METER INFO******** METER:A408301 FAC:14114063 MAKE:HERSEY READ:4040
201701821101 | 2017-12-15 | LEAD | 3110 | DESOTO |  | WILK | MI-METER BOX LEAKING EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A256368 SN: 0014804, *TAP: SIZE: B LOC: 69 FEET FROM P LINE AT LOPEZ N, *MB: CODE: CEM1 LOC: ON DE SOTO 78' FROM USPL N LOPEZ ****/ | 2018-01-06 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201701822601 | 2017-12-15 | LEAD | 726 H | FRENCHMEN | DAUPHINE | WILK | MI-LEAK ON THE SIDEWALK INLET SERVICE LEAK IN BOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-01-07 | EXCAVATED 5 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK AND RENEWED OUTLET SERVICE LINE TO PROPERTY BACKFILL AND CLEANED THE AREA
201701822701 | 2017-12-15 | LEAD/PLASTIC | 2322 | ST THOMAS |  | WOLK | ML- METER LEAKING MTR.# A 427707 ACCT.# 303589-542332 OUTLET SERVICE LEAK WHEN METER IS TURNED ON FLOODING METER BOX. **HOUSE UNDER RENOVATIONS** /** 1) MN: A342518 SN: 0054776, *TAP: SIZE: __ LOC: 164 FEET FROM P LINE AT PHILIP, *MB: CODE: ADKO LOC: ON ST. THOMAS,164.3' FROM U.P.L. PHILIP ****/ | 2017-12-21 | EXAMINED AREA EXPOSED OUTLET SERVICE ADDED COLLER AND PLASTIC CNI TO WHIP BACKFILLED
201701823301 | 2017-12-15 | LEAD | 1320 | JOLIET | WILLOW | WILK | ML METER LEAK ACCT# 300083-708539 METER# A420976 INLET SERVICE LEAK IN THE MUD PLOT, GETTING OFF IN THE DCB /** 1) MN: 000000 SN: 0044450, *TAP: SIZE: A LOC: 146 FEET FROM P LINE AT WILLOW, *MB: CODE: ADN LOC: ON JOLIET,146' FROM R.P.L. WILLOW ****/ | 2018-03-13 | EXCAVATED IN MUDPLOT. REPAIR 3/4 INLET LEAD LINE DRESS UP WITH RIVERSAND
201701823302 | 2018-03-13 | LEAD | 1320 | JOLIET | WILLOW | WSNR | REFER TO ZONE TO REMOVE LINAD LINE ON INLET /** 1) MN: 000000 SN: 0044450, *TAP: SIZE: A LOC: 146 FEET FROM P LINE AT WILLOW, *MB: CODE: ADN LOC: ON JOLIET,146' FROM R.P.L. WILLOW ****/ | 2018-11-05 | ZONE 1 WILL RE- SCHEDULE JOB AT A LATER DATE DO TO PAVING BACK LOG PER NETWORKS OFFICE
201701839602 | 2017-12-17 | LEAD | 1912 | FOUCHER | DRYADES | WMRE | NEED MACHINE METER BURIED,LOCATE & RAISE /** 1) MN: A315497 SN: 0050891, *TAP: SIZE: A LOC: 98 FEET FROM P LINE AT DRYADES, *MB: CODE: AEN1 LOC: ON FOUCHER 98FT FORM DRAYDES ****/ /** 1) MN: A315497 SN: 0050891, *TAP: SIZE: A LOC: 98 FEET FROM P LINE AT DRYADES, *MB: CODE: AEN1 LOC: ON FOUCHER 98FT FORM DRAYDES ****/ | 2018-01-15 | ARRIVED ON JOB EXCAVATYED IN MUDPLOT LOCATED METER AND RAISED IT TO GRADE AND BACFILLED JOB COMPLETE.
201701849301 | 2017-12-18 | LEAD | 6100 | N DERBIGNY | TUPELO | WMTLK | MI-LEAK IN THE SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK **********M DAIGLE 13:00********** 01/04/18 PER INSP K GRIFFIN UPGRD TO AN ( A ) GIVE OUT **********CUSTOMER NOW OUT OF WATER********** /** 1) MN: C023109 SN: 0131971, *TAP: SIZE: B LOC: 47 FEET FROM P LINE AT TUPELO, *MB: CODE: ADLM LOC: ON NO. DERBIGNY, 47' FROM P.L. TUPELO, 2' OUTSIDE ****/ | 2018-01-04 | EXCAVATED 4 X 2 MUD PLOT AT PROPERTY MADE REPAIR OUTLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201701851801 | 2017-12-18 | LEAD/PLASTIC | 1204 | ODEON AV |  | WILK | ML-- METER LEAK ACCT # 230461-408146 METER# A413629 INLET SERVICE LEAK BY CURB BY DRIVEWAY /** 1) MN: A281771 SN: 0138226, *TAP: SIZE: B LOC: 33 FEET FROM P LINE AT DE ARMAS, *MB: CODE: ADK LOC: ON ODEON 33FT FROM DE ARMAS 5FT OUTSIDE ****/ | 2017-12-27 | EXAMINED INLET SERVICE OBSERVED LEAK ON OUTLET SERVICE REPAIRED LEAK CLEANED AREA
201701852401 | 2017-12-18 | LEAD | 801 | FRENCHMEN |  | WMRE | LOCATION ID-223587 MTR-A410885 UNABLE TO LOCATE MTR/ PLEASE LOCATE LOCATE AND MARK METER /** 1) MN: C022296 SN: 0030704, *TAP: SIZE: A LOC: 41 FEET FROM P LINE AT DAUPHINE, *MB: CODE: AFHM LOC: ON FRENCHMEN 61FT FROM P.L. DAUPHIINE 3FT OUTSIDE ****/ | 2018-01-25 | MARKED METER TOP AND STREET SHOWING THE LOACTION OF THE METER
201701853201 | 2017-12-18 | LEAD/PLASTIC | 3759 | PRESTON PL | BRUNSWICK CT | WILK | ML METER LEAK METER# A271358 LOCATION# 232303-418746 INLET SERVICE LEAK BEHIND CURBCOCK FLOODING GUTTER BOTTOM /** 1) MN: A271358 SN: 0145613, *TAP: SIZE: B LOC: 164 FEET FROM P LINE AT BRUNSWICK CT, *MB: CODE: ADKL LOC: ON PRESTON PL 174' FROM PL BRUNSWICH 7' OUTSIDE PL ****/ | 2017-12-28 | EXCAVATED METER BOX AND FOUND LEAK ON COCK REPLACED COCK AND WASHERS
201701855401 | 2017-12-19 | LEAD/PLASTIC | 828 | ORANGE |  | WOLK | MI- CUT SERVICE ** CUSTOMER WITHOUT WATER ** ********CUT SERVICE ******** (S.SLACK @ 10:56AM) CUT OUTLET SERVICE BY ENTERGY GAS **FOREMAN SHANNON (337)344-2789*** /** 1) MN: A238184 SN: 0046829, *TAP: SIZE: A LOC: 87 FEET FROM P LINE AT ORANGE, *MB: CODE: BDH3 LOC: 77FT FROM PL ORANGE GUTTER NEEAR FOOT WALK ****/ | 2017-12-19 | EXAMINED LEAK EXCAVATED TO PROPERTY REPLACED LEAD LINE WITH PLASTIC REPAIRED LEAK BACKFILLED
201701855601 | 2017-12-19 | LEAD/PLASTIC | 911 | FLANDERS | PATTERSON DR | WOLK | LOCATIONID#229675-408517 METER#A242307 OUTLET CONNECTION LEAK /** 1) MN: A242307 SN: 0131200, *TAP: SIZE: B LOC: 22 FEET FROM P LINE AT PATTERSON DR, *MB: CODE: CD LOC: ON FLANDRES 22FT FROM PATTERSON 7FT OUTSIDE ****/ | 2017-12-28 | EXCAVATED METER BOX AND OUTLET BY HAND NO LEAK WAS FOUND NEED MACHINE TO REMOVE LEAD FROM INLET
201701855901 | 2017-12-19 | LEAD | 1433 | CLOUET | N ROBERTSON | WMTLK | MI--LEAK ON THE SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK IN THE GUTTER BOTTOM /** 1) MN: A331448 SN: 0061758, *TAP: SIZE: A LOC: 43 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: CDL LOC: 44' P.L. N ROBERTSON ****/ | 2018-02-05 | EXCAVATED 5 X 4 SIDEWLK CUT RELOCATED BOTH 1433 + 1435 CLOUET METER INTO THE SIDEWALK BACKFILLED AND CLEANED THE AREA
201701858101 | 2017-12-19 | LEAD | 853 | OLGA | DUMAINE | WILK | ML-METER LEAKING *****AGAIN***** INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A322938 SN: 0033601, *TAP: SIZE: A LOC: 200 FEET FROM P LINE AT DUMAINE, *MB: CODE: BD LOC: 200FT FROM USPL DUMAINE ****/ | 2017-12-19 | ARRIVE AT ABOVE LOCATION EXAMINE AND FOUND OUTLET LEAKING EXCAVATED IN MUDPLOT ON OUTLET MADE ALL REPAIRS TO STOP LEAK ON LEAD BACKFILL WITH RIVER SAND LJF
201701860101 | 2017-12-20 | LEAD | 1630 | ARABELLA |  | WILK | ML-- METER LEAK METER # B0394460 ACCT# 108057-568737 INLET SERVICE LEAK BEHIND CURB COCK, FLOODING GUTER BOTTOM /** 1) MN: B025603 SN: 0009163, *TAP: SIZE: B LOC: 103 FEET FROM P LINE AT DANNEEL, *MB: CODE: BEK LOC: 105' P.L. DANNEEL ****/ | 2018-02-07 | ARRIVED ON JOB EXCAVATED IN SIDEWALK FOUND 3/4 METER BOX COCK LEAKING MADE REPAIRS AND BACK FILLED. JOB COMPLETE.
201701861001 | 2017-12-20 | LEAD | 2638 | DUBREUIL | FLORIDA AV | WILK | MI-LEAK IN THE STREET CHANGED FROM FLORIDA AV/ DUBREUIL INLET SERVICE LEAK AT MAIN ON ABANDON SERVICE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-01-10 | EXCAVATED 4 X 10 MUD PLOT FOUND LEAK ON ABANDON INLET SERVICE AT THE WATERMAIN MADE REPAIR ON INELT BACKFILLED JOB WITH RIVERSAND
201701861701 | 2017-12-20 | LEAD | 1239 | CONGRESS |  | WILK | INLET SERVICE LEAK /** 1) MN: A116153 SN: 0050252, *TAP: SIZE: A LOC: 69 FEET FROM P LINE AT CONGRESS, *MB: CODE: ADHK LOC: 69'FROM L R P L CONGRESS SIDE ST ****/ | 2017-12-19 | EXCAVATED 4 X 8 GUTTER BOTTOM FOUND LEAK ON 5/8 INCH INLER SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND/COLDMILL
201701863001 | 2017-12-20 | LEAD/PLASTIC | 500 | RIVER OAKS DR | ANSON | WOLK | MI--LEAK IN THE SIDEWALK OUTLET SERVICE LEAK FLOODING CURB/SIDEWALK GETTING OFF INTO DRAIN CATCH BASIN 11/21/17 CUSTOMER HAS OUTLET SERVICE LEAK CAUSING VERY POOR PRESSURE ALSO CONSTANT REGISTRATION ON METER JOB UPGRADED TO 1ST AM PER INSP L HEBERT SENT TO ZONE 6 PRINTER (FCP) /** 1) MN: A242784 SN: 0118119, *TAP: SIZE: B LOC: 27 FEET FROM P LINE AT ANSON, *MB: CODE: CDL LOC: ON RIVER OAKS DR., 27' FROM P.L. ANSON, 7' OUTSIDE ****/ | 2017-12-22 | EXAMINED METER OBSERVED LEAK COMING FROM GRASS AREA EXCAVATED METER AND EXCAVATE GRASS AREA CUT THROUGH ROOTS TO EXPOSE LEAK AT PROPERTY CONECTION REPAIRED LEAK NOTIFIED OWNER THAT THERE A LEAK SOMEWHERE ON THEIR PROPERTY REASON NFOR METER CONSTRANT REGISRATION
201701863101 | 2017-12-20 | LEAD/PLASTIC | 121 | PINEWOOD CT | CYPRESS ACRES DR | WILK | ML- METER LEAK METER#A400891 ACCT#235925-407228 INLET SERVICE LEAK IN MUDPLOT FLOODING CURB /** 1) MN: A220670 SN: 0164441, *TAP: SIZE: A LOC: 8 FEET FROM P LINE AT CYPRESS ACRES DR, *MB: CODE: OOO LOC: ON PINWOOD 8FT FROM PL CYPRESS ACRES 9FT OUTSD ****/ | 2017-12-27 | EXCAVATED METER BOX BY HAND TO EXPOSED LEAK. FOUND LEAK ON INLET SERVICE COCK,,,REPLACED COCK
201701864001 | 2017-12-21 | LEAD/PLASTIC | 1471 | CASA CALVO | LAWRENCE ST | WMTLK | WM-LEAK IN SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER BOX OVERFLOW FLOODING AREA /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2017-12-27 | EXAMINED METER FOR LEAK FOUND LEAK ON BOX COCK EXCAVATED BY HAND AND REPALCED COCK IN BOX
201701866001 | 2017-12-21 | LEAD | 1996 | FLORIDA AV |  | WILK | ML- METER LEAK ACCT # 179112-496166 METER # B034097 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: B020656 SN: 0125314, *TAP: SIZE: B LOC: 20 FEET FROM P LINE AT FLORIDA AVE, *MB: CODE: BDLH LOC: ON ST ANTHONY 20FT FROM PL FLORIDA AVE 7' OUTSIDE ****/ | 2018-03-05 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK 3/4 INCH INLET SERVICE MADE REPAIR ON INLET RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILL JOB WITH RIVERSAND
201701868101 | 2017-12-21 | LEAD | 817 | N CLAIBORNE AV | ST ANN | WILK | MI- LEAK ON THE SIDEWALK, FLODDING THE AREA INLET SERVICE LEAK ON SIDEWALK FLOODING SIDEWALK 01/31/18 CUST STATES LEAK HAS GOTTEN WORST (KSW) /** 1) MN: SN: 0001288, *TAP: SIZE: A LOC: 5 FEET FROM P LINE AT ST.ANN, *MB: CODE: __ LOC: ON N CLAIBORNE 121'FROM P.L. ST.ANN IN SIDEWALK ** 2) MN: SN: 0001288, *TAP: SIZE: C LOC: 103 FEET FROM P LINE AT ST ANN, *MB: CODE: __ LOC: ON N.CLAIBORNE 103FT FRM ST ANN 9FT INSD CURB ****/ | 2018-03-20 | EXCAVTED IN CONCRETE SIDEWALK + MADE REPAIR ON 1 INCH ABANDONED INLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201701869101 | 2017-12-21 | LEAD | 3701 | LAUREL | AMELIA | WILK | ML--METER LEAK ACCT# 120718-709625 METER# A291301 INLET SERVICE LEAK /** 1) MN: A280671 SN: 0036895, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT LAUREL, *MB: CODE: BFHL LOC: ON AMELIA ST 63.5' FROM USPL LAUREL ST ****/ DOTTIE READY 6-7-18 EXP 6-27-18 | 2018-06-08 | REPLACED 5/8 METER BOX COCK. TIED INTO LEAD
201701869604 | 2018-01-05 | LEAD/PLASTIC | 2036 | OCTAVIA | S LIBERTY | WILK | LEAK ON SIDEWALK BY TREE STUMP INLET SERVICE LEAK FLOODING CURB IN FRONT OF EMPTY LOT ARRIVED ON JOB EXCAVATED IN MUDPLOT TRIED TO FIX JOB BUT COULD NOT FIX JOB DUE TO TREE ROOTS NEED TO COME BACK WITH MACHINE /** 1) MN: B020203 SN: 0063399, *TAP: SIZE: B LOC: 52 FEET FROM P LINE AT OCTAVIA, *MB: CODE: CDHL LOC: ON S LIBERTY ST 53' FROM URPL OCTAVIA ****/ | 2018-01-08 | REPLACED TWO 3/4 METERR BOX COMPLETE AND LEFT WHIPS UNABLE TO REPLACE LEAD FROM WATER MAIN DUE TO CAR PARKED OVER WATER MAIN TIED INTO LEAD AT CURB.
201701870001 | 2017-12-22 | LEAD | 2326 | GALLIER | N TONTI | WILK | ML METERLEAK MTR#A114527 ACCT#136247-434007 LEAK BEHIND CURBCOCK PER INSPECTOR /** 1) MN: A114527 SN: 0084295, *TAP: SIZE: A LOC: 189 FEET FROM P LINE AT TONTI N, *MB: CODE: CD LOC: ON GALLIER ST 190' FROM N TONTI ****/ | 2018-03-07 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING IN MUD PLOT + REPAIRED IT *BACKFILLED*
201701872201 | 2017-12-22 | LEAD | 1026 | ST CLAUDE AV |  | WILK | LOCATION: 109708 MTR# B022842 REPAIR BROKEN STEM ON CURB COCK AND CHANGE METER BROKEN CURB COCK /** 1) MN: B022842 SN: 0019805, *TAP: SIZE: B LOC: 115 FEET FROM P LINE AT URSULINES AV, *MB: CODE: CEL LOC: 115' P.L. URSULINES AV ****/ | 2018-02-27 | EXCAVATED IN CONCRETE SIDEWALK + REPLCAED 3/4 INCH CURB COCK BACLKFILLED + DRESSED UP AREA
201701872801 | 2017-12-22 | LEAD | 1944 | CHARBONNET | N JOHNSON | WILK | **********PICK UP********** INLET SERVICE LEAK IN METER BOX /** 1) MN: A152415 SN: 0134854, *TAP: SIZE: A LOC: 15 FEET FROM P LINE AT N JOHNSONN, *MB: CODE: BDL1 LOC: ON CHARBONNET, 15' FROM P.L. NO. JOHNSON, 7' OUT- ****/ | 2018-03-01 | EXCAVTED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201701874301 | 2017-12-22 | LEAD/PLASTIC | 1757 | N ROCHEBLAVE | ST BERNARD AV | WILK | WM LEAK BETWEEN STREET & SIDEWALK CHANGED FROM 1750 N ROCHEBLAVE INLET SERVICE LEAK ON AN ABANDON SERVICE IN FRONT VACANT LOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-02-25 | EXCAVATED AND MADE REPAIR ON 2" WATER LINE AT CURB MADE 5X9 MUDPLOT CUT BACKFILL HOLE
201701874901 | 2017-12-22 | LEAD | 1420 | DESIRE | N ROBERTSON | WILK | MI-LEAK AT CURB INLET SERVICE LEAK AT CURB /** 1) MN: A314522 SN: 0069806, *TAP: SIZE: A LOC: 176 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: CDM2 LOC: ON DESIRE,176.5' FROM U.R.P.L. NO. ROBERTSON ****/ | 2018-01-12 | EXCAVATED OVER A 6 INCH WATER MAIN TO FIND A 5/8 INCH ADAPTER LEAKING REMOVED AND REPLACED WITH A 5/8 INCH ADAPTER TO MAKE THE REPAIRS MADE A 8X8 BASE CUT BACKFILLED AND DRESS UP CUT
201701875101 | 2017-12-22 | LEAD | 1744 | N RAMPART | MC SHANE PL | WILK | ML METER LEAK METER # A211842 ACCOUNT # 123348-704831 INLET SERVICE LEAK BEHIND CURB COCK FLOODING GUTTER BOTTOM AND GRASS /** 1) MN: A211842 SN: 0042842, *TAP: SIZE: A LOC: 155 FEET FROM P LINE AT ST ANTHONY, *MB: CODE: BD25 LOC: ON NO. RAMPART,156.5' FROM U.R.P.L. ST. ANTHONY ****/ | 2018-03-05 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE AND A BAD 5/8 INCH 5/8 INCH METER MADE REPAIR ON INLET REPLACE 5/8 INCH METER OUTLET HAS BEEN RENEW FROM METER BOX TO PROPERTY BACKFILL JOB WITH RIVERSAND ***********OLD METER INFO********* METER:A427751 FAC:16312763 MAKE:HERSEY READ:25
201701876001 | 2017-12-23 | LEAD/PLASTIC | 726 | HAGAN AV | ORLEANS AV | WILK | ML METER LEAK METER A377305 ACCT 210625-520658 INLET SERVICE LEAK AT CURB GETTING OFF IN DCB **********D RANDOLPH 19:18********** INLET SERVICE LEAK @ THE CURB, 5 PSI @ OUTSIDE FAUCET, NO WATER IN HOME. **PER INSP W JOHNSON UPGRD TO AN ( A ) GIVE OUT. /** 1) MN: A118200 SN: 0050007, *TAP: SIZE: B LOC: 18 FEET FROM P LINE AT ORLEANS, *MB: CODE: BDC1 LOC: ON HAGAN ST. 18' FROM DIV. PL. OF ORLEANS AVE. 2' ****/ | 2017-12-31 | MADE A 4 X 4 STREET CUT EXCAVATED AND MADE REPAIRS ON A 3/4 LEAD LINE INLET LEAK IN THE STREET. REFER CUT TO PAVING PLASTIC ON THE OUTLET JOB COMPLETE JEG
201701879401 | 2017-12-24 | LEAD | 330 | VIRGINIA |  | WILK | INLET SERVICE LEAK /** 1) MN: A154140 SN: 0090499, *TAP: SIZE: B LOC: 111 FEET FROM P LINE AT CONTI, *MB: CODE: ADK LOC: ****/ | 2017-12-24 | EXCAVATED IN MUDPLOT ON INLET LEAK MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVER SAND
201701880601 | 2017-12-26 | LEAD/PLASTIC | 3607 | MAGAZINE | FOUCHER | WOLK | MI- CUT SERVICE CUT BY LOU'S PUMBING 11 ELM ST GRETNA, LA 70053 CHANGED FROM 2607 MAGAZINE **********DAMAGE CLAIM********** D RANDOLPH 12:21 *****CUSTOMER OUT OF WATER***** CUT OUTLET SERVICE BY LOU'S PLUMBING /** 1) MN: A154568 SN: 0016351, *TAP: SIZE: A LOC: 109 FEET FROM P LINE AT MAGAZINE, *MB: CODE: BFH2 LOC: SIDE BY DRIVE INSIDE 109FT FROM SPL MAGAZINE ****/ | 2017-12-26 | HAD TO MAKE 5 X5 DRIVEWAY CUT TO FIX OUTLET SERVICE LINE WAS HIT BY THE CONTRACTOR. FOUND LEAD ON INLET. NEED TO TAKE THE LEAD ON A LATER DAY. JEG
201701881601 | 2017-12-26 | LEAD/PLASTIC | 2158 | HOLIDAY DR | COPERNICUS | WOLK | ML- METER LEAK 'METER#A181137 ACCT#234098-408982 OUTLET SERVICE LEAK, FLOODING SIDEWALK /** 1) MN: A181137 SN: 0155687, *TAP: SIZE: B LOC: 47 FEET FROM P LINE AT COPERNICUS, *MB: CODE: ADL LOC: ON HOLIDAY DR., 47' FROM P.L. COPERNICUS, 10' OUT- ****/ | 2018-01-04 | EXAMINED METER EXCAVATED METER EXCAVATED TO PROPERTY NO LEAK OBSERVED METER NOT RESGESTERING BROKE METER IS IN WORKING ORDER
201701883301 | 2017-12-27 | LEAD | 1117 | MUSIC | MARAIS | WMTLK | ML- METER LEAK MN:A402325 ACCT#125923-481397 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: A225821 SN: 0048718, *TAP: SIZE: A LOC: 78 FEET FROM P LINE AT MARAIS, *MB: CODE: CEL LOC: ON MUSIC ST 78' FROM LRPL MARAIS ****/ | 2018-03-05 | REPLCAED 5/8 INCH HAND WHEEL IN MUD PLOT BACKFILL
201701883601 | 2017-12-27 | LEAD/PLASTIC | 8325 | SPRUCE |  | WILK | MI- LEAK BETWEEN S/WALK & STREET. INLET SERVICE LEAK ON PLASTIC WATER LINE, HOLE EXPOSED 03/23/18 CUSTOMER NOW OUT OF WATE PER INSPC C PLAINS, UPGRADE AND GIVE OUT ****D.RANDOLPH @ 12:55PM**** /** 1) MN: A285535 SN: 0039425, *TAP: SIZE: A LOC: 200 FEET FROM P LINE AT DANTE, *MB: CODE: CDL LOC: ON SPRUCE,100' FROM L.P.L. CAMBRONNE ****/ | 2018-03-23 | EXCAVATED AND MADE REPAIRS ON A 5/8 INLET SERVICE LEAK . LEAD LINE IN TREE ROOTS PLASTIC OUTLET JOB COMPLETE. JEG
201701883901 | 2017-12-27 | LEAD | 4733 | DEMONTLUZIN | CARNOT | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A293198 SN: 0082643, *TAP: SIZE: A LOC: 228 FEET FROM P LINE AT CARNOT, *MB: CODE: CDM1 LOC: ON DEMONTLUZIN,228' FROM L.S.P.L. CARNOT ****/ | 2018-01-25 | EXAMINE LOCATION FOUND METER COCK LEAKING EXCAVATED DOWN ON INLET SERVICE IN TREE ROOTS BY HAND FOUND LEAD SERVICE MADE REPAIRS BY REPLACING COCK WASHERS COVER BACKFILLED
201701884001 | 2017-12-27 | LEAD/PLASTIC | 4968 | DEMONTLUZIN | SELMA | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A222063 SN: 0087971, *TAP: SIZE: A LOC: 516 FEET FROM P LINE AT MIRABEAU AVE, *MB: CODE: ADK3 LOC: ON DEMONTLUZIN, 517.5' FROM P.L. MIRABEAU AVE., ****/ | 2018-01-25 | EXAMINE LACATION FOUND METER COCK LEAKING & METER WAS BELOW GRADE EXCAVATED DOWN ON INLET & OUTET SERVICES FOUND LEAD SERVICES MADE REPAIRS BY REPLACING COCK WASHERS HANDWHEEL BOTTOM & OUTLET SERVICE FROM METER TO PROPERTY ALSO RAISED METER TO GRADE BACKFILLED DRESS UP
201701884401 | 2017-12-27 | LEAD/PLASTIC | 4670 | MARIGNY | CARNOT | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A151204 SN: 0089525, *TAP: SIZE: A LOC: 66 FEET FROM P LINE AT CARNOT, *MB: CODE: BLN LOC: 66' P.L. CARNOT 9' OUTSIDE P/L ****/ | 2018-03-25 | EXCAVATED A 6 X 6 MUDPLOT CUT TO REPAIR INLET SERVICE LEAK RAISED METERBOX TO GRADE AND RENEW OUTLET SERVICE FROM METERBOX TO P.L. FOUND LEAD ON INLET SERVICE. JEG
201701885401 | 2017-12-27 | LEAD | 437 | S LOPEZ | BAUDIN | WILK | ML-METER LEAK ACCOUTN #184386-532541 METER #A391305 INLET SERVICE LEAK IN BOX /** 1) MN: A325498 SN: 0041200, *TAP: SIZE: A LOC: 81 FEET FROM P LINE AT LOPEZ S, *MB: CODE: AFHK LOC: ON BAUDIN 76FT FROM S LOPEZ 3' OUTSIDE PL 10' INS ****/ | 2018-03-02 | EXCAVTED 3 X 3 DRIVEWAY CUT RENEWED OUTLET TO PROPERTY AND RAISED THE METER BOX UP TO GRADE BACKFILLED AND CLEAQNED THE AREA
201701890903 | 2018-01-26 | LEAD | 6011 | WRIGHT RD |  | WRMS | RELOCATE EXISING SERVICE TO MUD PLOT PER MOSES ASAP /** 1) MN: C021293 SN: 0159233, *TAP: SIZE: C LOC: 685 FEET FROM P LINE AT I-10 SERVICE RD, *MB: CODE: ADK2 LOC: RES RES ON WRIGHT HPL CORNER OF HOUSE 2'FRM CRB ****/ /** 1) MN: C021293 SN: 0159233, *TAP: SIZE: C LOC: 685 FEET FROM P LINE AT I-10 SERVICE RD, *MB: CODE: ADK2 LOC: RES RES ON WRIGHT HPL CORNER OF HOUSE 2'FRM CRB ****/ | 2018-01-28 | EXCAVATED 3 X 3 MUD PLOT RELOCATED METER FROM ALREADY EXPOSED DRIVEWAY TO MUD PLOT LEFT WHIP FOR CUSTOMER TO TIE INTO BACKFILLED AND CLEANED THE AREA
201701892901 | 2017-12-29 | LEAD | 2928 | PALMER AV | S PRIEUR | WOLK | ACCT# 136376-567065 METER# A391825 CONSTANT REGISTRATION PLEASE REPAIR. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ DOTTIE READY 1-4-18 EXP 1-24-18 | 2018-01-29 | EXAMINE JOB AND FOUND OUTLET LEAKING ,EXCAVATED IN MUDPLOT ON 4 X 4 CUT AND MADE REPAIRS ON OUTLET HANDWHEEL.BACKFILL JOB WITH RIVERSAND AND LEFT JOB COMPLETE,ALSO TIED ON TO LEAD .
201701896201 | 2017-12-29 | LEAD | 1531 | LEDA CT | ESPLANADE AV | WILK | ML METER LEAK METER # A283593 ACCOUNT # 119296-535717 EXAMINE INLET SERVICE FOR LEAK IN BOX 03/24/18 LEAK GETTING WORSE (NLD) /** 1) MN: A283593 SN: 0031620, *TAP: SIZE: A LOC: 120 FEET FROM P LINE AT LEDA CT, *MB: CODE: BF LOC: 120FT FROM USPL PRIVATE ****/ | 2018-04-18 | EXCAVATED MUD PLOT REPLACED 5/8 INCH METER BOX COCK AND RENEWED OUTLET SERVICE LINE TOPROPERTY BACKFILLED AND CLEANED THE AREA
201701897801 | 2017-12-29 | LEAD | 5942 | STRATFORD PL | WESTCHESTER PL | WILK | ML- METER LEAK METER#B038786 ACCT#228892-418382 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: B028483 SN: 0125136, *TAP: SIZE: B LOC: 65 FEET FROM P LINE AT WESTCHESTER, *MB: CODE: ADLM LOC: ON STRATFORD PL 63FT FROM P.L. WESTCHESTER 7FT OUT ****/ | 2018-03-03 | EXCAVATED THROUGH TREE ROOTS AND REPAIR LEAK ON THE INLET SERVICE THEN WE BACKFILL AND CLEAN UP JOB SITE
201701898001 | 2017-12-29 | LEAD/PLASTIC | 6216 | ANNUNCIATION |  | WILK | METER # A362939 SEE WHY NO WATER ******CUSTOMER OUT OF WATER******* J CLARK @ 18:54PM DRY INLET /** 1) MN: A256293 SN: 0042105, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT HENRY CLAY AVE, *MB: CODE: AFK2 LOC: ON ANNUNCIATION ST 113' FROM UPL HENRY CLAY AVE ****/ | 2017-12-29 | EXCAVATED IN CONCRETE DRIVERWAY REPAIR 3/4 LEAD LINE DRESS UP WITH RIVERSAND & COLDMILL ENTERGY WHEN THROUGHT THE WATER LINE & BROKE IT ALSO RESET 5/8 METER A405882 REF TO ZONE 3 TO TAKE LEAD LINE OUT ALSO REF TO PAVE 4*4 CONCRETE D/W CUT,,, OLD METER A362939 FACT: 70690648 MAKE:SENSUS READ:7638
201701898301 | 2017-12-29 | LEAD | 2016 | DESLONDE | N GALVEZ | WILK | MI -LEAK IN STREET & GRASSY AREA ACROSS FROM 2016 DESLONDE INLET SERVICE LEAK AT VACANT LOT ACROSS FROM ADDRESS /** 1) MN: A217998 SN: 0126912, *TAP: SIZE: A LOC: 141 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CDM2 LOC: RES ON DESLONDE 140FT P.L. N.JOHNSON 8' OUTSIDE ****/ | 2018-03-20 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 ABANDON INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201701898901 | 2017-12-30 | LEAD/PLASTIC | 542 | HUNTLEE DR | VIVIAN CT | WILK | ML-METER LEAK INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A133341 SN: 0118373, *TAP: SIZE: A LOC: 121 FEET FROM P LINE AT VIVIAN CT, *MB: CODE: BFK LOC: ON HUNTLEE DR., 121' FROM P.L. VIVIAN CT., 4' OUT- ****/ | 2018-02-01 | EXCAVATED METER AND INSTALLED METER BOX COMPLETE AND RAISED TO GRADE
201701899301 | 2017-12-30 | LEAD/PLASTIC | 3815 | PIN OAK AV | TALL TIMBERS DR | WILK | ML-METER LEAK INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A323546 SN: 0148346, *TAP: SIZE: B LOC: 392 FEET FROM P LINE AT TALL TIMBERS DR, *MB: CODE: DM LOC: ON PIN OAK 30FT FROM TALL TIMBERS ****/ | 2018-03-29 | EXCAVATED METER BOX AND CHANGED HAND WHEEL
201800000301 | 2018-01-01 | LEAD/PLASTIC | 1016 | LEBOUEF | NEWTON | WILK | ML- METER LEAK METER# A353287 ACCT# 225219-404084 INLET SERVICE LEAK IN MUDPLOT CARS ROLLING OVER METER /** 1) MN: A260464 SN: 0135284, *TAP: SIZE: B LOC: 145 FEET FROM P LINE AT NEWTON, *MB: CODE: CD LOC: ON LEBOUEF 1145FT FROM NEWTON ****/ | 2018-02-25 | EXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOB SITE
201800007901 | 2018-01-02 | LEAD | 712 | ROYAL |  | WILK | ML- METER LEAK ACCT# 168790-528087 MTR# C020664 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: C020664 SN: 0023675, *TAP: SIZE: C LOC: 74 FEET FROM P LINE AT ROYAL, *MB: CODE: AEHN LOC: ON ORLEANS AVE 75' FROM PL ROYAL 2' OUTSIDE PL ****/ | 2018-03-22 | REPLACED 3/4 INCH HANDWHEEL IN METER BOX
201800008601 | 2018-01-03 | LEAD/PLASTIC | 17 | NEWCOMB BL | FRERET | WILK | ML METER LEAK METER# B031087 ACCT# 140685-585027 **PLEASE CONTACT UPON ARRIVAL** INLET SERVICE LEAK BEHIND CURB COCK /** 1) MN: B031087 SN: 0072322, *TAP: SIZE: B LOC: 661 FEET FROM P LINE AT ST CHARLES AVE, *MB: CODE: BGX LOC: ON LELAND 661FT FROM ST CHARLES ( YARD BY SWING ) ****/ DOTTIE READY 2-15-18 EXP 3-7-18 | 2018-05-27 | EXACAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 INLET SERVICE BACKFILLED AREA
201800009401 | 2018-01-03 | LEAD/PLASTIC | 3461 | VESPASIAN BL | CYPRESS | WOLK | ML- METER LEAK METER# A389416 ACCT# 235781-407119 OUTLET SERVICE LEAK IN THE SIDEWALK ( B ) LEAVE IN SYSTEM /** 1) MN: A133315 SN: 0163624, *TAP: SIZE: B LOC: 162 FEET FROM P LINE AT CYPRESS ACRES DR, *MB: CODE: __ LOC: ON VESPASIAN 162FT FROM PL CYPRESS ACRES ****/ | 2018-01-08 | EXAMINE OUTLET LINE FOUND A LEAK REPAIRED LEAK BY USING 3/4 COLLAR 3/4 PLASTIC TO 3/4 WAQTER LINE 1FT
201800010701 | 2018-01-03 | LEAD/PLASTIC | 2254 | MADRID |  | WOLK | UNABLE TO SET METER. INLET AND OUTLET NEEDS REPAIR. PLEASE REPAIR AND SET 5/8 METER. CUSTOMER IS HOME WAITING ON WATER PER INSPECTOR M. FRAZIER LOCATE, RAISE TO GRADE, REPAIR INLET AND OUTLET, SLAO SET 5/8 METER, UNDER CONSTRUCTION /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-03-06 | EXAMINED AND FOUND FILLER PIECE ON THE 5/8" METER BOX COCK EXCAVATED A 4 X 4 MUD PLOT CUT RAISE METER BOX TO GRADE SET A 5/8 WATER METER , AND RENEW OUTLET SERVICE FOUND LEAD PIPE ON INLET SERVICE JOB CONT- REPLACE LEAD SERVICE ON INLET
201800014301 | 2018-01-03 | LEAD | 523 | CAFFIN AV | CHARTRES | WILK | ML- METER LEAK METER# A306618 ACCT# 166587-425569 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A343403 SN: 0107874, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT CHARTRES, *MB: CODE: AF LOC: ON CAFFIN AVE 93FT FROM PL OF CHARTRES 1.5FT OUT- ****/ | 2018-03-19 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201800017001 | 2018-01-03 | LEAD/PLASTIC | 105 | FAIRFAX PL | WOODLAND DR | WMTLK | WM LEAK BETWEEN STREET & SIDEWALK EXAMINE INLET/OUTLET SERVICE FOR LEAK ON SIDEWALK FLOODING SIDEWALK /** 1) MN: A287228 SN: 0114865, *TAP: SIZE: A LOC: 244 FEET FROM P LINE AT WOODLAND, *MB: CODE: ADKL LOC: ON FAIRFAX 244' FROM PL WOODLAND 7' OUTSIDE PL 4' ****/ | 2018-01-11 | EXAMINED METER EXCAVATED METER REPAIRED LEAK BACKFILLED WITH SAND
201800018801 | 2018-01-04 | LEAD | 1674 | JEFFERSON AV | DANNEEL | WOLK | MI- LEAK IN THE STREET EXAMINE OUTLET SERVICE FOR LEAK @ PROPERTY LINE IN GRASS FLOODING SIDEWALK AND GRASS 01/13/18LEAK IS GETTING WORSE CALLER STATES HUS WIFE IS HANDICAP AND CAN NOT GET IN OR OUT OF HOME (KSW) /** 1) MN: A302257 SN: 0006935, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT DANNEEL, *MB: CODE: CDLN LOC: ON JEFFERSON AVE., 75' FROM U.R.P.L. DANNEEL ****/ DOTTIE READY 1-9-18 EXP 1-29-18 | 2018-01-18 | EXAMINED JOB FOUND ALREADY COMPLETED FOUND WASHER LEAK REPLACE 5/8 INCH WASHER TO STOP LEAK
201800019401 | 2018-01-04 | LEAD/PLASTIC | 4321 | BANKS | S HENNESSEY | WILK | MI- LEAK ON THE SIDEWALK CHNGED FROM 4319 BANKS INLET SERVICE LEAK IN THE SIDEWALK FLOODING SIDEWALK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-02-07 | EXCAVATED IN MUDPLOT WITH TREE ROOTS AROUND 5/8" METER BOX , MADE REPAIRS ON INLET SERVICE . ALSO RAISED METER BOX TO GRADE AND RENEWED OUTLET SERVICE FROM LEAD TO PLASTIC . CLEANED AND DRESSED UP AREA FOUND LEAD ON INLET SERVICE .
201800021101 | 2018-01-04 | LEAD | 4929 | IBERVILLE |  | WILK | ML- METER LEAK MTR.# A 294506 ACCT.# 126895-431239 INLET SERVICE LEAK IN METER BOX /** 1) MN: SN: 0079494, *TAP: SIZE: B LOC: 231 FEET FROM P LINE AT ST ANTHONY, *MB: CODE: CD LOC: ON IBERVILLE ST 230' FROM PL ST ANTHONY ST ****/ | 2018-03-07 | EXCAVATED IN GRAVEL / MUDPLOT OVER A 5/8" INLET SERVICE LEAK ABANDON AFTEER MOVING A PACK VEHICLE CHANGED THE COCK SEALED THE LEAK BACKFILLED AND DRESS UP WITH RIVER SAND AND COLD MILL
201800021601 | 2018-01-04 | LEAD | 1329 | MANDEVILLE | URQUHART | WILK | **********PICK UP********** INLET SERVICE LEAK IN METER BOX /** 1) MN: SN: 0046079, *TAP: SIZE: A LOC: 113 FEET FROM P LINE AT VILLERE N, *MB: CODE: BE2 LOC: ON MANDEVILLE ST 111' FROM LRPL N VILLERE ****/ | 2018-01-29 | EXCAVATED 4 X 4 CONCRETE SIDEWALK FOUND LEAK ON ABANDON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND JOB WITH RIVERSAND /COLDMILL
201800022202 | 2018-01-25 | LEAD | 2726 | BANKS | S BROAD | WOLK | EXAMINED JOB FOUND LEAK ON WATER MAIN REFER BACK ZONE 4 /** 1) MN: A333838 SN: 0016730, *TAP: SIZE: A LOC: 207 FEET FROM P LINE AT BROAD N, *MB: CODE: BFM LOC: METER ON BANKS 206.6 FT FROM PL N BROAD ****/ | 2018-01-27 | EXCAVATED AND REPLACED 10 FT OF 2 INCH CONTROLLING LINE [FOUND 5 2'' REPAIR CLAMPS] (RICHARD SMITH EXPERINCE AND MONEY MADE THIS REPAIR POSSIBLE) 5X10 DRIVEWAT CUT-->BACKFILLED==> NEED PAVING
201800023801 | 2018-01-04 | LEAD | 4024 | N ROBERTSON | MAZANT | WILK | ML- METER LEAK METER# A427164 ACCT# 303748-432687 ( PLEASE CALL UPON ARRIVAL (504) 9576383) INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A309646 SN: 0075206, *TAP: SIZE: B LOC: 178 FEET FROM P LINE AT BARTHOLOMEW, *MB: CODE: CDL1 LOC: ON N ROBERTSON ST 184' FROM PL BARTHOLOMEW ****/ | 2018-01-25 | /EXCAVATED 3 X 2 GUTTER BOTTOM AND 5 X 3 MUD PLOT RELOCATED METER BOX FROM GUTTER BOTTOM TO MUD PLOT CLOSE TO PROPERTY OUTLET WAS RENEWED AND RAISED TO GRADE
201800024401 | 2018-01-04 | LEAD | 1980 | N ROCHEBLAVE | ALLEN | WILK | ML- METER LEAK MTR# A 426457 ACCT# 156919-495566 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A284414 SN: 0092804, *TAP: SIZE: A LOC: 57 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BD LOC: ON ALLEN, 57' FROM P.L. NO. ROCHEBLAVE,9' OUTSIDE ****/ | 2018-01-25 | EXCAVATED 3 X 3 GUTTER TO FOUND METER BOX BURIED UNDER MUD RELOCATED METER TO EXPOSED SIDEWALK OUTLET SERVICE RENEWED TO PROPERTY BACKFILL AND CLEANED THE AREA
201800024901 | 2018-01-04 | LEAD/PLASTIC | 8320 | GREEN | DANTE | WILK | MI- LEAK IN SIDEWALK INLET SERVICE LEAK AT SIDEWALK /** 1) MN: A279035 SN: 0046164, *TAP: SIZE: B LOC: 137 FEET FROM P LINE AT DANTE, *MB: CODE: OOO LOC: ON GREEN 137FT FROM PL CAMBRONNE 8FT OUTSD PL ****/ | 2018-03-11 | EXCAVATED IN MUD PLOT. REPAIR 5/8 STOP AND WASTE LEAD LINE. DRESS UP WITH RIVERSAND.
201800029801 | 2018-01-05 | LEAD | 601 | N CLAIBORNE AV | LAFITTE | WMTLK | ML METER LEAK METER# C031245 ACCT# 220551-526812 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-01-28 | EXCAVATED AND REPAIRED INLET SERVICE LEAK 3X5 MUD CUT-->BACKFILLED--> NO DRESS UP NEEDED
201800029901 | 2018-01-05 | LEAD | 2738 | CLEVELAND AV | S BROAD | WILK | MI METER LEAK MTR# A 407259 ACCT # 115998-701469 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: SN: 0020359, *TAP: SIZE: A LOC: 193 FEET FROM P LINE AT WHITE N, *MB: CODE: CF LOC: ON CLEVELAND 192.5FT FROM WHITE ****/ | 2018-01-24 | EXCAVATED 3 X 3 GUTTER AND 5 X 2 MUD PLOT RENEWED OUTLET SERVICE LINE TO CUSTOMER ( BLUE ) PLASTIC LINE AND RAISED METER BOX TO GRADEBACK FILLED AND CLEANED THE AREA
201800030301 | 2018-01-05 | LEAD | 2605 | ST ANN |  | WMTLK | WM- LEAK ON THE SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A311580 SN: 0031896, *TAP: SIZE: A LOC: 44 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CDL5 LOC: BET BROAD/N DORGENOIS 44' P/L N DORGENOIS 9' ****/ | 2018-01-28 | EXCAVATED IN TREE ROOTS AND REPAIRED INLET SERVICE LEAK ALSO RAISED METER BOX TO GRADE 5X7 MUD CUT-->BACKFILLED-->NO DRESS UP NEEDED
201800037301 | 2018-01-07 | LEAD/PLASTIC | 529 | PACIFIC AV | EVELINA | WILK | MI- LEAK ON THE SIDEWALK INLET SERVICE LEAK @ SIDEWALK FLOODING CURB 03/13/18 PER INSP L HEBERT UPGRD TO *****B 1ST AM***** LEAK HAS GOTTEN WORSE FLOODING STREET & SURROUNDING AREA. **NO DRAIN IN AREA*** /** 1) MN: A278368 SN: 0066715, *TAP: SIZE: A LOC: 235 FEET FROM P LINE AT ELIZA, *MB: CODE: CDM1 LOC: RES ON PACIFIC AVE 235' FROM PL ELIZA ****/ | 2018-03-14 | CLEANED METER BOX OUT AND FOUND LEAK ON INLET REPLACED WASHERS TO REPAIR LEAK
201800038201 | 2018-01-07 | LEAD/PLASTIC | 8725 | JEANNETTE | MONROE | WOLK | ***********PICKUP JOB************ OUTLET LEAK ON THE SIDEWALK FLOODING THE SIDEWALK *********1ST AM MONDAY******** /** 1) MN: A232848 SN: 0046208, *TAP: SIZE: A LOC: 123 FEET FROM P LINE AT EAGLE, *MB: CODE: ADLM LOC: ON JEANNETTE,124.5' FROM L.P.L. EAGLE ****/ | 2018-01-09 | EXCAVATED IN MUDPLOT AND TREE ROOTS MADE REPAIRS ON 5/8 INLET SERVICE MADE REPAIRS AND BACKFILLED INLET HAS LEAD AND OUTLET HAS PLASTIC . JEG
201800040301 | 2018-01-08 | LEAD | 1209 | ANNETTE |  | WMRE | LOCATION: 303813 NEW CONSTRUCTION METER BOX BURIED / LOCATE AND SET 5/8 METER LOCATE, RAISE TO GRADE AND SET 5/8 METER HOUSE UNDER RENOVATION /** 1) MN: 000000 SN: 0079620, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: BD LOC: ON ANNETTE 73FT FROM PL OF ST CLAUDE AVE ****/ | 2018-01-23 | EXCAVATED IN BRICK SIDEWALK + LOCATED 5/8 INCH METER BOX RAISED 5/8 INCH METER BOX TO GRADE + SET 5/8 INCH METER BACKFILLED + DRESSED UP AREA
201800041901 | 2018-01-08 | LEAD/PLASTIC | 3618 | BLAIR | BERKLEY DR | WMTLK | LOCATION ID# 229935 MTR# A426058 BAD LEAK/UNABLE TO RETRIEVE READING /** 1) MN: A257454 SN: 0133311, *TAP: SIZE: B LOC: 450 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: ADK LOC: 450FT FROM P.L. BERKLEY ****/ | 2018-01-10 | EXAMINED METER EXCAVATED METER RAISED METER TO GRADE REPMOVED LEAD TO PROPERTY INSTALLED METER BOX COMPLETE BACKFILLED WITH SAND CLEANED AREA LEAK REPAIRED
201800043601 | 2018-01-08 | LEAD | 522 | S JEFFERSON DAVIS PK |  | WILK | ML METER LEAK ACCOUNT #300709531204 METER #A430133 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A305340 SN: 0047775, *TAP: SIZE: A LOC: 177 FEET FROM P LINE AT BAUDIN, *MB: CODE: BFM6 LOC: ON S JEFF DAVIS PK 176' FROM PL BAUDIN ****/ | 2018-01-26 | EXCAVATED 3 X 3 MUD PLOT MADE REPAIR ON INLET SERVICE AND REPLACE 5/8 INCH METER COCK TO STOP LEAK BACKFILL AND CLEANED THE AREA
201800045201 | 2018-01-08 | LEAD/PLASTIC | 3510 | LANG | BERKLEY DR | WMTLK | WM- LEAK ON THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN BOX /** 1) MN: A251488 SN: 0135543, *TAP: SIZE: B LOC: 62 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: ADKL LOC: ON LANG, 68' FROM P.L. BERKLEY DR., 8' OUTSIDE, 4' ****/ | 2018-02-12 | EXCAVATED METER BOX AND FOUND LEAK ON HANDWHEEL REPLACED HANDWHEEL AND RUBBER WASHERS
201800045501 | 2018-01-08 | LEAD/PLASTIC | 7200 | CHEF MENTEUR HW |  | WILK | ML- METER LEAK MTR# A 426869 ACCT# 152908 436654 EXAMINE INLET SERVICE IN SIDEWALK 01/29/18 LEAK HAS GOTTEN WORSE PER SR#12829901 (AJR) /** 1) MN: A275290 SN: 0139879, *TAP: SIZE: A LOC: 33 FEET FROM P LINE AT HYDT#12, *MB: CODE: CE LOC: ON CHEF MENTEUR HWY.,33' FROM L/S HYDT.#12,2' OUT- ****/ | 2018-02-18 | CUT CONCRETE SIDEWALK AND REPAIRED 5/8 INLET SERVICE BACKFILLED AND DRESS UP JOBSITE
201800046501 | 2018-01-08 | LEAD/PLASTIC | 1770 | PACE BL |  | WMTLK | ML METER LEAK ACCOUNT #231050406352 METER #A345149 EXAMINE INLET AND OUTLET SERVICE FOR LEAK INSIDE BOX /** 1) MN: A321635 SN: 0140172, *TAP: SIZE: B LOC: 554 FEET FROM P LINE AT MAGELLAN, *MB: CODE: AD23 LOC: 556FT FROM P.L. MAGELLAN ****/ | 2018-02-02 | EXAMINED JOB FOUND LEAK ON INLET LINE AT OUTLET OF BOX COCK REPLACE CONNECTION TO METER BOX TO CORRECT PROBLEM
201800051801 | 2018-01-09 | LEAD | 1617 | GENTILLY BL | MAUREPAS | WMTLK | ML-METER LEAK ACCT#181501-491529 METER#C007266 EXAMINE INLET AND OUTLET SERVICE FOR LEAK INSIDE MANHOLE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-01-27 | MADE REPAIR ON OUTLET SERVICE LINE INSIDE MANHOLE TO STOP LEAK
201800053601 | 2018-01-09 | LEAD | 2512 | GOV NICHOLLS | N ROCHEBLAVE | WILK | ML- METER LEAK- A296610 ACCT # 121783-523826 INLET SERVICE LEAK INSIDE BOX /** 1) MN: A296610 SN: 0040227, *TAP: SIZE: A LOC: 98 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: AD LOC: INSIDE - 98' P.L. N ROCHEBLAVE ****/ | 2018-01-31 | EXCAVATED 3 X 2 MUD PLOT REPLACED 5/8 INCH COCK AND HANDWHEEL BACKFILLED AND CLEANED THE AREA
201800053901 | 2018-01-09 | LEAD | 1523 | ST FERDINAND |  | WILK | MI - LEAK ON THE SIDEWALK *********J.GILIAM @ 11:30AM************ INLET SERVICE LEAK CAUSING POOR PRESSURE /** 1) MN: SN: 0055981, *TAP: SIZE: C LOC: 163 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: CEL2 LOC: ON ST FERDINAND 163FT FROM PL N ROBERTSON ** 2) MN: SN: 0055981, *TAP: SIZE: J LOC: 32 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: E LOC: ON ST FERDINAND UNDER OVERPASS--37'FROM P.L. ****/ | 2018-01-09 | EXCAVATED 6 X 3 SIDEWALK CUT MADE REPAIR ON INLET SERVICE LINE BACKFILLED FILLED AND CLEANED THE AREA CUSTOMER HAS GOOD PRESSURE NOW
201800054401 | 2018-01-09 | LEAD/PLASTIC | 3501 | LANG | BERKLEY DR | WOLK | LOCATION#230283-415163. METER#1393848. THE METER HAS A CON REG.A S&W TEST WAS DONE AND THE METER CONTNUED TO REG. /** 1) MN: A137059 SN: 0135542, *TAP: SIZE: B LOC: 62 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: ADKM LOC: ON LANG, 60' FROM P.L. BERKLEY DR., 8' OUTSIDE, 3' ****/ | 2018-02-02 | EXAMINED JOB DISCOVERED THAT WAS A LEAK AT HAND WHEEL REPALCED HAND WHEEL AND STOP LEAK
201800057001 | 2018-01-09 | LEAD/PLASTIC | 608 | S SCOTT | D"HEMECOURT | WILK | ML METER LEAK METER# A326830 ACCT# 111560-534316 EXAMINE INLET SERVICE LEAK FOR A LEAK /** 1) MN: A221425 SN: 0013425, *TAP: SIZE: A LOC: 72 FEET FROM P LINE AT D'HEMECOURT, *MB: CODE: AF LOC: INSIDE OPP MAIL BOX 72' P.L. D'HEMECOURT ****/ | 2018-05-26 | EXCAVATED IN MUD PLOT AND MADE REPAIR ON 3/4 INLET SERVICE BACKFILLED AREA
201800057901 | 2018-01-09 | LEAD | 1827 | TUPELO | N ROMAN | WILK | MI--LEAK AT METER BOX INLET SERVICE LEAK CAUSING OVERFLOW ON SIDEWALK /** 1) MN: A219449 SN: 0126045, *TAP: SIZE: A LOC: 199 FEET FROM P LINE AT NO. ROMAN, *MB: CODE: ADKL LOC: ON TUPELO, 199' FROM P.L. NO. ROMAN, 6' OUTSIDE ****/ | 2018-01-30 | EXCAVATED 3 X 3 GUTTER BOTTOM REPLACED 5/8 METER COCK AND RENEW OUTLET SERVICELINE TO PROERTY BACKFILLED AND CLEANED THE AREA METER BOX RAISED TO GRADE ALSO
201800060501 | 2018-01-10 | LEAD/PLASTIC | 3621 | PLYMOUTH PL | BERKLEY DR | WMTLK | ML METER LEAK METER# C012713 LOCATION# 234059-415243 EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: C012713 SN: 0152897, *TAP: SIZE: C LOC: 792 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: BDK2 LOC: BET BERKLEY-GEN DE GAULLE 793'FROM PL BERKLEY ****/ | 2018-02-12 | EXAMINED METER LEAK AND FOUND LEAK ON METER BOX WASHERS REPLACED WASHERS TO STOP LEAK
201800062001 | 2018-01-10 | LEAD | 2805 | ORLEANS AV | N WHITE | WILK | ML METER LEAK METER # A332063 ACCOUNT # 129961-507099 INLET SERVICE LEAK CARS PARKING ON METER /** 1) MN: A332063 SN: 0059263, *TAP: SIZE: A LOC: 42 FEET FROM P LINE AT WHITE N, *MB: CODE: BDL LOC: ON ORLEANS AVE.,41' FROM L.S.P.L. NO. WHITE ****/ | 2018-01-31 | EXCAVATED 3 X 3 GUTTER ALSO 3X 3 MUD PLOT ON THE OTHER SIDE OF SIDEWALK RELOCATED METER BOX FROM GUTTER TO MUD PLOT RENEWED OUTLET SERVICE TO PROPERTY BACKFILLED AND CLEANED THE AREA
201800063701 | 2018-01-10 | LEAD | 3209 | LAFITTE | N LOPEZ | WMTLK | ML-METER LEAK ACCOUNT #137558-520325 METER #A412331 EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A131632 SN: 0068243, *TAP: SIZE: B LOC: 88 FEET FROM P LINE AT LOPEZ S, *MB: CODE: CDLM LOC: ON LAFITTE AVE 87.5' FROM PL N LOPEZ ****/ | 2018-02-04 | EXCAVATED 3 X 3 GUTTER ALSO 4 X 2 MUD PLOT UP TO PROPERTY RELOCATED METER FROM GUTTER TO MUD PLOT CLOSE TO PROPERTY RENEWED OUTLET SERVICE LINE ALSO BACKFILLED AND CLEANED THE AREA
201800066701 | 2018-01-11 | LEAD | 1430 | N ROCHEBLAVE | BAYOU RD | WMEX | LOCATION ID-103589 MTR-A407557 CEMENT IN MTR BOX/PLEASE REMOVED /** 1) MN: A123375 SN: 0013092, *TAP: SIZE: A LOC: 168 FEET FROM P LINE AT BAYOU RD LRPL, *MB: CODE: ADK LOC: 168' FROM LRPL BAYOU RD. ****/ | 2018-01-26 | REMOVED ALL CEMENT FROM AROUND METER
201800067701 | 2018-01-11 | LEAD | 724 | DUMAINE | ROYAL | WILK | MI LEAK IN THE STREET CHANGED FROM 716 DUMAINE INLET SERVICE LEAK IN STREET /** 1) MN: A295899 SN: 0001707, *TAP: SIZE: B LOC: 166 FEET FROM P LINE AT ROYAL, *MB: CODE: AEK5 LOC: ON DUMAINE,162' FROM U.P.L. BOURBON ****/ | 2018-06-26 | ARRIVED AT ABOVE LOCATION + FOUND NO LEAK IN STREET EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201800067901 | 2018-01-11 | LEAD/PLASTIC | 2945 | AMERICUS | MURL | WILK | ML-- METER LEAK METER # C017397 ACCT # 231246-406782 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: C017397 SN: 0141785, *TAP: SIZE: C LOC: 200 FEET FROM P LINE AT MURL, *MB: CODE: CDN1 LOC: 204FT FROM P.L. MURL ****/ | 2018-01-29 | EXAMINED JOB FOUND LEAK IN WASHER REPLACE WASHERS
201800068901 | 2018-01-11 | LEAD | 320 | S DORGENOIS | PALMYRA | WILK | ML- METER LEAK METR#A387889 ACCT# 110168-530772 INLET SERVICE LEAK IN BRICK SIDEWALK /** 1) MN: A290503 SN: 0057183, *TAP: SIZE: B LOC: 151 FEET FROM P LINE AT PALMYRA, *MB: CODE: CFM LOC: ON S DORGENOIS 151 FT FROM PL PALMYRA ****/ | 2018-03-01 | EXCAVATED IN BRICK SIDEWALK + REPLACED 3/4 INCH LEAD OUTLET SERVICE LINE FROM METER BOX TO PROPERTY BACKFILLED + DRESSED UP AREA
201800070101 | 2018-01-11 | LEAD/PLASTIC | 514 | NEWTON | VERRET | WILK | MI- LEAK AT THE SIDEWALK INLET SERVICE LEAK IN SIDEWALK /** 1) MN: A316130 SN: 0034143, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT NUNEZ, *MB: CODE: AFKL LOC: EDGE OF HOUSE 514 INSIDE SIDEWALK 3 APTS ****/ | 2018-01-29 | EXAMINED JOB FOUND LEAK IN HAND WHEEL INSTALL NEW HAND WHEEL AND REPLACED WASHERS
201800071001 | 2018-01-11 | LEAD | 4810 | DRYADES | UPPERLINE | WILK | ML METER LEAK METER # A335846 ACCOUNT # 152911-571825 INLET SERVICE LEAK /** 1) MN: A309542 SN: 0008920, *TAP: SIZE: B LOC: 54 FEET FROM P LINE AT UPPERLINE, *MB: CODE: CDO3 LOC: ON DRYADES,58' FROM P.L. UPPERLINE,7' OUTSIDE P.L. ****/ DOTTIE READY 5-8-18 EXP 5-28-18 | 2018-05-17 | ARRIVED AT THE ABOVE LOCATION MADE A 4X4 MUDPLOT CUT AROUND THE METER BOX. MADE REPAIR ON 3/4 LEAD LINE. THEN BACKFILLED AND CLEANED THE AREA . ALSO REFER TO CREW TO RENEW THE INLET FROM THE METER BOX TO THE MAIN
201800072701 | 2018-01-12 | LEAD | 1737 | WASHINGTON AV | BARONNE | WMTLK | ML- METER LEAK LOCATION # 108035 CUST # 548552 MTR # B035957 METER BOX OVERFLOWING /** 1) MN: B022311 SN: 0019566, *TAP: SIZE: B LOC: 80 FEET FROM P LINE AT WASHINGTON AVE, *MB: CODE: ADK2 LOC: SIDE ST DR ON BARONNE 90' P.L. WASHINGTON AV ****/ DOTTIE READY 4-18-18 EXP 5-8-18 | 2018-04-23 | ARRIVED ON JOB SITE FOR METER LEAK EXAMINE JOB AND FOUND METER COCK WAS LEAKING,MADE 4 X 4 CUT IN DRIVEWAY EXCAVATED IN SIDEWALK AND REPAIR ON METER BOX COCK.TIED ONTO LEAD LINE LEAD NEED TO BE REMOVED FROM WATER MAIN.BACKFILL AND DRESSED CUT UP.
201800073601 | 2018-01-12 | LEAD | 1832 | GORDON | N PRIEUR | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A318257 SN: 0139437, *TAP: SIZE: __ LOC: 270 FEET FROM P LINE AT NO. PRIEUR, *MB: CODE: BDKL LOC: ON GORDON, 270' FROM P.L. NO. PRIEUR, 7' OUTSIDE ****/ | 2018-04-22 | EXCAVATED AND REPLACED INLET SERVICE IN METER BOX 3'X3' MUD CUT -BACKHFILLED - NO DRESS - UP NEEDED
201800073901 | 2018-01-12 | LEAD | 6413 | N TONTI | DELERY | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-04-22 | EXCAVATED 4 X 4 MUD PLOT AT CURB MADE REPAIR 1 INCH SERVICE UNDERNEATH CURB TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201800074001 | 2018-01-12 | LEAD/PLASTIC | 3811 | N TEAK AV | INWOOD AV | WILK | ML METER LEAK METER# C007679 ACCT# 233663-413026 INLET SERVICE LEAK IN MUDPLOT FLOODING CURB /** 1) MN: C007679 SN: 0151097, *TAP: SIZE: C LOC: 115 FEET FROM P LINE AT PIN OAK AVE, *MB: CODE: AFK LOC: RES. 115FT FROM PL PIN OAK AVE 8' OUTSIDE PL 3' I ****/ | 2018-02-02 | EXCAVATED JOB CHANGED WASHER STOPPED LEAKING DUG UP AROUND TO MAKE SHOW THE LINE WASN,T LEAKING
201800077501 | 2018-01-12 | LEAD/PLASTIC | 4827 | DESIRE DR | MIRABEAU AV | WOLK | ML-METER LEAK ACCOUNT #170369-468855 METER #A430654 OUTLET SERVICE LEAK INSIDE METER BOX LEAKING FROM THE HANDWHEEL WITH CONSTANT REGISTRATION, ALSO EXAMINE FOR INLET ON THE MAIN IN THE STREET /** 1) MN: A143631 SN: 0112947, *TAP: SIZE: A LOC: 293 FEET FROM P LINE AT MIRABEAU AVE, *MB: CODE: BDLM LOC: ON DESIRE DR 293' FROM PL MIRABEAU AVE 7' OUTSIDE ****/ | 2018-02-17 | ARRIVED ON JOB SITE TO REPAIR AND OUTLET LEAK SO WE REPAIRED THE LEAKING OUTLET AND RENEW THE OUTLET SERVICE BACKFILLED AND DRESS UP JOB SITE
201800079201 | 2018-01-12 | LEAD | 2119 | ST ANN |  | WMRE | LOCATION ID-127000 MTR-A294784 UNABLE TO LOCATE MTR/PLEASE LOCATE AND RAISE TO GRADE LOCATE/RAISE METER TO GRADE /** 1) MN: A197226 SN: 0057529, *TAP: SIZE: A LOC: 142 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CDL1 LOC: 145FT FROM PL N JOHNSON ****/ | 2018-02-06 | METER BOX IS UP TO GRADE CUSTOMER COVER U7P METER WITH LIMESTONE IN FRONT OF HIS HOME MARKED METER BOX TOP AND SIDEWALK WITH BLUE PAINT METER IS LOCATED 2 FT OFF THE EDGE OF SIDEWALK
201800079301 | 2018-01-12 | LEAD | 1494 | MITHRA | CARTIER AV | WILK | ML - METER LEAK ACCOUNT NUMBER - 167876 - 506071 METER NUMBER - A238863 CUSTOMER STATES A DEPRESSION IS BEGINNING TO FORM INLET SERVICE LEAK ON SIDEWALK FLOODING SIDEWALK/CURB STREET 04/27/18 UPDATED TO ****1ST AM**** PER INSPECTOR.....CUSTOMER HAS 20PSI @ OUTSIDE FAUCET NLD /** 1) MN: A238863 SN: 0114008, *TAP: SIZE: A LOC: 733 FEET FROM P LINE AT CARTIER AVE, *MB: CODE: BD LOC: 733FT FROM PL CARTIER MTR ON MITHRA 8FT OUTSIDE PL ****/ | 2018-04-29 | EXCAVATED 2 X 2 DRIVEWAY CUT REPLACED 5/8 INCH HANDWHEEL TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201800079401 | 2018-01-12 | LEAD/PLASTIC | 4235 | IBERVILLE | N HENNESSEY | WILK | ML- METER LEAK METER#A325583 ACCT#114970-515684 INLET SERVICE LEAK IN MUDPLOT FLOODING CURB/STREET /** 1) MN: A301223 SN: 0017954, *TAP: SIZE: A LOC: 46 FEET FROM P LINE AT HENNESSEY N, *MB: CODE: CDL LOC: ON IBERVILLE 49FT FROM PL OF N HENNESSEY ****/ | 2018-03-07 | EXCAVATED IN MUDPLOT THOUGH DEBRIS OVER A 5/8" INLET LEAD INLET & PLASTIC OUTLET REPLACED INLET SERVICE FROM CURB TO METER BOX
201800079501 | 2018-01-12 | LEAD | 826 | N DORGENOIS | DUMAINE | WILK | ML-- METER LEAK MTR# A325191 ACCT# 108529 523221 INLET SERVICE LEAK ONSIDEWALK FLOODING SIDEWALK/STREET CURB /** 1) MN: A290615 SN: 0010215, *TAP: SIZE: B LOC: 110 FEET FROM P LINE AT DUMAINE, *MB: CODE: AENL LOC: 110' P.L. DUMAINE ****/ | 2018-02-04 | EXCAVATED 7 X 1 SIDEWALK CUT RENEWED OUTLET SERVICE LINE TO PROPERTY TO STOP LEAK BACFILLED AND CLEANED THE AREA
201800079601 | 2018-01-12 | LEAD/PLASTIC | 5830 | ABBEY DR | SHETLAND DR | WILK | MI- LEAK IN SIDEWALK NEAR INTERSECTION INLET SERVICE LEAK @ SIDEWALK /** 1) MN: A278896 SN: 0142301, *TAP: SIZE: B LOC: 30 FEET FROM P LINE AT DURBRIDGE DR, *MB: CODE: BD7 LOC: ON ABBEY 28FT FROM DURBIDGE 7FT OUTSIDE ****/ | 2018-01-31 | EXCAVATED 5/8 METER BOX IN MUD PLOT AND CHANGED 5/8 WASHERS
201800080601 | 2018-01-13 | LEAD | 2414 | ROYAL | MANDEVILLE | WILK | ML-METER LEAK INLET SERVICE LEAK IN SIDEWALK FLOODING SIDEWALK /** 1) MN: A150237 SN: 0056260, *TAP: SIZE: B LOC: 110 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: BDLM LOC: 107' P.L. MANDEVILLE ****/ | 2018-02-05 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA OUTLET SERVICE HAS BEEN REMOVED TO PROPERTY ALREADY
201800085701 | 2018-01-14 | LEAD | 1823 | BURGUNDY | ST ANTHONY | WILK | MI- LEAK IN THE STREET INLET SERVICE LEAK /** 1) MN: A190016 SN: 0039633, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT BOURBON, *MB: CODE: CFL LOC: 143' P.L. BOURBON ****/ | 2018-01-28 | EXCAVATED 5 X 5 SIDEWALK CUT REPLACE 4 FT OF LEAD TO STOP LEAK UNABLE TO REMOVE LEAD FROM THE MAIN DUE RO CAR PARKED ON JOB SITE BACKFILLED AND CLEANED THE AREA
201800086101 | 2018-01-14 | LEAD/PLASTIC | 5841 | ABBEY DR | SHETLAND DR | WILK | MI- LEAK BETWEEN SIDWALK AND CURB INLET SERVICE LEAK AT CURB /** 1) MN: C017479 SN: 0146990, *TAP: SIZE: C LOC: 40 FEET FROM P LINE AT SHETLAND DR, *MB: CODE: BD16 LOC: ON ABBEY DR., 54' FROM P.L. SHETLAND DR., 5' OUT- ****/ | 2018-01-31 | EXCAVATED IN MUD PLOT REPLACED 1INCH STOP COCK AND ADDED 1" COPPER TO COPPER AND 3FT OF 1" PLASTIC
201800089501 | 2018-01-15 | LEAD | 965 | HARDING DR | DELGADO DR | WILK | MI LEAK ON SIDEWALK AT METER INLET SERVICE LEAK IN ASPHALT STREET FLOODING STREET /** 1) MN: C020888 SN: 0079130, *TAP: SIZE: C LOC: 148 FEET FROM P LINE AT DELGADO DR, *MB: CODE: ADM6 LOC: METER ON HARDING DR 146 FT FROM PL DELGADO DR ****/ | 2018-02-03 | EXCAVATED 8 X 12 STREET CUT REPLACED 1 INCH CORPORATION CORK ON A 6 INCH WATER MAIN TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201800093601 | 2018-01-16 | LEAD | 2809 | ST CLAUDE AV | ST FERDINAND DR | WMTLK | LOCATIONID#127721-709868 METER#A409202 METERBOX OVERFLOWING /** 1) MN: A276744 SN: 0061113, *TAP: SIZE: A LOC: 84 FEET FROM P LINE AT ST FERDINAND, *MB: CODE: CDM1 LOC: ON ST CLAUDE AVE 85.5FT FROM PL OF ST FERDINAND ****/ | 2018-02-05 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201800094401 | 2018-01-16 | LEAD | 3251 | DERBY PL | DESAIX BL | WILK | ML- METER LEAK METER# A310167 ACCT# 155237-492941 INLET SERVICE LEAK CARS ROLLING OVER METER /** 1) MN: A310167 SN: 0091879, *TAP: SIZE: A LOC: 419 FEET FROM P LINE AT SALTUS, *MB: CODE: CDM1 LOC: ON DERBY PL.,491' FROM P.L. SALTUS,6' OUTSIDE P.L. ****/ | 2018-02-01 | EXCAVATED 4 X 2 MUD PLOT RELOCATE METER BOX TO SIDEWALK BACKFILLED AND CLEANED THE AREA
201800095701 | 2018-01-16 | LEAD/PLASTIC | 2901 | LAWRENCE RD | ELIZARDI BL | WOLK | ML METER LEAK ACCT# 231866-406895 METER# A421369 OUTLET SERVICE LEAK IN MUDPLOT FLOODING AREA /** 1) MN: A220787 SN: 0143959, *TAP: SIZE: B LOC: 8 FEET FROM P LINE AT ELIZARDI BLVD, *MB: CODE: BDKL LOC: 6FT FROM P.L. ELIZARDI MTR ON LAWRENCE ****/ | 2018-03-13 | ARRIVED ON JOBSITE EXAMINED METER FOUND LEAK ON OUTLET EXCAVATED BY HAND AND REPAIRED
201800096601 | 2018-01-16 | LEAD/PLASTIC | 7920 | LUCERNE | HAYNE BL | WOLK | ML METER LEAK ACCT# 171654-465435 METER# A261161 OUTLET SERVICE LEAK /** 1) MN: A261161 SN: 0137346, *TAP: SIZE: B LOC: 422 FEET FROM P LINE AT HAYNES BLVD, *MB: CODE: BG LOC: FRONT 422' P/L HAYNE BL 7' OUTSIDE 4' INSIDE CURB ****/ | 2018-03-06 | EXCAVATED IN A 4X4 MUD PLOT BY HAND, FOUND PLASTIC ON INLET AND LEAD ON OUTLET WITH 5/8 HAND WHEEL AND METER BOX BOTTOM BROKE. REPLACE 5/8 HAND WHEEL WITH 5 FT OF WATER TUBING TO PROPERTY WITH A METER BOX COMPLETE. RAISE METER TO FRADE BACKFILL WITH RIVER SAND. JOB COMPLETE.
201800097001 | 2018-01-16 | LEAD | 2521 | EADS | LAW | WILK | ML -METER LEAK MTR # A127301 ACCT # 166820-485144 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A127301 SN: 0076612, *TAP: SIZE: A LOC: 99 FEET FROM P LINE AT LAW, *MB: CODE: ADLM LOC: EDGE OF HOUSE 99FT PL LAW 8' OUTSIDE ****/ | 2018-02-14 | EXCAVTED 3 X 3 GITTER ALSO 3 X 3 MUD PLOT RENEWED OUTLET SERVICE LINE TO PROPERTY AND RELOCATED METER BOX TO MUD PLOT BACKFILLED AND CLEANED THE AREA ***********OLD METER INFO********** METER:A127301 FAC:18225705 MAKE:ROCKWELL READ:250
201800097101 | 2018-01-16 | LEAD | 4121 | EVE | S WHITE | WILK | PP POOR PRESSURE ACCOUNT #142193575959 METER #A342653 INLET SERVICE LEAK BEHIND CURB COCK MAYBE CAUSING CUSTOMER TO HAVE POOR PRESSURE. ***NO OUTSIDE FAUCET*** 020/02/18 CUSTOMER NOW OOUT OF WATER PER SR#12830624, UPGRADE TO A, GIVE OUT ***L.THOMPSON @ 10:24AM*** (AJR) 02/02/18 CUSTOMER OUT OF WATER PER INSP B BOURNES JOB GIVEN OUT TO ZONE 7 SENT TO PRINTER TO J DUNBAR @ 2029 (FCP) /** 1) MN: SN: 0073374, *TAP: SIZE: A LOC: 170 FEET FROM P LINE AT WHITE S, *MB: CODE: ADK4 LOC: ON EVE, 170' FROM P.L. SO. WHITE ****/ | 2018-02-03 | EXCAVATED 3 X 3 SIDEWALK CUT REPLACED 5/8 INCH METER COCK AND METER BACKFILLED AND CLEANED THE AREA *************OLD METER INFO******** METER:A342653 FAC:62023860 MAKE:SENSUS READ:7021
201800098701 | 2018-01-16 | LEAD/PLASTIC | 2810 | BRISTOL PL | ANSON | WOLK | ML- METER LEAKING METER# B 036899 ACCT# 228566 - 416617 CHECK OUTLET SERVICE FOR A LEAK @ PROPERTY LINE FLOODNG SIDEWALK /** 1) MN: B029280 SN: 0122542, *TAP: SIZE: B LOC: 840 FEET FROM P LINE AT ANSON, *MB: CODE: CDMN LOC: ON BRISTOL PL., 841' FROM P.L. ANSON, 9' OUTSIDE, ****/ | 2018-02-25 | EXAMINED METER LEAK OBSERVED LEAK ON PROPERTY PLOT EXCAVATED AT PROPERTY REMOVED LEAD TO PROPERTY REPLACED WITH PLASTIC BACKFILLED DRESSED WITH SAND
201800099601 | 2018-01-16 | LEAD | 3226 | BYRNE PL | PIETY | WILK | MI--LEAK IN THE EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-02-01 | EXCAVATED 4 X 8 ASPHALT STREET CUT FOUND LEAK ON 5/8 INCH INLET SERVICE IN STREET MADE REPAIRS ON INLET RELOCATED METER BOX INTO SIDEWALK RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILL JOB WITH RIVERSAND CLODMILL
201800101701 | 2018-01-16 | LEAD/PLASTIC | 2011 | VALENTINE CT | EASTER LN | WILK | ML-- METER LEAK METER # A128843 ACCT# 231288-409418 INLET SERVICE LEAK IN DRIVEWAY /** 1) MN: A128843 SN: 0140774, *TAP: SIZE: B LOC: 335 FEET FROM P LINE AT EASTER LANE, *MB: CODE: ADK2 LOC: 337FT FROM P.L. EASTER LANE ****/ | 2018-02-15 | EXCAVTED METER BOX AND MADE REPAIR ON HAND WHEEL BACKFILLED WITH RIVER SAND
201800105501 | 2018-01-17 | LEAD/PLASTIC | 5801 | ABBEY DR |  | WILK | WM-LEAK IN SIDEWALK INLET SERVICE AT CURB FLOODING AREA GETTING OFF AT DRAIN CATCH BASIN LEFT ONE (1) CONE **1ST AM** /** 1) MN: A145256 SN: 0142762, *TAP: SIZE: B LOC: 32 FEET FROM P LINE AT WOODLAND, *MB: CODE: ADM7 LOC: RES. 32' FROM DPL WOODLAND DR 3' INSIDE CURB ****/ | 2018-02-22 | BROKE THE STREET AND EXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOB SITE
201800105801 | 2018-01-18 | LEAD | 6123 | BIENVENUE | ST MAURICE | WMRE | ML METER LEAK ACCT# 119741-707453 METER# A423211 /** 1) MN: A313535 SN: 0035703, *TAP: SIZE: A LOC: 126 FEET FROM P LINE AT ST MAURICE, *MB: CODE: CF1 LOC: ON BIENVENUE 126FT FROM USPL ST MAURICE ****/ METER HAVE CONCRETE POUR OVER IT, INSIDE METER BOX. | 2018-02-04 | EXAMINED JOB AND FOUND CEMENT INSIDE METER BOX REMOVED CEMENT OUT OF METER BOX AND CLEANED INSIDE BOX
201800106801 | 2018-01-18 | LEAD | 2420 | ST CLAUDE AV | ST ROCH AV | WILK | MI-CLOSE FOR REPAIRS BROKEN OUTSIDE METER#A422131 ACCT#219002-481571 CUSTOMER STATES INSPECTOR TOLD HER TO CALL AGAIN FIRST AM **********M ROBINSON 09:38********** CURB COCK FROZEN UNABLE TO CLOSE SERVICE /** 1) MN: SN: 0041410, *TAP: SIZE: A LOC: 174 FEET FROM P LINE AT ST ROCH AVE, *MB: CODE: CDLN LOC: ON ST CLAUDE 173.4FT FROM ST ROCH ****/ | 2018-05-25 | EXCAVATED 2 X 2 MU DPLOT THROUGH ROOTS REPLACE 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA
201800109201 | 2018-01-18 | LEAD/PLASTIC | 4118 | MACARTHUR BL | HOLIDAY DR | WMTLK | ML-METER LEAK ACCT#229146-409635 METER#B034238 EXAMINE INLET & OUTLET SERVICE FOR A LEAK OVERFLOWING ON SIDEWALK /** 1) MN: B023177 SN: 0127212, *TAP: SIZE: B LOC: 141 FEET FROM P LINE AT HOLIDAY DR, *MB: CODE: BD LOC: ON MAC ARTHUR BLVD 140' FROM PL HOLIDAY DR 6' OUTI ****/ | 2018-02-20 | EXAMINED LEAKING AREA OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK CLEANED AREA
201800109501 | 2018-01-18 | LEAD | 2238 | ST CLAUDE AV |  | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A334113 SN: 0005806, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT MARIGNY, *MB: CODE: __ LOC: 45' P.L. MARIGNY ****/ | 2018-04-24 | EXCAVATED 3 X 11 SIDEWALK CUT REPLACED 5/8 INCH METER COCK AND RENEWED OUTLET SERVICE LINE TO PROPERTY BACKFILLED AND CLEANED THE AREA
201800111101 | 2018-01-18 | LEAD | 120 | N RENDON | CANAL | WILK | ML METER LEAK ACCT# 101803-519058 METER# A299459 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A299459 SN: 0014636, *TAP: SIZE: B LOC: 141 FEET FROM P LINE AT CANAL, *MB: CODE: AFO6 LOC: ON RENDON 141FT L.R.P.L. CANAL ****/ | 2018-03-23 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH HANDWHEEL LEAKING + RPAIRED IT AT PROPERTY BACKFILL
201800111901 | 2018-01-18 | LEAD | 1427 | N ROMAN | KERLEREC | WILK | MI- LEAK IN SIDEWALK ( WATER GUSHING OUT) INLET SERVICE LEAK ON SIDEWALK /** 1) MN: A251195 SN: 0015928, *TAP: SIZE: A LOC: 119 FEET FROM P LINE AT KERLEREC, *MB: CODE: AFKM LOC: ON N ROMAN 119'F ROM LSPL KERLEREC ****/ | 2018-03-07 | EXCAVATED IN MUD PLOT + REPLACED 3/4 INCH LEAD OUTLET SERVICE LINE FROM LINE FROM METER BOX TO PROPERTY INLET IS LEAD + NEED TO BE REPLACED FROM WATER MAIN TO METER BOX
201800112001 | 2018-01-18 | LEAD | 2816 | ALLEN | DUELS | WILK | ML- METER LEAK METER#A299945 ACCT#211095--704787 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A287556 SN: 0079058, *TAP: SIZE: B LOC: 99 FEET FROM P LINE AT DUELS, *MB: CODE: ADC LOC: ON ALLEN 101FT FROM DUELS 9FT OUTSIDE ****/ | 2018-03-01 | EXCAVATED IN MUD PLOT + REPLACED 3/4 INCH LEAD OUTLET SERVICE LINE FROM METER BOX TO PROPERTY BACKFILLED + DRESSED UP AREA
201800112801 | 2018-01-18 | LEAD/PLASTIC | 714 | LANG | MACARTHUR BL | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK FLOODING SIDEWALK LEFT ONE (1) CONE /** 1) MN: A237629 SN: 0115435, *TAP: SIZE: A LOC: 202 FEET FROM P LINE AT MAC ARTHUR BLVD, *MB: CODE: CFL LOC: 202FT FROM P.L. MAC ARTHUR ****/ | 2018-02-25 | BROKE THE SIDEWALK AND THE STREET AND EXCAVATED ON THE INLET SERVICE THAT COMING FROM ACROSS THE STREET AND WE REPAIR THE LEAK THEN WE BACKFILL AND CLEAN UP JOB SITE
201800113601 | 2018-01-19 | LEAD | 1473 | N VILLERE | COLUMBUS | WILK | ML-METER LEAK ACCT#122831-479464 METER#A251937 /** 1) MN: A251937 SN: 0041657, *TAP: SIZE: A LOC: 80 FEET FROM P LINE AT COLUMBUS, *MB: CODE: CDLM LOC: ON N VILLERE 80' FROM USPL COLUMBUS ST ****/ EXAMINE INLET SERVICE FOR LEAK | 2018-01-22 | EXCAVATED 9 X 3 SIDEWALK RENEWED OUTLET SERVICE LINE TO PROPERTY TO GIVE CUSTOMER WATER UNABLE TO DO A COMPLETE BACK FILLED BUT CLEANED THE AREA LEFT 2 BARRELS ON CUTFOR SAFETY
201800115301 | 2018-01-19 | LEAD | 2025-23 | S GAYOSO | FONTAINEBLEAU DR | WILK | /** AT 2023: 1) MN: A278332 SN: 0067703, *TAP: SIZE: B LOC: 141 FEET FROM P LINE AT GEN. PERSHING, *MB: CODE: BDN LOC: ON SO. GAYOSO, 140' FROM P.L. GEN. PERSHING ** 2) MN: A214452 SN: 0067703, *TAP: SIZE: A LOC: 141 FEET FROM P LINE AT VINCENT RD, *MB: CODE: BDN LOC: FIRST METER ****/ | 2018-01-18 | EXCAVATED IN THE MUD PLOT OVER 5/8 INCH METER BOX AND FOUND STOP COCK LEAKING REPLACE 5/8 INCH STOP COCK BACKFILL (ACTIVITY CODE 2333)
201800119701 | 2018-01-19 | LEAD | 2504 | ST ANTHONY | N DORGENOIS | WILK | **********PICKUP JOB********** INLET SERVICE LEAK IN MUDPLOT FLOODING SIDEWALK & CURB /** 1) MN: A225048 SN: 0176730, *TAP: SIZE: CCCC LOC: 48 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CDL LOC: 47FT FROM PL N DORGENOIS ****/ | 2018-02-05 | EXCAVATED 4 X 6 MUD PLOT AND SIDEWALK FOUND LEAK ON 5/8 INCH INLET AT THE WATERMAIN RENEW INLET FROM WATERMAN TO METER BOX RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY RELOCATED METER INTO SIDEWALK BACKFILL JOB WITH RIVERSAND COLDMILL
201800122301 | 2018-01-19 | LEAD/PLASTIC | 1619 | RIVER OAKS DR | GEN MEYER AV | WOLK | ML METER LEAK ACCT# 228476-416508 METER# A245667 EXAMINE OUTLET SERVICE AT PROPERTY LINE FOR LEAK SIDEWALK FLOODING LEFT ONE (1) CONE /** 1) MN: A245667 SN: 0121446, *TAP: SIZE: B LOC: 153 FEET FROM P LINE AT PATTERSON DR, *MB: CODE: ADM LOC: ON RIVER OAKS 153FT FROM PATTERSON 11FT OUTSIDE ****/ | 2018-02-27 | EXAMINEG LEAKING AREA EXCAVATED METER BOX OBSERVED LEAK ON OUTLET SIDE REPAIRED LEAK BACKFILLED CLEANED AREA
201800122601 | 2018-01-19 | LEAD | 717 | COMMON | ST CHARLES AV | WMLK | WM- LEAK IN THE STREET LEAK ON MAIN FLOODING AREA GETTING OFF INTO DRAIN CATCH BASIN **1ST AM** /** 1) MN: 000000 SN: 0002871, *TAP: SIZE: B LOC: 122 FEET FROM P LINE AT ST CHARLES AVE, *MB: CODE: BE LOC: ON COMMON 122FT FROM LSPL OF ST CHARLES AVE ** 2) MN: D005313 SN: 0002871, *TAP: SIZE: D LOC: 126 FEET FROM P LINE AT ST CHARLES AVE, *MB: CODE: BE LOC: ON COMMON, 126' FROM P.L. ST. CHARLES AVE., 5' OUT ****/ | 2018-04-28 | FOUND LEAK IN MANHOLE - MADE REPAIRS
201800137201 | 2018-01-20 | LEAD/PLASTIC | 1965 | CHIPPEWA | ST ANDREW | WILK | ML METER LEAK ACCT# 217635-544420 METER# A426603 INLET SERIVE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-02-24 | EXCAVATED AND MADE REPAIR ON 3/4 INLET ALSO REPLACED 3/4 OUTLET SERVICE MADE 4X6 MUDPLOT CUT BACKFILL HOLE
201800137401 | 2018-01-20 | LEAD | 3214 | ORLEANS AV | N RENDON | WILK | ML-METER LEAK INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A311622 SN: 0073073, *TAP: SIZE: B LOC: 117 FEET FROM P LINE AT RENDON N, *MB: CODE: __ LOC: ON ORLEANS 114FT FROM CORNER PL N RENDON ****/ | 2018-02-01 | EXCAVATED 2 X 6 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH OUTLET SERVICE RENEW OUTLET SERVICE FROM METER BOX TO PROPERTYTIE INTO 3/4 INCH PLASTIC LINE BACKFILL JOB WITH RIVERSAND COLLDMILL ALSO HAVE TO REPLACE 5/8 INCH METER AT ABOVE LOCATION... OLD METER INFO: METER:A362169 FACT:70689878 MAKE:SENSUS READ:20562
201800140201 | 2018-01-21 | LEAD | 4221 | ST CLAUDE AV | LESSEPS | WILK | MI-LEAK IN SIDEWALK INLET SERVICE LEAK IN MUDPLOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-02-16 | EXAMINED JOB FOR LEAK FOUND LEAK ON INLET EXCAVATED 2 X 4 SIDEWALK REPAIR JOB BACKFILLED AND CLEAN EDTHE AREA
201800141601 | 2018-01-21 | LEAD | 2324 | PORT | N TONTI | WILK | MI METER BOX LEAKING INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: SN: 0094115, *TAP: SIZE: A LOC: 79 FEET FROM P LINE AT TONTI N, *MB: CODE: AEL2 LOC: ON PORT 182FT FROM TONTI 7.5FT OUTSIDE P/L ****/ | 2018-02-04 | EXCAVATED /REPAIR 3/4 INCH INLET SERVICE LEAK
201800142201 | 2018-01-21 | LEAD | 3043 | MAUREPAS | N LOPEZ | WILK | ML METER LEAK ACCT# 146415-535859 METER# A231879 INLET SERVICE LEAK IN MUDPLOT FLOODING STREET/CURB /** 1) MN: A231879 SN: 0103659, *TAP: SIZE: A LOC: 334 FEET FROM P LINE AT SAUVAGE, *MB: CODE: CDL2 LOC: ON MAUREPAS 334FT FROM PL OF SAUVAGE 8FT OUTSIDE ****/ | 2018-02-02 | EXCAVATED 4 X 3 SIDEWALK CUT RENEWED OUTLET SERVICE UP TO PROPERTY RELOCATED METER BOX TO SIDEWALK BACKFILLED AND CLEANED THE AREA
201800143501 | 2018-01-21 | LEAD | 6 | YOSEMITE DR | PARK TIMBERS DR | WMLK | C Y NO WATER METER#A316741 ACCT#234387-412177 LEAK ON WATER MAIN FLOODING SIDEWALK /** 1) MN: A316741 SN: 0154534, *TAP: SIZE: B LOC: 152 FEET FROM P LINE AT PARK TIMBERS DR, *MB: CODE: BL LOC: ON YOSEMITE 133FT FROM PARK TIMBERS 10FT OUTSIDE ****/ | 2018-01-21 | EXCAVATED 6 X 3 MUD PLOT MADE REPAIR ON 1 INCH SERVICE LINE AT 8 INCH WATER MAIN REPLACE CHOKE METER WITH NEW ONE BARRICADE AREA OFF WITH BARRELS AND FLAGS FOR SAFETY REFER BACK TO ZONE 6 FOR BACKFILLED AND CLEANED UP AREA,,, JO CONTINUED OLD METER: A316741 FACT:53074624 MAKE:SENSUS READ:1304
201800145601 | 2018-01-22 | LEAD/PLASTIC | 1127 | LEBOUEF | DE ARMAS | WOLK | ML-METER LEAK ACCT#225551-403783 METER#A351835 OUTLET SERVICE LEAK IN BOX /** 1) MN: A241786 SN: 0119842, *TAP: SIZE: B LOC: 47 FEET FROM P LINE AT DE ARMAS, *MB: CODE: __ LOC: ON LEBOUEF 47'FROM P.L. DE ARMAS ****/ | 2018-02-14 | CUT METER BOX OUT OF DRIVEWAY WITH AIR GUN TO REPLACE HAND WHEEL AND OUTLET PLASTIC BAD BACKFILLED WITH RIVER SAND
201800145701 | 2018-01-22 | LEAD/PLASTIC | 359 | 39TH | FLEUR DE LIS DR | WILK | ML-METER LEAK ACCT#194524-599346 METER#A413572 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A275710 SN: 0134740, *TAP: SIZE: B LOC: 385 FEET FROM P LINE AT BELLAIRE DR, *MB: CODE: BDM2 LOC: ON 39TH 386' FROM PL BELLAIRE DR 7' OUTSIDE PL 10' ****/ | 2018-05-19 | EXCAVATED REPAIRED INLET AND FOUND LEAD ON INLET PLASTIC ON OUTLET AND FIXED
201800148101 | 2018-01-22 | LEAD/PLASTIC | 183 | PINEWOOD CT | CYPRESS ACRES DR | WOLK | WM - LEAK IN THE STREET OUTLET SERVICE LEAK IN MUDPLOT /** 1) MN: A128359 SN: 0164635, *TAP: SIZE: A LOC: 7 FEET FROM P LINE AT CYPRESS ACRES DR, *MB: CODE: OOO LOC: ON PINEWOOD 25FT FROM PL CYPRESS ACRES 9FT OUTS ****/ | 2018-02-24 | EXAMINED LEAKING AREA EXCAVATED INLET AND OUTLET LEFT SERVICE OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK BACKFILLED DRESSED UP WITH SAND
201800148201 | 2018-01-22 | LEAD/PLASTIC | 4177 | DUMAINE |  | WILK | ML METER LEAK ACCOUNT #115256-515120 METER #A281408 INLET SERVICE LEAK /** 1) MN: A328111 SN: 0019586, *TAP: SIZE: B LOC: 120 FEET FROM P LINE AT SOLOMON N, *MB: CODE: CDLM LOC: 116' P.L. N SOLOMON ****/ | 2018-02-20 | EXCAVATED IN MUDPOT WITH TREE ROOTS AROUND 5/8 METERBOX , MADE REPAIRS ON INLET SERVICE ALSO RAISED METERBOX TO GRADE AND RENEWED OUTLET SERVICE FROM LEAD TO PLASTIC,CLEANED AND DRESSED UP AREA FOUND LEAD ON INLET SERVICE. JEG
201800149101 | 2018-01-22 | LEAD/PLASTIC | 2840 | KENT DR | GEN MEYER AV | WILK | WM LEAK BETWEEN CURB AND STREET EXAMINE INLET SERVICE FOR LEAK BETWEEN CURB AND STREET /** 1) MN: A274544 SN: 0150777, *TAP: SIZE: B LOC: 242 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: CDN6 LOC: ON KENT 29FT FORM GEN MEYER 4.5FT INSIDE ****/ | 2018-02-25 | BROKE THE DRIVEWAY AND WXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOB SITE THE LEAK WAS ON THE HOUSE ACROSS THE STREET AT 2840 KENT DR
201800150001 | 2018-01-22 | LEAD | 3711 | BARONNE |  | WILK | ML- METER LEAK METER# A328919 ACCT # 117535-712838 INLET SERVICE LEAKING BEHIND CURB COCK /** 1) MN: A180888 SN: 0025199, *TAP: SIZE: A LOC: 69 FEET FROM P LINE AT AMELIA, *MB: CODE: BEK2 LOC: ON BARONNE 69FT FROM AMELIA ****/ | 2018-01-30 | EXAMINE JOB PUMP WATER OUT METR BOX AND FOUND THAT THE METER COCK WAS LEAKING AND EXCAVATED IN 4 X 4 MUDPLOT AND MADE REPAIRS TO BAD METER COCK.TIED COCK BACK ON TO LEAD LINE AND THEN BACKFILLED JOB WITH MUD.
201800151801 | 2018-01-22 | LEAD | 4310 | N RAMPART |  | WILK | ML-- METER LEAK METER # A263443 ACCT # 145658-428957 INLET SERVICE LEAK INSIDE BOX FOUND OFF LEFT OFF /** 1) MN: A263443 SN: 0077362, *TAP: SIZE: A LOC: 69 FEET FROM P LINE AT LESSEPS, *MB: CODE: CEL LOC: ON N RAMPART 85.7FT FROM PL OF LESSEPS ****/ | 2018-02-03 | EXCAVATED REPAIRED INLET SERVICE LEAK 4X4 SIDEWALK CUT-->BACKFILLED-->NEED PAVING
201800152901 | 2018-01-22 | LEAD/PLASTIC | 925 | ST ANDREW | CONSTANCE | WLPR | PP- POOR PRESSURE ACCT# 146126-543723 METER# A389377 EXAMINE INLET FOR POOR PRESSURE /** 1) MN: A309711 SN: 0048349, *TAP: SIZE: A LOC: 207 FEET FROM P LINE AT LAUREL, *MB: CODE: CDN1 LOC: ON ST ANDREW 194FT FROM LAUREL ****/ | 2018-02-24 | EXCAVATED AND REPLACED 3/4 OUTLET SERVICE MADE 4X5 SIDEWALK CUT BACKFILL HOLE
201800153501 | 2018-01-22 | LEAD/PLASTIC | 1614 | FARRAGUT | LAWRENCE ST | WILK | ML-METER LEAK METER#A250528 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A250528 SN: 0117974, *TAP: SIZE: B LOC: 126 FEET FROM P LINE AT LAWRENCE, *MB: CODE: ADN1 LOC: ON FARRAGUT 126' FROM PL LAWRENCE 7' OUTSIDE PL ****/ | 2018-02-21 | EXCAVATED METER REMOVED LEAD REPLACED WITH PLASTIC PLACE METER COMPLETE IN WITH NEW METER BACKFILLED WITH SAND **************OLD METER INFO*********88 METER:A250528 FAC:35452994 MAKE:ROCKWELL READ:3945
201800157301 | 2018-01-23 | LEAD | N/A | FLORIDA AV | CONGRESS | WMLK | MI- LEAK IN THE STREET LEAK ON THE MAIN @ INTESECTION, AREA UNDER CONSTRUCTION /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-04-28 | EXCAVATED AND REPAIRED 1 INCH INLET SERVICE LEAK AT CURB THIS IS A CONTROLLING LINE
201800157401 | 2018-01-23 | LEAD | 3135 | N VILLERE | CLOUET | WILK | ML- METER LEAK ACCT#134066-505208 METER#A332931 INLET SERVICE LEAK ON SIDEWALK FLOODING SIDEWALK 03/29/18 PER S/R 12836791 METER LEAK (KSW) /** 1) MN: A261117 SN: 0065836, *TAP: SIZE: A LOC: 275 FEET FROM P LINE AT CLOUET, *MB: CODE: CDEL LOC: 275' P.L. CLOUET ****/ | 2018-04-24 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND CLDMILL
201800160701 | 2018-01-23 | LEAD | 1510 | MUSIC | N ROBERTSON | WOLK | MI CUT SERVICE UNKNOWN IF CUSTOMER WITHOUT WATER CUT BY C W UNDERGROUND UTILITIES 281-541-1391 ***********DAMAGE CLAIM********** (J.GILLIAM @ 13:06PM) CHANGED FROM 1500 MUSIC CUT OUTLET SERVICE AND CRUSHED METER BOX CUSTOMER OUT OF WATER BY C W UNDERGROUND /** 1) MN: A234436 SN: 0014178, *TAP: SIZE: A LOC: 107 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: ADKN LOC: 107' P.L. N ROBERTSON ****/ | 2018-01-23 | FOUND INLET SERVICE EXPOSED BY CONTRACTOR EXCAVATED 12 X 1 MUD PLOT RENEWED INLET SERVICE LINE FROM WHERE DAMAGE CAUSE BY CONTRACTOR TO METER BOX FORCE ACCOUNT TO C + W UNDERGROUND
201800160801 | 2018-01-23 | LEAD | 3105 | ST PHILIP | N LOPEZ | WILK | ML-METER LEAK ACCT# 125207-521622 METER# A295980 INLET SERVICE LEAK /** 1) MN: A295980 SN: 0054501, *TAP: SIZE: B LOC: 50 FEET FROM P LINE AT LOPEZ N, *MB: CODE: __ LOC: ON ST PHILIP 57.5FT FROM PL OF N LOPEZ ****/ | 2018-02-06 | EXCAVATED 2 X 2 GUTTER THROUGH TREE AND 3 X 1 AT PROPERTY RENEWED OUTLET SERVICE LINE TO PROPERTY AND REPLACED 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA
201800161301 | 2018-01-23 | LEAD | 2713 | N ROMAN |  | WILK | ML METER LEAK ACCOUNT #156234-403759 METER #A340776 INLET SERVICE LEAK @ SIDEWALK, FLOODING SIDEALK /** 1) MN: A340776 SN: 0162809, *TAP: SIZE: A LOC: 103 FEET FROM P LINE AT PORT, *MB: CODE: BDLM LOC: ON ROMAN 102.5FT FROM PORT 8FT OUTSIDE 2FT INSIDE ****/ | 2018-02-09 | EXCAVATED 3 X 2 SIDEWALK CUT MADE REPAIR ON INLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201800162201 | 2018-01-23 | LEAD | 900 | INDEPENDENCE | BURGUNDY | WILK | ML-METER LEAK ACCT# 106969-427613 METER#A268650 INLET SERVICE LEAK /** 1) MN: A268650 SN: 0018880, *TAP: SIZE: B LOC: 64 FEET FROM P LINE AT INDEPENDENCE, *MB: CODE: AFHK LOC: SIDE ST ON BURGUNDY 64' P.L. INDEPENDENCE ****/ | 2018-02-07 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY TIE INTO 3/4 INCH COOPER LINE BACKFILLED JOB WITH RIVERSAND COLDMILL
201800162301 | 2018-01-23 | LEAD | 3262 | DERBY PL | N SALCEDO | WILK | MI - CURB COCK IS BROKEN - PLUMBER IS UNABLE TO TURN METER OFF FROZEN CURB COCK UNABLE TO CLOSE OFF SERVICE /** 1) MN: B024020 SN: 0091645, *TAP: SIZE: B LOC: 47 FEET FROM P LINE AT SALCEDO N, *MB: CODE: ADLM LOC: ON DERBY PL.,47' FROM P.L. NO. SALCEDO, 5.5' OUT- ****/ | 2018-02-08 | REMOVED ALL OUT OF METER BOX METER BOX COCK IS NOT BROKEN
201800162801 | 2018-01-23 | LEAD | 2506 | ST ANTHONY AV | AGRICULTURE | WILK | MI- METER BOX LEAK INLET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-02-14 | EXAMINED JOB FOUND NO LEAK
201800163201 | 2018-01-23 | LEAD/PLASTIC | 3510 | DICKENS DR | BERKLEY DR | WOLK | WM LEAK IN SIDEWALK EXAMINE OUTLET SERVICE FOR LEAK @ PROPERTY LINE /** 1) MN: A314737 SN: 0149987, *TAP: SIZE: B LOC: 94 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: CDL2 LOC: 96FT FROM PL BERKLEY DR 8' OUTSIDE PL 2' INSIDE CU ****/ | 2018-02-23 | EXAMINED METER EXCAVTED INL;ET AND OUTLET SERVICE OBSERVED NO LEAK TRACED LINE TO PROPERTY REPAIRED LEAK BACKFILLED
201800163401 | 2018-01-23 | LEAD | 710 | DESIRE | ROYAL | WILK | ML-METER LEAK ACCT#144488-427984 METER#A284703 INLET SERVICE LEAK /** 1) MN: A284703 SN: 0046280, *TAP: SIZE: A LOC: 107 FEET FROM P LINE AT ROYAL, *MB: CODE: AEM5 LOC: ON DESIRE, 88' FROM P.L. ROYAL ****/ | 2018-03-02 | EXCAVATED 7 X 2 SIDEWALK CUT THUR BRICK RENEWED OUTLET SERVICE TO PROPERTY AND REPLACED 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA
201800163801 | 2018-01-23 | LEAD/PLASTIC | 2378 | ST THOMAS | 1ST | WILK | ML- METER LEAK ACCT# 279070-700308 MTR# A429374 INLET SERVICE LEAK BEHIND CURB COCK FLOODING GRASSY AREA & SIDEWALK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-02-07 | EXAMINE JOB FOUND LEAK ON WASH
201800165101 | 2018-01-23 | LEAD | 2222 | PORT | N MIRO | WILK | ML- METER LEAK METER#A257913 ACCT#157173-479483 INLET SERVICE LEAK 01/30/18 INLET SERVICE LEAK CARS ROLLING OVER METER (KSW) /** 1) MN: A151583 SN: 0094484, *TAP: SIZE: A LOC: 50 FEET FROM P LINE AT MIRO N, *MB: CODE: BEM2 LOC: 159'P/L N MIRO 8' OUTSIDE P/L 2' INSIDE CURB ** 2) MN: A328076 SN: 0094484, *TAP: SIZE: A LOC: 153 FEET FROM P LINE AT MIRO N, *MB: CODE: BEM2 LOC: 155' FROM PL. N MIRO 4' OUTSIDE PL ON PORT ****/ | 2018-03-07 | EXCAVATED 3 X 4 MUD PLOT IN SIDEWALK FOUND LEAK ON ABANDON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND COLDMILL
201800166601 | 2018-01-23 | LEAD/PLASTIC | 2901 | HOLIDAY DR | VIXEN | WMTLK | ML.- METER LEAK MTR# C023589 ACCT # 229303 408678 EXAMINE INLET/OUTLET SERVICE FOR A LEAK 01/29/18 CHECK OUTLET SERVICE FOR A LEAK @ PROPERTY LINE FLOODING SIDEWALK (KSW) /** 1) MN: C023589 SN: 0129174, *TAP: SIZE: C LOC: 205 FEET FROM P LINE AT MAC ARTHUR BLVD, *MB: CODE: C LOC: ON HOLIDAY DR., 201' FROM P.L. MAC ARTHUR BLVD., ****/ | 2018-02-20 | EXAMINED LEAKING AREA AFTER EXPOSING LINE OBSERVED LEAK AT PROPERTY FOUND LEAD AND PLASTIC ON OUT SERVICE REPLACED LINE TO PROPERTY BACKFILLED CLEANED AREA REPLACED CONE ON MUD PLOT SAND NEED FOR DRESS UP
201800166901 | 2018-01-23 | LEAD | 3333 | PALMYRA | S JEFFERSON DAVIS PK | WLPR | PP-POOR PRESSURE ACCOUNT #186500-714839 METER #A420561 EXAMINE INLET FOR POOR PRESSURE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-01-26 | FOUND METER HALF WAY OFF TURNED METER ALL THE WAY TO RESTORE PRESSURE
201800167001 | 2018-01-23 | LEAD | 2829 | GRAND RTE ST JOHN | CRETE | WILK | ML- METER LEAK MTR# A376761 ACCT# 105751 490629 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A294929 SN: 0021569, *TAP: SIZE: B LOC: 94 FEET FROM P LINE AT CRETE, *MB: CODE: ADLN LOC: CRETE AND WHITE 95FT FROM PL CRETE ****/ | 2018-03-09 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING + REPAIRED IT BACKFILLED
201800167801 | 2018-01-23 | LEAD/PLASTIC | 5645 | BRIGHTON PL | CHELSEA DR | WILK | ML- METER LEAK METER#A291438 ACCT#231952-418188 INLET SERVICE LEAK /** 1) MN: A291438 SN: 0144324, *TAP: SIZE: B LOC: 326 FEET FROM P LINE AT CHELSEA DR, *MB: CODE: CD1N LOC: 32'FROM P L CHELSEA ****/ | 2018-03-27 | EXAMINED METER EXCAVATED THROUGH ROOTS EXPOSING INLET AND OUTLET SERVICE OBSERVED LEAK ON INLET SERVICE REPLACED OLD METER CASING AND RAISED TO GRADE BACKFILLED AND CLEANED SITE
201800168101 | 2018-01-23 | LEAD/PLASTIC | 436 | DE ARMAS | NUNEZ | WILK | ML METER LEAK METER# A352402 ACCT# 228872-401658 INLET SERVICE LEAK 02/16/18 CUSTOMER STATES LEAK IS GETTING WORSE (KSW) /** 1) MN: A294452 SN: 0124751, *TAP: SIZE: __ LOC: 265 FEET FROM P LINE AT TECHE, *MB: CODE: AD LOC: ON DEARMAS 265FT FROM P.L. TECHE 10FT OUTSIDE P.L. ****/ | 2018-02-22 | EXAMINED METER EXCAVATED METER OBSERVED LEAK ON LEAD LINE REPLACE LEAD LINE WITH PLASTIC FROM MAIN 4" LINE WITH METER BOX COMPLELE AND RAISED TO GRADE BACKFILLED WITH SAND AND COAL MILL CLEANED AREA
201800168301 | 2018-01-23 | LEAD/PLASTIC | 1212 | ELIZARDI BL | GEN MEYER AV | WILK | MI METER BOX LEAKING INLET SERVICE LEAK /** 1) MN: A228708 SN: 0135456, *TAP: SIZE: B LOC: 185 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: ADLO LOC: ON ELIZARDI 185' FROM PL GEN MEYER AVE 8' OUTSIDE ****/ | 2018-02-21 | EXAMINED LEAKING METER BOX EXCAVATED METER EXPOSED INLET AND OUTLET SERVICE MADE REPAIRS TO INLET SERVICE BACKFILLED WITH SAND CLEANED AREA
201800168501 | 2018-01-23 | LEAD/PLASTIC | 1421 | SHIRLEY DR | LAWRENCE RD | WMTLK | MI- LEAK ON THE SIDEWALK EXAMINE INLET/OUTLET SERVICE @ SIDEWALK FOR A LEAK /** 1) MN: A113197 SN: 0096026, *TAP: SIZE: B LOC: 278 FEET FROM P LINE AT SOCRATES, *MB: CODE: BD5 LOC: ON SHIRLEY 4FT FROM DIV P/L SOCRATES 2FT INTSIDE ****/ | 2018-02-19 | EXCAVATED METER BOX BY HAND AND COUND LEAK ON LEAD OUTLET REMOVED LEAD AND REPLACED WITH PLASTIC WITH PLASTIC LEAD ON INLET NEED TO BE CHANGED REMOVED BACKFILLED WITH RIVER SAND
201800169801 | 2018-01-24 | LEAD/PLASTIC | 3815-17 | PERRIER |  | WILK | ML METER LEAK METER# A422620 ACCT# 116034-700553 INLET SERVICE LEAK NO METER IN BOX CURB COCK IN OFF POSITION ATR PASSING THROUGH FLOODNG SIDEWALK /** AT 3815: 1) MN: A143847 SN: 0020782, *TAP: SIZE: A LOC: 96 FEET FROM P LINE AT GEN TAYLOR, *MB: CODE: AEN1 LOC: ON PERRIER 96FT FROM GEN TAYLOR (2ND MTR) ** AT 3817: 2) MN: 000000 SN: 0020782, *TAP: SIZE: B LOC: 95 FEET FROM P LINE AT GEN TAYLOR, *MB: CODE: CD LOC: ON PERRIER 96.6 FROM P.L. GEN TAYLOR ****/ DOTTIE READY 5-7-18 EXP 5-27-18 | 2018-05-07 | EXCAVATED IN SIDEWALK ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK ALSO REFERRED TO ZONE 3 TO REMOVE LEAD BACKFILL WITH RIVERSAND AND COLDMILL
201800170801 | 2018-01-24 | LEAD | 1757 | N GAYOSO | O"REILLY | WILK | WM-- LEAK IN STREET INLET SERVICE LEDAK IN SIDEWALK /** 1) MN: A125949 SN: 0059364, *TAP: SIZE: A LOC: 125 FEET FROM P LINE AT AUBRY, *MB: CODE: BDO2 LOC: 125FT FROM LSPL AUBRY BY TREE ****/ | 2018-02-12 | REPLACE BOTH INLET OUTLET WASHERS AT ABOVE LOCATION
201800171501 | 2018-01-24 | LEAD/PLASTIC | 8625 | COHN |  | WMRE | LOCATION: 303576 NEW CONSTRUCTION LOCATE & MARK METER IF NEEDED INSTALL NEW SERVICE NEED NEW SERVICE INSTALLED, ALSO SET 5/8 METER /** 1) MN: 000000 SN: 0067161, *TAP: SIZE: A LOC: 165 FEET FROM P LINE AT MONROE, *MB: CODE: BDK4 LOC: 166FT FROM LPL MONROE FIRST POST CURB ****/ | 2018-02-16 | EXCAVATED A 5 X 5 MUDPLOT AND LOCATED A 5/8" METER BOX RAISED TO GRADE , RENEW OUTLET SERVICE , AND SET A NEW 5./8" METER INLET SERVICE HAS LEAD & NEED'S TO BE REMOVED JOB CONT---
201800173501 | 2018-01-24 | LEAD/PLASTIC | 928 | 6TH | CONSTANCE | WILK | ML METER LEAK METER# A280355 ACCT# 145962-539711 CURB COCK PASSING IN OFF POSITION, NO METER IN NBOX /** 1) MN: A280355 SN: 0003649, *TAP: SIZE: B LOC: 206 FEET FROM P LINE AT LAUREL, *MB: CODE: CELN LOC: ON SIXTH ST 206.5' FROM PL LAUREL ST ****/ DOTTIE READY 8-6-18 EXP 8-26-18 | 2018-08-13 | MADE 3X5 CUT IN SIDEWALK OVER 5/8 INLET CHANGE TWO 5/8 CURB COCKS TIED BACK ON TO LEAD,NEED TO REMOVE LEAD FROM WATER MAIN TO METER BOX AND PROPERTY.(SOC 5 FT. X 5 FT .S/W)
201800174801 | 2018-01-24 | LEAD/PLASTIC | 720 | SORAPARU | ANNUNCIATION | WILK | WM LEAK @ THE CURB INLET SERVICE LEAK BEHIND CURB COCK /** 1) MN: A123912 SN: 0050178, *TAP: SIZE: B LOC: 155 FEET FROM P LINE AT CHIPPEWA, *MB: CODE: CELM LOC: 155FT FROM PL CHIPPEWA ****/ | 2018-02-26 | EXCAVATED AND REPLACED OUTLET SERVICE FROM METER BOX TO PROPERTY ALSO RAISED METER BOX TO GRADE FOUND LEAD ON OUTLET SERVICE
201800174901 | 2018-01-24 | LEAD | 6601 | E HERMES | DWYER RD | WILK | ML METER LEAK ACCT# 178059-451171 METER# C021673 EXAMINE INLET SERVICE INSIDE METER BOX, ALSO BROKEN METER BOX CASING /** 1) MN: C021673 SN: 0159764, *TAP: SIZE: C LOC: 115 FEET FROM P LINE AT HYDT #1, *MB: CODE: ADL3 LOC: RES 115FT FROM L/S HYDT #1 8' OUTSIDE 2' INSIDE ****/ | 2018-03-02 | EXAMINE LOCATION FOUND METER COCK LEAKING & METER WAS BELOW GRADE. EXCAVATED DOWN ON INLET SERVICE'S. FOUND LEAD SERVICE'S. MADE REPAIR'S BY REPLACING COCK WASHER'S, HAND WHEEL UPPER CASING. ALSO RAISED METER TO GRADE. BACKFILLED DRESS UP.
201800175301 | 2018-01-24 | LEAD | 1406 | LESSEPS | N VILLERE | WILK | ML- METER ELAK MTR# A 372851 ACCT# 130155-430701 INLET SERVICE LEAK IN BOX /** 1) MN: A272290 SN: 0047432, *TAP: SIZE: __ LOC: 47 FEET FROM P LINE AT N VILLERE ST, *MB: CODE: BDL1 LOC: ON LESSEPS ST 44' FROM USPL N VILLERE ST ****/ | 2018-02-04 | EXCAVATED AND REPLACED OUTLET SERVICE FROM METER BOX TO PROPERTY ALSO RAISED METER BOX TO GRADE 2X3 MUD CUT BACKFILLED NO DRESS UP NEEDED 3X3 MUD CUTBACKFILLED NO DRESS UP NEEDED
201800177601 | 2018-01-24 | LEAD | 1114 | N ROBERTSON |  | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK IN CONCRETE STREET /** 1) MN: 000000 SN: 0067642, *TAP: SIZE: B LOC: 134 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: AFO7 LOC: ON NO. ROBERTSON, 118' FROMP.L. URSULINES AVE., 3' ****/ | 2018-02-12 | EXCAVATED 4 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER COCK AND LEFT WHIP OUT FOR CUSTOMER BACKFILLED AND CLEANED THE AREA
201800178801 | 2018-01-24 | LEAD | 1812 | CHARBONNET | N ROMAN | WILK | ML- METER LEAK METER#A379587 ACCT#173662-422112 INLET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-02-06 | REPLACED 5/8 HANDWHEEL + GUTS IN METER BOX
201800179501 | 2018-01-25 | LEAD | 3001 | CHARTRES | MONTEGUT | WILK | MI- LEAK BETWEEN SIDEWALK AND CURB /** 1) MN: A208612 SN: 0024503, *TAP: SIZE: A LOC: 58 FEET FROM P LINE AT MONTEGUT, *MB: CODE: ADN4 LOC: 1ST METER 58' P.L. MONTEGUT ****/ INLET SERVICE LEAKING INSIDE METER BOX, CAUSING BOX TO OVERFLOW | 2018-02-03 | EXCAVATED REPAIRED INLET SERVICE LEAK REPLACED METER CURB COCK 3X5 SIDEWALK CUT-->BACKFILLED-->NEED PAVING
201800180301 | 2018-01-25 | LEAD | 826 | DELERY |  | WOLK | LOCATION ID-181512 MTR-A313632 UNDERGROUND LEAK AROUND MTR/MTR IS TURN OFF OUTLET SERVICE LEAK CON REG /** 1) MN: A155854 SN: 0129750, *TAP: SIZE: A LOC: 137 FEET FROM P LINE AT DAUPHINE, *MB: CODE: CDL2 LOC: ON DELERY 131FT FROM PL DAUPHINE 6FT OUTSD PL ** 2) MN: A231830 SN: 0129750, *TAP: SIZE: A LOC: 131 FEET FROM P LINE AT DAUPHINE, *MB: CODE: CDL2 LOC: ON DELERY 130FT FROM PL DAUPHINE 6FT OUTSD PL THERE ARE 2 MORE NOT LISTED. ****/ | 2018-02-16 | EXAMINED JOB NO LEAK IN METER BOX LEAK IS ON PROPERTY
201800183401 | 2018-01-25 | LEAD | 730 | ESPLANADE AV |  | WMTLK | MI LEAK ON THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR LEAK ON SIDEWALK INSIDE MANHOLE /** 1) MN: B026820 SN: 0009863, *TAP: SIZE: B LOC: 106 FEET FROM P LINE AT BOURBON URPL, *MB: CODE: CD5 LOC: 106' FROM URPL BOURBON ****/ | 2018-02-03 | REPAIED 2 INCH INLET SERVICE INSIDE MANHOLE
201800183601 | 2018-01-25 | LEAD/PLASTIC | 567 | AURORA OAKS DR |  | WILK | ML METER LEAK ACCOUNT #237034-416248 METER #A395883 INLET SERVICE LEAK IN SIDEWALK /** 1) MN: A266549 SN: 0171303, *TAP: SIZE: B LOC: 30 FEET FROM P LINE AT HERSCHEL, *MB: CODE: CD LOC: ON AURORA OAKS DR., 30' FROM P.L. HERSCHEL, 6' OUT ****/ | 2018-02-12 | EXAMINED METER AND FOUND THAT IT WAS LOOSE REPLACED WASHERS AND TIGHTENED METER
201800185401 | 2018-01-25 | LEAD | 3901 | TOULOUSE | N SCOTT | WILK | ML- METER LEAK ACCT# 119436-515157 METER# A312757 INLET SERVICE LEAK /** 1) MN: A312757 SN: 0032177, *TAP: SIZE: A LOC: 67 FEET FROM P LINE AT TOULOUSE, *MB: CODE: BFH7 LOC: ON N. SCOTT 67' FROM LSPL TOULOUSE ST ****/ | 2018-02-08 | EXCAVATED 4 X 2MUD PLOT REPLACED 5/8 INCH METER COCK AND HANDWHEEL TO STOP LEAK OUTLET SERVICE HAS BEEN ALREADY RENEWED TO PROPERTY BACKFILLED AND CLEANED THE AREA
201800185601 | 2018-01-25 | LEAD/PLASTIC | 724 | WASHINGTON AV | ANNUNCIATION | WMTLK | ML METER LEAK MTR# A382430 ACCT# 125054 539606 EXAMINE INLET & OUTLET SERVICE FOR A LEAK UNABLE TO DETERMINE WHERE LEAK IS FLOODING GUTTER BOTTOM /** 1) MN: A258640 SN: 0047038, *TAP: SIZE: A LOC: 168 FEET FROM P LINE AT ANNUNCIATION, *MB: CODE: BEM2 LOC: CURB AT 24 IN DRIVE167' P.L. ANNUNCIATION ****/ | 2018-02-20 | LEAK ON BOX COCK IN DRIVWAY CUT JOB OUT WITH AIR GUN TO MAKE REPAIRS REPLACED BOX COCK AND BACKFILLED WITH RIVER SAND LEAD LINE NEED TO BE REMOVED ON INLET
201800186601 | 2018-01-25 | LEAD/PLASTIC | 2364 | ANNUNCIATION |  | WILK | ML-- METER LEAK METER # A305916 ACCT# 123320-541970 INLET SERVICE LEAK BAD CURB COCK FLOODNIG GUTTER BOTTOM /** 1) MN: A305916 SN: 0042665, *TAP: SIZE: A LOC: 71 FEET FROM P LINE AT 1ST, *MB: CODE: BDLN LOC: IN FRONT ON CONCRETE 70' P.L. 1ST ****/ | 2018-02-20 | EXAMING LEAK OBSERVED LEAK ON INLET SERVICE BROKE OUT CONCRETE WITH AIR GUN OBSERVED LEAD LINE ON OUTLET REPAIRED LEAK REPLACED LEAD LINE WITH PLASTIC TO PROPERTY BACKFILLED WITH SAND AND COAL MILL REMOVED OLD CHOKED METER REPLACED WITH NEW OLD METER INFO METER:A305916 FACT:52084774 MAKE: SENSUS READ:13965
201800190001 | 2018-01-25 | LEAD/PLASTIC | 2709 | ST THOMAS | THIRD | WILK | MI-LEAK IN THE SIDEWALK CHANGED FROM 2620 ST THOMAS INLET SERVICE LEAK @ CURB FLOODING CURB /** 1) MN: A152756 SN: 0020084, *TAP: SIZE: B LOC: 83 FEET FROM P LINE AT FOURTH, *MB: CODE: FKO LOC: 83FT FROM PL FOURTH 2' OUTSIDE PL 6' INSIDE CURB ****/ | 2018-02-07 | LOCATED LEAK FOUND ABANDONED SERVICE TURN OFF BY STOP COT THEN BURIED IT
201800190101 | 2018-01-25 | LEAD | 872 | TAFT PL | DUMAINE | WILK | ML-METER LEAK ACCOUNT #132289-514131 METER #A296934 INLET SERVICE LEAK IN MUDPLOT FLOODING CURB/STREET /** 1) MN: A296934 SN: 0062956, *TAP: SIZE: A LOC: 41 FEET FROM P LINE AT DUMAINE, *MB: CODE: AD LOC: METER ON TAFT PL 41 FT FROM PL DUMAINE ****/ | 2018-02-08 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR ON OUTLET SERVICE TO STOP LEAK BACKFILED AND CLEANED THE AREA
201800192801 | 2018-01-26 | LEAD | 1235 | FRANKLIN AV | URQUHART | WMRE | LOCATION ID# 115440 MTR# A429936 PLEASE LOCATE AND RAISE TO GRADE /** 1) MN: A215365 SN: 0034781, *TAP: SIZE: A LOC: 29 FEET FROM P LINE AT FRANKLIN AVE, *MB: CODE: AFHL LOC: ON URQUHART 29.5FT FROM PL OF FRANKLIN AVE ****/ | 2018-04-09 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK WAS LEAKING ON LINE + HAD A LEAK ON OUTLET + REPAIRED RAN PLASTIC TO PROPERTY ALSO LEAK ON PROPERTY RAISED TO GRADE + MARKED
201800193001 | 2018-01-26 | LEAD | 3739 | SOMERSET DR | GEN DE GAULLE DR | WMRE | LOCATION ID# 230203 MTR# A188025 METER BURIED/LOCATE AND RAISE /** 1) MN: A188025 SN: 0141532, *TAP: SIZE: B LOC: 45 FEET FROM P LINE AT GEN DE GAULLE DR, *MB: CODE: CDMN LOC: ON SOMERSET DR., 44' FROM P.L. GEN. DE GAULLE DR., ****/ | 2018-03-03 | LOCATED THE METER BOX AND EXCAVATED ON THE INELT AND OUTLET SERVICE AND RAISED METER BOX TO GRADE AND THEN WE MARK IT THEN WE BACKFILL AND CLEAN UP JOB SITE
201800196601 | 2018-01-26 | LEAD/PLASTIC | 5410 | LACOUR MONIQUE |  | WMTLK | ML-METER LEAK ACCT#232412-416830 METER#A114917 EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN BOX /** 1) MN: A114917 SN: 0145580, *TAP: SIZE: B LOC: 119 FEET FROM P LINE AT ETON, *MB: CODE: BDK2 LOC: ON LACOUR MONIQUE, 122' FROM P.L. ETON, 7' OUT- ****/ | 2018-02-25 | EXAMINED METER FOR LEAK EXCAVATED INLET AND OUTLET SERVICE LINE NO LEAKS OBSERVED
201800197601 | 2018-01-26 | LEAD | 2151 | HOPE | FRENCHMEN | WILK | ML - METER LEAK ACCOUNT NUMBER - 133113-496354 METER - A392686 INLET SERVICE LEAK IN BOX /** 1) MN: A235718 SN: 0079936, *TAP: SIZE: B LOC: 6 FEET FROM P LINE AT FRENCHMEN, *MB: CODE: BDK1 LOC: ON HOPE ST. 6' FROM DIV. P.L. OF FRENCHMEN ST. 4' ****/ | 2018-03-05 | REPLACED 5/8 INCH CURB COCK IN MUD PLOT
201800199101 | 2018-01-26 | LEAD | 2037 | DUMAINE |  | WILK | MI- LEAK BETWEEN SIDEWALK IN THE STREET INLET SERVICE LEAK BETWEEN SIDEWALK AND STREET /** 1) MN: A194242 SN: 0052682, *TAP: SIZE: A LOC: 104 FEET FROM P LINE AT DUMAINE, *MB: CODE: ADL2 LOC: SIDE DRIVE 2ND 104FT FROM LSPL DUMAINE ****/ | 2018-03-08 | RRIVED AT ABOVE LOCATION EXCAVATED IN SIDEWALK FOUND 5/8 INCH CURB COCK LEAKING + REPAIRED IT BACKFILLED
201800199801 | 2018-01-26 | LEAD | 2541 | ESPLANADE AV |  | WMRE | METER BURIED. PLEASE LOCATE AND CHANGE METER A428939 LOC ID 139225 LOCATE, RAISE TO GRADE AND CHANGE METER /** 1) MN: A279091 SN: 0069863, *TAP: SIZE: B LOC: 143 FEET FROM P LINE AT BROAD N, *MB: CODE: DIO LOC: ON BELL STRE 143FT FROM BROAD N ****/ | 2018-04-11 | ARRIVED AT ABOVE LOCATION LOCATED WATER METER AT CURB ALREADY RASIED TO GRADE CHANGED METER + MARKED ***********OLD METER INFO*********** METER:A428939 FAC:16314551 MAKE:HERSEY READ:265
201800200201 | 2018-01-26 | LEAD | 5911 | MARIGNY |  | WOLK | OUTLET SERVICE NEEDS TIE IN. PLEASE REPAIR METER A427114 LOC ID 303602 OUTLET TIE IN HOUSE UNDER RENOVATIONS /** 1) MN: A273698 SN: 0103355, *TAP: SIZE: A LOC: 88 FEET FROM P LINE AT PRESSBURG, *MB: CODE: BE LOC: ON MARIGNY, 86' FROM P.L. PRESSBURG, 8' OUTSIDE ****/ | 2018-02-05 | EXCAVATED IN MUDPLOT RENEW 3/4" OUTLET SERVICE PLASTIC LINE FROM METER BOX TO PROPERTY LINE. DRESS UP WITH RIVERSAND ALSO REF TO ZONE 1 TO TAKE 3/4" LEAD LINE OUT ON INLET SIDE JOB REF TO ZONE1 TO TAKE LEAD LINE OUT ON THE IN LET SIDE
201800200202 | 2018-02-05 | LEAD | 5911 | MARIGNY | PRESSBURG | WILK | REFER TO ZONES TO REMOVE LEAD LINE ON THE INLET SIDE /** 1) MN: A273698 SN: 0103355, *TAP: SIZE: A LOC: 88 FEET FROM P LINE AT PRESSBURG, *MB: CODE: BE LOC: ON MARIGNY, 86' FROM P.L. PRESSBURG, 8' OUTSIDE ****/ | 2018-12-19 | JOB WAS DONE
201800200401 | 2018-01-26 | LEAD | 1200 | DAUPHINE | GOV NICHOLLS | WILK | MI LEAK ON THE SIDEWALK ,NEXT TO METER INLET SERVICE LEAK IN SIDEWALK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-03-08 | EXCAVATED 2 X 6 CONCRETE SIDEWALK FOUND LEAK ON ABANDON INELT SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND COLDMILL
201800200901 | 2018-01-26 | LEAD | 5817 | ANNUNCIATION | ELEONORE | WILK | MI STANDING WATER BY CURB IN STREET ACCT# 205369-566259 EXAMINE INLET SERVICE @ CURB FOR A LEAK /** 1) MN: A179822 SN: 0035545, *TAP: SIZE: B LOC: 13 FEET FROM P LINE AT ELEONORE, *MB: CODE: ON A LOC: ON ANNUNCIATION 13' FROM DIV PL ELEONORE 7' OUTSID ****/ DOTTIE READY 8-16-18 EXP 9-5-18 | 2018-08-19 | EXAMINED AREA CLEANED OUT METER BOX EXCAVATED ON INLET + OUTLET SERVICE OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK BACKFILLEDCLEANED AREA SITE
201800202201 | 2018-01-26 | LEAD | 4617 | CHESTNUT | VALENCE | WILK | ML- METER LEAK ACCT # 122897-561176 METER # A414275 INLET SERVICE LEAK /** 1) MN: A303613 SN: 0041858, *TAP: SIZE: A LOC: 160 FEET FROM P LINE AT VALENCE, *MB: CODE: AE2 LOC: ON CHESTNUT 160FT FROM VALENCE ****/ DOTTIE READY 5-7-18 EXP 5-27-18 | 2018-05-10 | EXCAVATED IN CONCRETE DRIVEWAY REPAIR 5/8 STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND & COLD MILL. JOB REFER TO ZONE 3 TO TAKE LEAD OUT FROM WATER MAIN TO METER BOX
201800202202 | 2018-05-10 | LEAD | 4617 | CHESTNUT | VALENCE | WSNR | JOB REFER TO ZONE 3 TO TAKE LEAD OUT FROM WATER MAIN TO METER BOX /** 1) MN: A303613 SN: 0041858, *TAP: SIZE: A LOC: 160 FEET FROM P LINE AT VALENCE, *MB: CODE: AE2 LOC: ON CHESTNUT 160FT FROM VALENCE ****/ DOTTIE READY 6-4-18 EXP 6-24-18 | 2018-06-19 | RENEW INLET SERVICE AND OUTLET SERVICE. REMOVED LEAD FROM WATER MAIN TO PROPERTY 5/8. 5/8 RAISE METER BOX TO GADE.BACKFILLED AND CLEANED JOB SITE.
201800203201 | 2018-01-26 | LEAD | 1565 | N DORGENOIS | LAPEYROUSE | WILK | ML-METER LEAK INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A239659 SN: 0044223, *TAP: SIZE: A LOC: 146 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: DN2 LOC: ON NO. DORGENOIS,144' FROM U.S.P.L. LAPEYROUSE ****/ | 2018-03-07 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK RISED 5/8 INCH METER BOX BOTTOM TO GRADE + REPLACED DAMAGED 5/8 INCH WATER METER BACKFILLED + DRESSED UP AREA ***********OLD METER INFO************ METER:A395720 FAC: 14077270 MAKE:HERSEY READ:1728
201800203501 | 2018-01-26 | LEAD | 2015 | S SALCEDO | VINCENT | WMTBG | ********PICKUP JOB********* METER BOX BELOW GRADE, ADJUST METER BOX TO PROPER GRADE /** 1) MN: B023749 SN: 0065098, *TAP: SIZE: B LOC: 123 FEET FROM P LINE AT , *MB: CODE: BDK LOC: ON SALCEDO 123' FROM PL OF VINCENT ****/ DOTTIE READY 2-1-18 EXP 2-21-18 | 2018-02-07 | EXAMINE JOB PUMP WATER OUT METER BOX AND FOUND THAT METER HAD BAD METER COCK AND METER BOX BELOW GRADE .EXCAVATED IN MUDPLOT AND CHANGED METER COCK AND TIED BACK INTO LEAD LINE AND ALSO FIX METER BOX TO PROPER GRADE .BACKFILL JOB WITH COLMILL.
201800205501 | 2018-01-27 | LEAD | 2331 | CANAL | N TONTI | WMTLK | LOCATED METER , METER LEAKING NEEDS TO BE RELOCATED IN S/W PAINTED BLUE. ACCT#004389090 METER#B023692 METER BURIED,LOCATE & RAISE /** 1) MN: B023692 SN: 0065452, *TAP: SIZE: B LOC: 60 FEET FROM P LINE AT TONTI N, *MB: CODE: ADN1 LOC: ON CANAL 60FT FROM LRPL OF N TONTI ****/ | 2018-02-26 | EXCAVATED 6 X 2 SIDEWALK CUT ALSO 3 X 3 MUD PLOT THROUGH TREE ROOTS RELOCATED METER FROM OUT OF MUD PLOT TO SIDEWALK BACKFILL AND CLEAN THE AREA *****************OLD METER INFO************ METER:B023692 FAC:34847167 MAKE:SENSUS READ:10095
201800208701 | 2018-01-27 | LEAD | 1804 | ALVAR | N ROMAN | WMRE | UNABLE TO LOCATE METER NEED MACHINE FORMDIG UP ACCT#082820132 METER#A404395 METER BURIED,LOCATE & RAISE /** 1) MN: A331599 SN: 0080484, *TAP: SIZE: A LOC: 66 FEET FROM P LINE AT ROMAN N, *MB: CODE: BDL2 LOC: L.P.L. CURB ON ALVAR 66 FT FROM PL N ROMAN ****/ | 2018-05-04 | EXCAVATED 4 X 4 MUD PLOT RAISED METER BOX UP TO GRADE BACKFILLED JOB WITHRIVERSAND JOBIS COMPLETE
201800210101 | 2018-01-27 | LEAD | 1317 | KENTUCKY | URQUHART | WMRE | UNABLE TO LOCATE NEED MACHINE ACCT#043048121 METER#A398107 METER BURIED,LOCATE & RAISE /** 1) MN: A238843 SN: 0050231, *TAP: SIZE: A LOC: 131 FEET FROM P LINE AT URQUHART, *MB: CODE: BDL2 LOC: ON KENTUCKY,132.5' FROM L.S.P.L. URQUHART ****/ | 2018-02-27 | REMOVED DEBRIS OFF METER COVER MARKED METER BOX COVER WITH BLUE PAINT ALSO THE SIDEWALK WAS MARKED METER BOX IS ALREADY UP TO GRADE
201800215501 | 2018-01-28 | LEAD | 3009 | SERANTINE | ROSIERE | WMRE | LOCATED METER AND MARKED ,ETER BELOW GRADE NEED TO BE RAISED NEED MACHINE ACCT#138088070 METER#C033041 METER CASING BELOW GRADE /** 1) MN: C011941 SN: 0092985, *TAP: SIZE: C LOC: 106 FEET FROM P LINE AT ROSIERE, *MB: CODE: BDK LOC: ON SERANTINE 67' FROM PL ROSIERE 8' OUTSIDE PL ****/ | 2018-04-11 | ARRIVED AT ABOVE LOCATION FOUND 1 INCH METER BOX CASING BROKE WITH ALOT OF TRASH + UP TO GRADE REPLACED CASING,MARKED METER BACKFILLED
201800216101 | 2018-01-28 | LEAD | 2229 | N GALVEZ | MARIGNY | WMRE | ACCT#172455127 METER#A363058 METER BURIED,LOCATE & RAISE UNABLE TO LOCATE NEED MACHINE /** 1) MN: A302694 SN: 0046073, *TAP: SIZE: __ LOC: 8 FEET FROM P LINE AT MARIGNY, *MB: CODE: __ LOC: ON N GALVEZ 7FT FROM D.P.L. MARIGNY 8FT OUTSIDE ****/ | 2018-04-09 | ARRIVED AT ABOVE LOCATION EXCAVATED IN MUD PLOT RIGHT ON MESUREMENT FOUND 5/8 METER RAISED TO GRADE + MARKED
201800218301 | 2018-01-28 | LEAD/PLASTIC | 5819 | RHODES AV | DOWNEY | WOLK | ML-METER LEAK EXAMINE INLET/OUTLET SERVICE FOR LEAK OVERFLOWING ONTO CURB /** 1) MN: A130827 SN: 0143369, *TAP: SIZE: B LOC: 202 FEET FROM P LINE AT DOWNEY, *MB: CODE: ADK2 LOC: ON RHODES 192FT FROM DOWNEY 7FT OUTSIDE ****/ | 2018-02-21 | EXCAVATED METER BOX BY HAND AND FOUND LEAK ON BOX COCK
201800218601 | 2018-01-28 | LEAD | 10337 | BROOKFIELD DR | PLAINFIELD DR | WOLK | ******************PCKUP************** J GILLIAM DRY OUTLET CUSTOMER OUT OF WATER /** 1) MN: A306780 SN: 0152261, *TAP: SIZE: B LOC: 100 FEET FROM P LINE AT RESTGATE, *MB: CODE: BDKN LOC: BET HANOVER AND RESTGATE 76FT FROM PL RESTGATE ****/ | 2018-01-28 | EXCAVATED 4 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE LINE TO STOP LEAK AND GIVE CUSTOMER WATER BACKFILLED AND CLEANED THE AREA
201800218701 | 2018-01-28 | LEAD/PLASTIC | 3200 | PLYMOUTH PL | MACARTHUR BL | WMTLK | ML- METER LEAK ACCT# 228746-414921 MTR# B025461 EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX OVERFLOWING /** 1) MN: B025461 SN: 0123503, *TAP: SIZE: C LOC: 258 FEET FROM P LINE AT DOVER PL, *MB: CODE: AD LOC: ON PLYMOUTH PL 253FT FROM P.L. DOVER 9FT OUTSIDE ****/ | 2018-02-09 | EXAMINED JOB DUG UP BOX FOUND LEAK ON INLET REPAIRED STOP LEAKING NEED TO BE DRESSED UP
201800218901 | 2018-01-28 | LEAD/PLASTIC | 3718 | PRESTON PL | BERKLEY DR | WILK | ML-METER LEAK INLET SERVICE LEAK FLOODING AREA AT RAPID PACE CAUSING VERY POOR PRESSURE **1ST AM** **CUSTOMER AGREES TO WAIT UNTIL TOMORROW MORNING** /** 1) MN: A273459 SN: 0145696, *TAP: SIZE: B LOC: 25 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: AD LOC: ON PRESTON PL 2.5' FROM DPL BERKLEY DR 2'INSIDE CU ****/ | 2018-01-29 | EXCAVATED METER BOX AND FOUND LEAK ON INLET REPLACED BOX COCK TO REPAIR LEAK
201800219301 | 2018-01-28 | LEAD | 1701 | NASHVILLE AV | DANNEEL | WILK | MI-LEAK IN SIDEWALK EXAMINE INLET SERVICE FOR LEAK IN MUDPLOT ACROSS FROM 1701 NASHVILLE AV **CHANGED FROM 1700BLK NASHVILLE AV** /** 1) MN: D006897 SN: 0094177, *TAP: SIZE: D LOC: 35 FEET FROM P LINE AT NASHVILLE AV, *MB: CODE: BE LOC: MH ON DANNEEL 41' P/L NASHVILLE AV 6' OUTSIDE 5' ** 2) MN: A306701 SN: 0000000, *TAP: SIZE: A LOC: 42 FEET FROM P LINE AT DANNEEL, *MB: CODE: CP LOC: ON NASHVILLE AVE.,42' FROM P.L. DANNEEL,4' OUTSIDE ****/ DOTTIE READY 8-16-18 EXP 9-5-18 | 2018-08-19 | EXAMINED AND FOUND LEAK INSIDE MANHOLE ALSO MADE REPAIR ON 1 1/2 INLET. JOB COMPLETE
201800219501 | 2018-01-28 | LEAD/PLASTIC | 197 | PINEWOOD CT | CYPRESS ACRES DR | WILK | MI-LEAK IN STREET INLET SERVICE /** 1) MN: A241298 SN: 0164641, *TAP: SIZE: A LOC: 10 FEET FROM P LINE AT CYPRESS ACRES DR, *MB: CODE: OOO LOC: ON PINEWOOD 10FT FROM PL CYPRESS ACRES 9FT OUT ****/ | 2018-02-05 | EXCAVATED METER BOX AND FOUND LEAK ON FITTING UNDER CURB REPLACED LINE AND FITTING ON INLET SIDE
201800219601 | 2018-01-28 | LEAD/PLASTIC | 203 | PINEWOOD CT | CYPRESS ACRES DR | WILK | ML-METER LEAK METER#A270535 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A270535 SN: 0164642, *TAP: SIZE: A LOC: 10 FEET FROM P LINE AT CYPRESS ACRES DR, *MB: CODE: __ LOC: ON PINEWOOD 10FT FROM PL CYPRESS 9FT OUTSD PL ****/ | 2018-02-05 | EXAMINED METER AND CLEANED MUD AND RCOKS OUT OF METER BOX NO LEAK WAS FOUND
201800223501 | 2018-01-29 | LEAD/PLASTIC | 1237 | CASA CALVO | SOCRATES | WOLK | LOCATION#226543-404745. METER#A355511. METER HAS A SLOW CON REG. NO FAUCET TO PERFORM TEST /** 1) MN: A305574 SN: 0103437, *TAP: SIZE: A LOC: 192 FEET FROM P LINE AT SOCRATES, *MB: CODE: CDN3 LOC: ON CASA CALVO 192FT FROM SOCRATES 6FT OUTSIDE ****/ | 2018-02-27 | EXAMINED METER EXCAVATED METER THRU ROOTS OBSERVED LEAK ON OUTLET SERVICE REPAIRED OUTLET SERVICE BACKFILLED
201800223801 | 2018-01-29 | LEAD/PLASTIC | 616 | VALLETTE | EVELINA | WOLK | LOCATION#224632-400688. METER#A352044. METER HAS A CON REG. A LEAK WAS FOUND UNDERGROUND BETWEEN THE METER AND S7W RD. /** 1) MN: A329006 SN: 0070330, *TAP: SIZE: A LOC: 115 FEET FROM P LINE AT EVELINA, *MB: CODE: BDM1 LOC: ON VALLETTE 116FT FROM P.L. EVELINA ****/ | 2018-05-29 | ARRIVED ON JOB SITE EXAMINE CON REG ON METER CUT OUT CONCRETE BY HAND EXCAVATED IN MUD PLOT BY HAND MADE REPAIRS AND SET UP NEW METER BOX COMPLETE BACKFILLED DRESS UP WORK SITE....JOB COMPLETE
201800226902 | 2018-01-29 | LEAD | 1225 | N RAMPART | GOV NICHOLLS | WMRE | ACCT#001647030 METER#C020761 NEED MACHINE METER BURIED,LOCATE & RAISE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ /** 1) MN: C020761 SN: 0006861, *TAP: SIZE: C LOC: 189 FEET FROM P LINE AT GOV. NICHOLLS, *MB: CODE: BDKN LOC: ON RAMPART,187.4' FROM P.L. GOV. NICHOLLS,9.5' ****/ | 2018-04-06 | EXCAVATED 4 X 3 SIDEWALK CUT FOUND ABANDON 1 INCH SERVICE LINE AND NO METER CUSTOMER HAS FIRE SERVICE AND DOMESTIC DRINKING WATER TIE INTO TOGETHER MARK CURB WHERE 1 INCH SERVICE IS LOCATED BACK FILLED AND CLEANED THE AREA
201800227003 | 2018-04-19 | LEAD | 1125 | N TONTI | GOV NICHOLLS | WMRE | ARRIVED AT ABOVE LOCATION EXCAVATED ON METER BOX MEASUREMENT UNABLE TO LOCATE NEED MACHINE /** 1) MN: C025648 SN: 0005668, *TAP: SIZE: C LOC: 71 FEET FROM P LINE AT N TONTI, *MB: CODE: OOO LOC: ON GOVERN NICHOLLS 71.5FT FROM USPL OF N TONTI ** 2) MN: C017860 SN: 0005668, *TAP: SIZE: C LOC: 71 FEET FROM P LINE AT TONTI N, *MB: CODE: OOO LOC: SIDE STREET ON GOV. NICHOLLS 62' P/L N TONTI 8' THERE ARE 2 MORE NOT LISTED. ****/ | 2018-04-23 | LOCATED METER AT ABOVE LOCATION + MARKED WITH PAINT
201800227903 | 2018-05-01 | LEAD | 2721 | N TONTI | ALMONASTER AV | WMRE | UNABLE TO LOCATE WITH MEASOUREMENT GIVEN NEED MACHINE TO HELP LOCATE METER /** 1) MN: A290266 SN: 0072443, *TAP: SIZE: A LOC: 66 FEET FROM P LINE AT ALMONASTER AV, *MB: CODE: ADLM LOC: 65FT FROM USPL ALMONASTER AV ****/ | 2018-05-02 | ARRIVED AT ABOVE EXCAVATED IN GUTTER BOTTOM FOUND ABANDON SERVICE WITH NO METER BOX + SET METER BOX COMPLETE IN SIDEWALK NO METER
201800228002 | 2018-01-29 | LEAD | 1125 | N TONTI | GOV NICHOLLS | WMRE | LOCATIONID#181827-524550 METER#C017860 NEED MACHINE CAN'T LOCATE METER/LOCATE & RAISE /** 1) MN: C025648 SN: 0005668, *TAP: SIZE: C LOC: 71 FEET FROM P LINE AT N TONTI, *MB: CODE: OOO LOC: ON GOVERN NICHOLLS 71.5FT FROM USPL OF N TONTI ** 2) MN: C017860 SN: 0005668, *TAP: SIZE: C LOC: 71 FEET FROM P LINE AT TONTI N, *MB: CODE: OOO LOC: SIDE STREET ON GOV. NICHOLLS 62' P/L N TONTI 8' THERE ARE 2 MORE NOT LISTED. * /** 1) MN: C025648 SN: 0005668, *TAP: SIZE: C LOC: 71 FEET FROM P LINE AT N TONTI, *MB: CODE: OOO LOC: ON GOVERN NICHOLLS 71.5FT FROM USPL OF N TONTI ** 2) MN: C017860 SN: 0005668, *TAP: SIZE: C LOC: 71 FEET FROM P LINE AT TONTI N, *MB: CODE: OOO LOC: SIDE STREET ON GOV. NICHOLLS 62' P/L N TONTI 8' THERE ARE 2 MORE NOT LISTED. ****/ | 2018-05-02 | EXAMINED JOB AND FOUND ONLY 1 METER BOX AT THIS LOCATION
201800229901 | 2018-01-29 | LEAD | 2703 | LAFITTE | N BROAD | WILK | LEAK IN GRASSY AREA CHANGED FROM 2701 LAFITTE INLET SERVICE LEAK ON ABANDON SERVICE IN FRONT VACANT LOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-02-12 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK 3/4 INCH ABANDON INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND
201800230203 | 2018-04-19 | LEAD | 328 | N PRIEUR |  | WMRE | ARRIVED AT ABOVE LOCATION EXCVAVATED ON METER BOX MEASUREMENT + WAS UNABLE TO LOCATE NEED MACHINE /** 1) MN: A225061 SN: 0050305, *TAP: SIZE: A LOC: 93 FEET FROM P LINE AT CONTI, *MB: CODE: CDL5 LOC: ON N PRIEUR ST 95' FROM URPL CONTI ****/ | 2018-04-23 | EXCAVATED IN MUD PLOT + LOCATED 5/8INCH WATER METER MARKED WITH BLUE PAINT BACKFILLED + DRESSED UP AREA
201800230402 | 2018-01-29 | LEAD | 1661 | N ROMAN | ST BERNARD AV | WMRE | ACCT#079531021 METER#B040514 NEED MACHINE METER BURIED,LOCATE & RAISE /** 1) MN: B018947 SN: 0078093, *TAP: SIZE: B LOC: 169 FEET FROM P LINE AT ST BERNARD AVE, *MB: CODE: ADK LOC: ON N ROMAN 169' FROM PL OF ST BERNARD AVE ****/ /** 1) MN: B018947 SN: 0078093, *TAP: SIZE: B LOC: 169 FEET FROM P LINE AT ST BERNARD AVE, *MB: CODE: ADK LOC: ON N ROMAN 169' FROM PL OF ST BERNARD AVE ****/ | 2018-05-01 | EXCAVATED 4 X 8 LIMESTONE GUTTER BOTTOM RAISED METER BOX UP TO GRADE BACKFILLEDJOB WITH RIVERSAND COLDMILL MARKED WITH BLUE PAINT WHERE METER BOX IS LOCATED
201800230602 | 2018-01-29 | LEAD | 1661 | N ROMAN | ST BERNARD AV | WMRE | ACCT#146215 MET#B40514 NEED MACHINE PLEASE LOC & RAISE TO GRADE /** 1) MN: B018947 SN: 0078093, *TAP: SIZE: B LOC: 169 FEET FROM P LINE AT ST BERNARD AVE, *MB: CODE: ADK LOC: ON N ROMAN 169' FROM PL OF ST BERNARD AVE ****/ /** 1) MN: B018947 SN: 0078093, *TAP: SIZE: B LOC: 169 FEET FROM P LINE AT ST BERNARD AVE, *MB: CODE: ADK LOC: ON N ROMAN 169' FROM PL OF ST BERNARD AVE ****/ | 2018-05-02 | ARRIVED AT ABOVE LOCATION FOUND METER ALREADY LOCATED
201800231101 | 2018-01-29 | LEAD/PLASTIC | 3720 | RUE NICHOLE | CARLISLE CT | WOLK | ML- METER LEAK ACCT# 232509-416883 MTR# A278581 ***************PLEASE CONTACT UPON ARRIVAL****************** **********CUSTOMER OUT OF WATER********** S SLACK 11:05 OUTLET SERVICE LEAK HOLE EXPOSED /** 1) MN: A124973 SN: 0146302, *TAP: SIZE: B LOC: 170 FEET FROM P LINE AT CARLISLE CT, *MB: CODE: CDLN LOC: ON RUE NICHOLE 170FT FROM CARLISLE 9FT OUTSIDE ****/ | 2018-01-29 | EXAMINED JOB CHECK UP THE PROPERTY LINE AND REPLACED CONNECTION
201800234901 | 2018-01-29 | LEAD | 318 | S BROAD | BANKS | WILK | ML METER LEAK METER# A426240 INLET SERVICE LEAK IN DRIVEWAY FLOODING CURB & SUROUNDING AREA /** 1) MN: SN: 0035123, *TAP: SIZE: B LOC: 143 FEET FROM P LINE AT PALMYRA, *MB: CODE: __ LOC: 143 FT FROM URP LINE AT PALMYRA ST. ****/ | 2018-02-04 | EXCAVATED 8 X 8 SIDEWALK BY HAND TRACED ABANDONED OUTLET SERVICE LINE TO MAKE REPAIR BACKFILLED AND CLEANED THE AREA
201800235501 | 2018-01-29 | LEAD | 2626 | GOV NICHOLLS |  | WILK | ML-METER LEAK ACCT#104572-523622 METER#A241894 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A241894 SN: 0002732, *TAP: SIZE: B LOC: 276 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CE LOC: ****/ | 2018-02-12 | EXCAVATED 2 X 10 SIDEWALK CUT REPLACED 5/8 INCH METER COCK AND RENEWED OUTLET SERVICE LINE TO RPOPERTY BACKFILL AND CLEANED THE AREA,,,LEFT BARRELS AROUND CONCRETE THAT WAS UNABLE TO PICK UP
201800235701 | 2018-01-29 | LEAD | 1931 | DESIRE | N JOHNSON | WILK | ML- METER LEAK ACCT# 218138-432362 METER# A412734 INLET SERVICE LEAK IN DRIVEWAY /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-02-22 | EXCAVATED IN CONCRETE DRIVEWAY + REPLACED 5/8 INCH CURB COCK ON 3/4 INCH PLASTIC INELT SERVICE LINE BACKFILLED + DRESSED UP AREA
201800235801 | 2018-01-29 | LEAD | 2545 | HAVANA | HIAWATHA | WILK | ML-METER LEAK ACCT#142463-476612 METER#A281137 EXAMINE INLET SERVICE FOR A LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-02-14 | EXCAVATED 2 X 6 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET RENEW OUTLET SERVICE FROM METER BOX TO LEAD GOIN UNDER STEPS BACKFILLED JOB WITH RIVERSAND COLDMILL
201800236102 | 2018-01-29 | LEAD | 2641 | EADS |  | WMRE | LOCATIONID#157276-485094 METER#A276392 NEED MACHINE METER BELOW GRADE,RAISE /** 1) MN: A276392 SN: 0094545, *TAP: SIZE: A LOC: 15 FEET FROM P LINE AT FLORIDA AVE, *MB: CODE: CDN1 LOC: ON EADS, 15' FROM P.L. FORIDA AVE.,8' OUTSIDE P.L. ****/ /** 1) MN: A276392 SN: 0094545, *TAP: SIZE: A LOC: 15 FEET FROM P LINE AT FLORIDA AVE, *MB: CODE: CDN1 LOC: ON EADS, 15' FROM P.L. FORIDA AVE.,8' OUTSIDE P.L. ****/ | 2018-04-24 | EXCAVATED 3 X 3 GUTTER BOTTOM + 4 X 2 IN ALREADY EXPOSED SIDEWALK RELOCATED THE METER BOX TO SIDEWALK BACKFILLED AND CLEANED THE AREA
201800236202 | 2018-01-29 | LEAD | 1901 | ELYSIAN FIELDS AV | N PRIEUR | WMRE | ACCT#149259242 METER#A396362 NEED MACHINE METER BURIED,LOCATE & RAISE /** 1) MN: A141110 SN: 0037474, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT ELYSIAN FIELDS AVE, *MB: CODE: BF LOC: ON N PRIEUR 99FT PL ELYSIAN FIELDS AV 2' OUTSIDE ****/ /** 1) MN: A141110 SN: 0037474, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT ELYSIAN FIELDS AVE, *MB: CODE: BF LOC: ON N PRIEUR 99FT PL ELYSIAN FIELDS AV 2' OUTSIDE ****/ | 2018-02-26 | EXCAVATED IN MUD PLOT + LOCATED METER BOX MARKED WITH BLUE PAINT
201800237401 | 2018-01-29 | LEAD | 814 | ALVAR | DAUPHINE | WOLK | ML- METER LEAK METER#A421347 ACCT#160605-428473 EXAMINE OUTLET SERVICE FOR A LEAK CONSTANT REG ON METER /** 1) MN: A295060 SN: 0052538, *TAP: SIZE: B LOC: 97 FEET FROM P LINE AT DAUPHINE, *MB: CODE: ADO2 LOC: ON ALVAR, 97' FROM P.L. DAUPHINE, 7.5' OUTSIDE ****/ | 2018-02-16 | EXAMINED JOB FOUND LEAK ON OUTLET EXCAVATED 2 X 4 REPAIR JOB BACKFILLED AND CLEANED THE AREA
201800237501 | 2018-01-29 | LEAD | 3151 | BURGUNDY | LOUISA | WILK | ML- METER LEAK CAUSING POOR PRESSURE TO PROPERTY METER#A369931 ACCT#121724-427343 *******B LEAVE IN SYSTEM******* BAD BLEEDER VALVE ON CURB COCK CAUSING POOR PRESSURE /** 1) MN: A143356 SN: 0055795, *TAP: SIZE: A LOC: 140 FEET FROM P LINE AT LOUISA, *MB: CODE: BF LOC: 138FT FROM USPL LOUISA ****/ | 2018-01-31 | EXCAVATED 4 X 2 SIDEWALK CUT REPLACED METER BOX COCK AND RENEWED OUTLET SERVICE LINE TO PROPERTY BACKFILL AND CLEANED THE AREA
201800242401 | 2018-01-30 | LEAD/PLASTIC | 4042 | FRANKLIN AV | JASMINE | WILK | MI LEAK IN THE STREET INET SERVICE LEAK @ CURB IN STREET /** 1) MN: A323318 SN: 0088235, *TAP: SIZE: A LOC: 94 FEET FROM P LINE AT VERBENA, *MB: CODE: BDK LOC: ****/ | 2018-05-30 | EXCAVATED IN STREET OVER 6" WATER MAIN LEAK MADE ALL REPAIRS TO STOP LEAK ON LEAD REFERRE TO ZONE 5 TO REMOVE LEAD BACKFILL WITH RIVERSAND AND COLDMILL
201800243601 | 2018-01-30 | LEAD/PLASTIC | 138 | DAVID | IBERVILLE | WILK | WM-LEAK IN SIDEWALK CHANGED FROM 4122 IBERVILLE INLET SERVICE LEAK CARS ROLLING OVER METER THAT SITS ON IBERVILLE NEX TO 4122 IBERVILLE /** 1) MN: A272428 SN: 0066756, *TAP: SIZE: B LOC: 178 FEET FROM P LINE AT CARROLLTON AVE N, *MB: CODE: ADH3 LOC: ON IBERVILLE ST 178' FROM PL N CARROLLTON AVE ****/ | 2018-03-17 | EXCAVATED AND MADE REPAIRS ON A 5/8 INLET SERVICE LEAK LEAD. PLASTIC ON THE OUTLET JOB COMPLETE. JEG
201800246901 | 2018-01-30 | LEAD/PLASTIC | 822 | HENDEE | HOMER | WMTLK | ML- METER LEAK METER # A351876 ACCT # 237376-404086 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER OVERFLOWING ON SIDEWALK /** 1) MN: A285989 SN: 0095781, *TAP: SIZE: B LOC: 5 FEET FROM P LINE AT HOMER, *MB: CODE: CD LOC: ON HENDEE 6FT FROM DPL OF HOMER 8FT OUTSIDE PL AND ****/ | 2018-02-19 | EXCAVATED METER BOX BY HAND TO REPAIR LEAK FOUND LEAK ON OUTLET REPLACED HAND WHEEL
201800249801 | 2018-01-30 | LEAD | 3332 | N DERBIGNY |  | WILK | MI LEAK ON SIDEWALK INLET SERVICE LEAK ON ABANDON SERVICE 02/20/18 LEAK GETTING WORSE PER SR#12832800 (AJR) /** 1) MN: A285129 SN: 0104596, *TAP: SIZE: A LOC: 158 FEET FROM P LINE AT PIETY, *MB: CODE: BE LOC: ON NO. DERBIGNY, 158' FROM P.L. PIETY, 7.5' OUT- ****/ | 2018-03-13 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK ON 5/8 INCH ABANDON INLET SERVICE FLOODING SIDEWALK MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201800250401 | 2018-01-30 | LEAD | 437 | S RENDON | BANKS | WILK | MI- LEAK AT THE STREET INLET SERVICE LEAK IN MUDPLOT FLOODING AREA /** 1) MN: 000000 SN: 0067049, *TAP: SIZE: B LOC: 188 FEET FROM P LINE AT BANKS, *MB: CODE: ADN2 LOC: ON S RENDON 201FT PL BANKS 8' OUTSIDE 3' INSIDE CU ** 2) MN: A116125 SN: 0067030, *TAP: SIZE: B LOC: 188 FEET FROM P LINE AT BANKS, *MB: CODE: BDN2 LOC: ON RENDON 187' FROM PL OF BANKS ****/ | 2018-03-08 | ARRIVED AT ABOVE LOCATION PUMPED AREA DOWN + FOUND NO LEAK WATER AT STAND STILL
201800250701 | 2018-01-30 | LEAD | 1416 | ALABO | N VILLERE | WILK | ML-METER LEAK EXAMINE INLET SERVICE FOR LEAK ON ABANDON SERVICE /** 1) MN: A183474 SN: 0104390, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT VILLERE N, *MB: CODE: D LOC: ON ALABO, 134' FROM P.L. NO. VILLERE, 7' OUTSIDE ****/ | 2018-03-06 | ARRIVED AT ABOVE LOCATION EXCAVATED IN MUD PLOT AND FOUND 5/8 INCH CURB COCK WITH LEAK AND REPAIRED
201800251001 | 2018-01-30 | LEAD | 1526 | MANDEVILLE |  | WILK | LOCATION ID-125922 MTR-A266297 LEAK AT AND AROUND MTR/MTR BOX FILLING UP INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A127680 SN: 0048546, *TAP: SIZE: A LOC: 128 FEET FROM P LINE AT CLAIBORNE AVE S, *MB: CODE: AEL LOC: ON MANDEVILLE 128.5' FROM URPL N CLAIBORNE AVE ****/ | 2018-03-08 | EXCAVATED 2 X 8 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH OUTLET SERVICE RENEW OUTLET SERVICE FROMMETER BOX TO LEAD LINE GOIN UNDER STEPS BACKFILL JOB WITH RIVERSAND COLDMILL
201800251401 | 2018-01-30 | LEAD | 1747 | INDEPENDENCE | N ROMAN | WILK | MW- LEAK ON THE SIDEWALK EXAMINE INLET SERVICE FOR LEAK /** 1) MN: SN: 0094036, *TAP: SIZE: A LOC: 30 FEET FROM P LINE AT ROMAN N, *MB: CODE: BD LOC: 30'PL N ROMAN 5.5' OUTSIDE PL 1.5' INSIDE CURB ON ****/ | 2018-03-13 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH ABANDON ILET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201800252601 | 2018-01-30 | LEAD | 3509 | NASHVILLE AV | S ROCHEBLAVE | WMTLK | ML-METER LEAK ACCT#154844-574884 METER#B033203 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: B030856 SN: 0091374, *TAP: SIZE: B LOC: 81 FEET FROM P LINE AT ROCHEBLAVE S, *MB: CODE: AF LOC: ON NASHVILLE AVE 82' FROM PL S ROCHEBLAVE 3' OUTSI ****/ DOTTIE READY 4-26-18 EXP 5-16-18 | 2018-04-26 | ARRIVED ON JOB SITE FOR INLET SERVICE LEAK EXCAVTED AND FOUND LEAK ON METER COCK ,MADE A 3 X 3 SIDEWALK CUT BACKFILLED AND DRESSED CUT UP,ALSO LEAD NEED TO BE REMOVED FROM WATER MAIN TO METER BOX. METER:B033203 FAC:62026246 MAKE:SENSUS READ:750
201800253301 | 2018-01-30 | LEAD/PLASTIC | 5456 | BELLAIRE DR | COUNTRY CLUB DR | WILK | ML-METER LEAK ACCOUNT #184592-596730 METER #C030623 INLET SERVICE LEAK IN MUDPLOT FLOODING DRIVEWAY 01/25/19 UPGRADE TO B LEVE IN SYSTEM PER INSPC L HEBERT (AJR) /** 1) MN: C017352 SN: 0137580, *TAP: SIZE: C LOC: 139 FEET FROM P LINE AT HYDT #3, *MB: CODE: AGKM LOC: 139FT FROM HYDT 3 ON BELLAIRE 9FT OUTSD PL 15FT IN ****/ | 2019-01-31 | EXAMINED & EXCAVATED OVER 1" METER IN TROO ROOTS TO MAKE REPAIRS ON INLET SERVICE IN MUDPLOT , RAISED TO GRADE AND DRESS UP & BACKFILLED
201800254801 | 2018-01-30 | LEAD/PLASTIC | 2508 | ST THOMAS |  | WLPR | LOCATION ID-123644 MTR-A323330 LOW PRESSURE EXAMINE INLET SERVICE FOR POOR PRESSURE /** 1) MN: A323330 SN: 0043386, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT SECOND, *MB: CODE: CD LOC: ON ST. THOMAS,66.3' FROM U.S.P.L. SECOND ****/ | 2018-02-24 | EXCAVATED AND REPLACED 3/4 OUTLET SERVICE MADE 4X5 SIDEWALK CUT BACKFILL HOLE
201800259301 | 2018-01-31 | LEAD | 2634 | GOV NICHOLLS | N DORGENOIS | WILK | **********PICK UP********** INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A249204 SN: 0020512, *TAP: SIZE: A LOC: 192 FEET FROM P LINE AT BROAD N, *MB: CODE: CF LOC: 192' P.L. N BROAD ****/ | 2018-02-12 | EXCAVATED 4 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INELT SERVICE MADE REPAIR ON INLET UNABLE TO RENEW INLET DUE TO CARS PARK ON JOB SITE RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILLED JOB WITH RIVERSAND COLDMILL
201800259401 | 2018-01-31 | LEAD | 1205 | SUMNER |  | WMRE | MI- LEAK AT THE SIDEWALK LOCATE METER & REPAIR INLET /** 1) MN: A208873 SN: 0095005, *TAP: SIZE: B LOC: 43 FEET FROM P LINE AT DE ARMAS, *MB: CODE: CD3 LOC: ON SUMNER 46FT FROM DE ARMAS ****/ | 2018-03-03 | EXAMINED METER EXCAVATED METER ODSERVED LEAK ON INLET SERVICE REPAIRED LEAK BACKFILLED
201800260301 | 2018-01-31 | LEAD/PLASTIC | 301 | PACIFIC AV | ATLANTIC AV | WILK | MI LEAK BETWEEN SIDEWALK / CURB WATER SHOOTING UP IN AIR **********S SLACK 12:51********** 1 " INLET LEAK SHOOTING IN AIR FROM REPAIRS MADE ON 01/22/18 HOLE OPEN INTERFERING WITH CONTRACTORS WORK /** 1) MN: C019587 SN: 0026917, *TAP: SIZE: B LOC: 35 FEET FROM P LINE AT PELICAN AVE, *MB: CODE: AD LOC: 35'FROM P L PELICAN MTR ON PACIFIC AVE ****/ | 2018-01-31 | ARRIVED ON JOB AN FOUND HOLE OPEN AND FLOODED CREW PUMP OUT WATER REMOVED ROCK & MUD FROM AROUND LEAKING LEAD LINE AND MADE ALL REPAIR TO TOP LEAK ALSO WHILE REMOVED ROCK & MUD WE DISCOVERED A GAS LEAK CALL ENTERGY TO COME MAKE REPAIR REFERRED TO ZONE 6 TO REMOVE LEAD LINE. JOB COMPLETE
201800260501 | 2018-01-31 | LEAD/PLASTIC | 1905 | PENISTON | DRYADES | WMTLK | LOCATION#103551-554748.METER#A398175. METER FILLS BACK UPWITH WATER AFTER BEING PUMPED OUT. MAY BE A POSSIBLE UNDERGROUND LEAK REPORTED BY THE INSPECTOR. /** 1) MN: A334353 SN: 0007446, *TAP: SIZE: B LOC: 54 FEET FROM P LINE AT PENISTON, *MB: CODE: BDH LOC: ON DRYADES 54FT FROM LSPL OF PENISTON ****/ | 2018-01-31 | EXCAVATED IN MUDPLOT ON INLET SERVICE AND FOUND COCK LEAKING. CREW MADE ALL REPAIR ON INLET SERVICE AND DRESSED JOB WITH SAND. JOB COMPLETE LJF
201800261401 | 2018-01-31 | LEAD | 901 | CLOUET | BURGUNDY | WILK | ML- METER LEAK ACCT# 181734-427538 MTR# A283964 EXAMINE INLET SERVICE FOR A LEAK SONEONE PARKING ON METER /** 1) MN: A283964 SN: 0146639, *TAP: SIZE: B LOC: 43 FEET FROM P LINE AT CLOUET, *MB: CODE: BDNH LOC: ON BURGUNDY, 43' FROM P.L. CLOUET, 7' OUTSIDE,3' ****/ | 2018-02-14 | EXCAVATED 3 X 2 BRICK SIDEWALK REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA LEFT BRICKS STACK ON SIDE OF THE HOUSE
201800261901 | 2018-01-31 | LEAD | 1435-33 | CLOUET | N VILLERE | WILK | ML METER LEAK METER # A409567 ACCOUNT # 219429-429543 EXAMINE INLET SERVICE FOR A LEAK /** AT 1433: 1) MN: A331448 SN: 0061758, *TAP: SIZE: A LOC: 43 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: CDL LOC: 44' P.L. N ROBERTSON ****/ | 2018-02-14 | EXAMINED AND FOUND NO LEAK
201800262601 | 2018-01-31 | LEAD/PLASTIC | 10825 | CURRAN BL | READ BL | WILK | ***************PICKUP*************** INLET SERVICE LEAKING FROM CURB COCK IN BOX FLOODING SIDEWALK AND GUTTER BOTTOM /** 1) MN: A180820 SN: 0137375, *TAP: SIZE: A LOC: 90 FEET FROM P LINE AT LAFRENIERE, *MB: CODE: ADK2 LOC: ON CURRAN 90FT FROM PL LAFOURCHE 9' OUTSIDE PL ****/ | 2018-02-01 | EXCAVATED IN MUDPLOT. REPAIR INLET & OUTLET SERVICE PLASTIC LINE. ALSO RAISE TO GRADE. DRESS UP WITH RIVER SAND. TAKE 3/4 LEAD LINE ON THE INLET SIDE. JOB REFER TO ZONE 5 TO TAKE LEAD LINE OUT LJF
201800263101 | 2018-01-31 | LEAD | 1626 | FRANCE | N CLAIBORNE AV | UNKN | MI- METER LEAK ACCT#156623-496972 METER# A427466 WATER IS GUSHING FROM METER **********CUSTOMER OUT OF WATER**********J GILLIAM14:26 UNABLE TO RESET METER DUE TO METER IN LOW LYING AREA THAT IS FLOODED /** 1) MN: A114786 SN: 0093777, *TAP: SIZE: B LOC: 215 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: CDL1 LOC: ON FRANCE, 215' FROM P.L. NO. CLAIBORNE AVE.,6' ****/ | 2018-01-31 | REMOVED CHOKE METER AND SET NEW ONE FOUND THE FIRST METER TO BELONG TO 2628 FRANCE AND SSECOND METER BELONG TO 2626 FRANCE ST MARKED THE CORRECT SIDEWALK SHOWING WHICH METER BELONGS TO YHE CORRECT ADDRESS OLD METER INFO: METER:A412425 FACT:14118187 MAKE:HERSEY READ:1074
201800263401 | 2018-01-31 | LEAD/PLASTIC | 2129 | HOLIDAY DR | COPERNICUS | WILK | ML-METER LEAK INLET SERVICE LEAK IN THE MUD PLOT FLOODING CURB /** 1) MN: A240526 SN: 0144099, *TAP: SIZE: B LOC: 1 FEET FROM P LINE AT COPERNICUS, *MB: CODE: ADK LOC: 1FT FROM P.L. COPERNICUS MTR ON HOLIDAY 4FT INSIDE ****/ | 2018-02-07 | EXAMINED METER BOX AND AREA AROUND BOX DIGGING UP TO INLET AND OUTLET TO EXAMINED MAKE SHOW THAT EITHER WAS NOT LEAKING BETERMINED THAT IT WAS A WASHER LEAK ALSO CHANGED OUT OUT HAND WHEEL
201800263801 | 2018-01-31 | LEAD | 2032 | PIETY | N GALVEZ | WILK | MI METER BOX LEAK EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A191330 SN: 0084803, *TAP: SIZE: A LOC: 192 FEET FROM P LINE AT GALVEZ N, *MB: CODE: AE5 LOC: R.S. 192' P.L. N GALVEZ ****/ | 2018-02-14 | RPLACED 5/8 WASHERS TO TO STOP LEAK
201800264001 | 2018-01-31 | LEAD | 2916 | CASTIGLIONE | N GAYOSO | WILK | MI LEAK ON THE SIDEWALK EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: B031854 SN: 0101371, *TAP: SIZE: B LOC: 131 FEET FROM P LINE AT ROSIERE, *MB: CODE: AD LOC: 131FT FROM PL ROSIERE 10' OUTSIDE PL ****/ | 2018-02-12 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 3/4 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOBB WITH RIVERSAND UNABLE TORENEW INLET DUE TO CAR PARK ON JOB SITE
201800265101 | 2018-01-31 | LEAD | 4721 | EASTVIEW DR | HAMMOND | WILK | **********PICKUP JOB********** ******CUSTOMER OUT OF WATER******** L FREEMAN @ 16:18PM INLET SERVICE LEAK IN MUDPLOT, FLOODING AERA /** 1) MN: A265515 SN: 0137993, *TAP: SIZE: B LOC: 109 FEET FROM P LINE AT HYDT. #7, *MB: CODE: ADMO LOC: ON EASTVIEW DR., 109' FROM P.L. HYDT. #7, 7' OUT- ****/ | 2018-01-31 | EXCAVATED IN MUDPLOT. REPAIR 5/8 STOP & WASTE LEAD LINE . DRESS UP WITH RIVER SAND. JOB REF ZONE 5 TO TAKE LEAD LINE OUT OF GROUND LJF
201800266302 | 2018-02-16 | LEAD/PLASTIC | 4785 | PAULINE DR | CONGRESS | WILK | INLET SERVICE LEAK /** 1) MN: A335497 SN: 0113314, *TAP: SIZE: A LOC: 548 FEET FROM P LINE AT MIRABEAU AVE, *MB: CODE: BDL LOC: ON PAULINE DR., 548' FROM P.L. MIRABEAU AVE., 6' ****/ | 2018-02-17 | ARRIVED ON JOB SITE AND EXCAVATED AND REPAIRED 5/8 INLET SERVICE LEAK BACKFILLED AND DRESS UP JOB SITE ALSO LEFT AND OUTLET WHIP NO METER UN METER BOX
201800267301 | 2018-01-31 | LEAD/PLASTIC | 1435 | JOSEPH | GARFIELD | WILK | WM LEAK ON THE SIDEWALK INLET SERVICE LEAK IN METER BOX BAD BLEEDER VALVE /** 1) MN: A238809 SN: 0018916, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT GARFIELD, *MB: CODE: CELM LOC: 100' P.L. GARFIELD ****/ | 2018-02-08 | EXCAVATED IN CONCRETE SIDEWALK. REPAIR 5/8 STOP AND WASTE. DRESS UP WITH RIVERSAND AND COLD MILL. ALSO REFER TO ZONE 3 TO TAKE LEAD OUTON THE IN-LET SIDE. JOB REF TO PAVE 4X4 CONCRETE S/W CUT
201800267701 | 2018-02-01 | LEAD | 2408 | REYNES | N ROCHEBLAVE | WILK | WM-LEAK ON THE SIDEWALK /** 1) MN: A280114 SN: 0132155, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BDL1 LOC: ON REYNES 75FT FROM ROCHEBLAVE 7FT OUTSIDE ****/ INLET ON ABANDON SERVICE IN FRONT OF EMPTY LOT | 2018-02-06 | EXAMINED JOB AT LOCATION FOUND NO LEAK IN MUD PLOT OR STREET
201800274001 | 2018-02-01 | LEAD | 6000 | CHARTRES |  | WMTLK | ML - METER LEAK ACCOUNT NUBMER - 131204-426125 A324348 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A319110 SN: 0161332, *TAP: SIZE: B LOC: 87 FEET FROM P LINE AT CHARTRES, *MB: CODE: CDJ LOC: ON ALABO, 71.5' FROM P.L. CHARTRES ****/ | 2018-02-23 | EXCAVATED 4 X 3 MUD PLOT MADE REPAIR ON INLET SERVICE TO STOP LEAK OUTLET HAS BEEN ALREADY NEWED BACKFILL AND CLEANED THE AREA
201800274601 | 2018-02-01 | LEAD/PLASTIC | 4010 | ST CHARLES AV | CONSTANTINOPLE | WILK | INLET SERVICE LEAK IN ASPHALT STREET FLOODING GUTTER BOTTOM ***DO NOT CREATE PAVING REFERRAL. DPW WILL PERFORM RESTORATION*** /** 1) MN: C022603 SN: 0059963, *TAP: SIZE: CC LOC: 115 FEET FROM P LINE AT CONSTANTINOPLE, *MB: CODE: ADLM LOC: ON ST. CHARLES AVE.,114' FROM P.L. CONSTANTINOPLE, ****/ | 2018-05-18 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 1 1/2 COUPLING LEAKING.REPLACED 3 FT .OF 1 1/2 TUBING TIED INTO LEAD .BACKFILLED AND COMPACKED TO GRADE WITH RIVER SAND AND COLDMILL..
201800275301 | 2018-02-01 | LEAD | 705 | GEN PERSHING | LAUREL | WMTLK | ML- METER LEAK ACCT# 116774-558574 MTR# A191175 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: A191175 SN: 0022791, *TAP: SIZE: A LOC: 50 FEET FROM P LINE AT LAUREL, *MB: CODE: ADN4 LOC: 47' P.L. LAUREL ****/ | 2018-05-10 | EXCAVATED IN MUDPLOT ON INLET ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND ALSO REFER TO ZONE 3 TO REMOVE LEAD
201800275302 | 2018-05-10 | LEAD | 705 | GEN PERSHING | LAUREL | WSNR | REFER TO ZONE TO REMOVE LEAD SERVICE ON INLET /** 1) MN: A191175 SN: 0022791, *TAP: SIZE: A LOC: 50 FEET FROM P LINE AT LAUREL, *MB: CODE: ADN4 LOC: 47' P.L. LAUREL ****/ DOTTIE READY 6-4-18 EXP 6-24-18 | 2018-06-10 | EXCAVATED IN S/W AND STREET OVERR 3/4 SERVICE TO REPLACE LEAD FROM W/M TO PROPERTY LINE FOUND 4" WATER MAIN BROKE AT 3/4 TAP .REPLACED 10 FT. OF 4" PVC PIPE AND REPLACED 29 FT. OF 3/4 TUBING TO PROPERTY LINE.(SOC 10FT. X 24 FT. CONCRETE BASE / 5FT. X 10 FT. S/W)
201800276201 | 2018-02-01 | LEAD | 2521-25 | URSULINES AV | N ROCHEBLAVE | WILK | RPML- METER LEAK MTR# A 276244 ACCT# 110181-523677 EXMINE INLET SERVICE FOR A LEAK /** AT 2521: 1) MN: A276244 SN: 0012520, *TAP: SIZE: A LOC: 171 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: CFL LOC: ON URSULINES AVE.,171' FROM L.S.P.L. N. ROCHEBLAVE ** AT 2525: 2) MN: A211903 SN: 0012521, *TAP: SIZE: A LOC: 171 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: CFL LOC: ON URSULINES AVE.,171' FROM L.S.P.L. N. ROCHEBLAVE ****/ | 2018-02-19 | ARRIVE AT ABOVE LOCATION FOUND LEAK ON 5/8 OUTLET SERVICE IN BOX EXCAVATED 4 X 6 MUD PLOT IN TREE ROOT RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY TIE INTO OLD GALVANIZE PIPE BACKFILL JOB WITH RIVERSAND CLEAN UP JOB SITE
201800277501 | 2018-02-01 | LEAD | 5850 | FLORIDA AV | ALABO | WILK | ML- METER LEAK SEWER # B036937 ACCT # 180672-421761 INLET SERVICE LEAK IN SIDEWALK /** 1) MN: SN: 0142179, *TAP: SIZE: B LOC: 122 FEET FROM P LINE AT ALABO, *MB: CODE: CEMO LOC: ON FLORIDA 122FT FROM PL ALABO 4FT OUTSIDE ****/ | 2018-02-28 | EXCAVATED 4 X 2 SIDEWALK CUT REPLACED 3/4 INCH METER BOX AND HANDWHEEL TO STOP LEAK BACKFILL AND CLEANED THE AREA
201800278101 | 2018-02-01 | LEAD | 1910 | ONZAGA | N PRIEUR | WILK | MI- LEAK BETWEEN SIDEWALK AND CURB INLET SERVICE LEAK IN MUDPLOT FLOODING AREA /** 1) MN: A321740 SN: 0079136, *TAP: SIZE: B LOC: 69 FEET FROM P LINE AT PRIEUR N, *MB: CODE: __ LOC: ON ONZAGA 69FT FROM PL N PRIEUR 7FT OUTSD PL ****/ | 2018-02-16 | EXAMINED JOB AT ABOVE LOCATION FOUND NO LEAK LEAK IS ON METER BOX AT 1914 ONZAGA
201800278301 | 2018-02-01 | LEAD | 700 | DELERY | ROYAL | WMLK | MI- LEAK IN STREET CAUSING SINKHOLE LEAK ON WATER MAIN IN ASPHALT STREET ON ROYAL /** 1) MN: A208924 SN: 0058903, *TAP: SIZE: A LOC: 51 FEET FROM P LINE AT DELERY, *MB: CODE: CDH6 LOC: ON ROYAL,51.5' FROM U.S.P.L. DELERY ****/ | 2018-03-08 | MADE 6 X 6 CUT IN BLACK TOP STREET AND MADE REPAIRS ON 3/4 INCH TAILPIECE FOR ABANDON SERVICE BACKFILL AREA
201800279201 | 2018-02-01 | LEAD/PLASTIC | 2945 | AMERICUS | MURL | WILK | ML- METER LEAK METER# C017397 ACCT# 231246-406782 INLET SERVICE LEAK /** 1) MN: C017397 SN: 0141785, *TAP: SIZE: C LOC: 200 FEET FROM P LINE AT MURL, *MB: CODE: CDN1 LOC: 204FT FROM P.L. MURL ****/ | 2018-03-08 | EXCAVATED METER BOX AND FOUND LEAK ON BOX COCK REPLACED BOX COCK
201800280001 | 2018-02-02 | LEAD | 1701 | PAINTERS | N DERBIGNY | WILK | LOCATION# 137839 CUSTOMER# 482928 METER# A338777 INSPECTOR DID AN OUTSIDE INSPECTION FOUND A STOP & GO CONSTANT REGISTRATION ON METER, CAN'T DETERMINE WHERE LEAK IS COMING FROM.......PLEASE REPAIR /** 1) MN: A338777 SN: 0068606, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT PAINTERS, *MB: CODE: CDHM LOC: ON N DERBIGNY 47FT FROM PL OF PAINTERS ****/ | 2018-02-19 | EXCAVATED 3 X 3 MUD PLOT FOUND NO LEAK OUTLET SERVICE LINE HAS BEEN RENEWED FROM METER BOX TO
201800282301 | 2018-02-02 | LEAD/PLASTIC | 4225 | HAMBURG |  | WMTLK | ML - METER LEAK ACCOUNT NUMBER - 302444-709985 METER NUMBER - A430827 EXAMINE INLET AND OUTLET SERVICE FOR LEAK WATER BUBBLING UP IN BOX, FLOODING SIDEWALK AND STREET 02/02/18 LEAK HAS GOTTEN WORSE PER INSPC (AJR) /** 1) MN: A154695 SN: 0107465, *TAP: SIZE: A LOC: 143 FEET FROM P LINE AT PELOPIDAS, *MB: CODE: BKO LOC: 143FT FROM PL PELOPIDAS MTR ON HAMBURG 7FT OUTSD ****/ | 2018-03-13 | EXCAVATED IN MUDPLOT THROUGH DEBRIS OVER A 5/8" INLET SERVICE LEAK BY HAND CHANGED THE COCK RAISE METER BOX UP TO GRADE BACKFILLED AND DRESS UP (LEAD INLET & PLASTIC OUTLET) JOB COMPLETE
201800282901 | 2018-02-02 | LEAD | 2509 | FRENCHMEN |  | WILK | INLET AND OUTLET NOT LINING UP, AND CAUSING LEAK. UNABLE TO LEAVE WATER ON. CUSTOMER IS HOME WAITING ON WATER. PLEASE REPAIR METER A427529 LOC ID 131387 INLET SERVICE NOT LINING UP PROPERLY ***HOUSE UNDER RENOVATIONS /** 1) MN: A284784 SN: 0062064, *TAP: SIZE: B LOC: 50 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: BD2 LOC: 54FT FROM PL DORGENOIS 2' INSIDE CURB ****/ | 2018-02-19 | EXCAVATED 2 X 2 GUTTER BOTTOM AND 3 X 3 MUD PLOT RELOCATED METER BOX FROM GUTTER TO MUD PLOT OUTLET SERVICE LINE RENEWED TO PROPERTY BACKFILL AND CLEANED THE AREA
201800284101 | 2018-02-02 | LEAD | 1722 | ESPLANADE AV | N ROMAN | WILK | ML - METER LEAK MTR # A421238 ACCT # 126354-525534 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A209730 SN: 0050150, *TAP: SIZE: A LOC: 136 FEET FROM P LINE AT ROMAN N, *MB: CODE: ADLN LOC: 134' P.L. N ROMAN ****/ | 2018-02-16 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACE 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA
201800284501 | 2018-02-02 | LEAD/PLASTIC | 3728 | PIN OAK AV | TALL OAKS DR | WOLK | ML METERLEAK MTR#A412546 ACCT#233409-703047 CONS REG ON METER /** 1) MN: A335118 SN: 0151501, *TAP: SIZE: B LOC: 332 FEET FROM P LINE AT TALL OAK DR, *MB: CODE: BFK LOC: RES. 332FT FROM PL TALL OAKS ****/ | 2018-02-26 | EXCAVATED METER BOX AND REPLACED OUTLET FROM BOX TO PROPERTY METER REQISTERING CUSTOMER HAS SMALL LEAK ON PROPERTY
201800284601 | 2018-02-02 | LEAD/PLASTIC | 314 | HUNTLEE DR | GALLATIN | WILK | WM LEAK IN THE STREET INLET SERVICE LEAK BETWEEN STREET & CURB /** 1) MN: A340950 SN: 0117799, *TAP: SIZE: A LOC: 220 FEET FROM P LINE AT COPERNICUS, *MB: CODE: BFL LOC: 220'FROM P L COPERNICUS ****/ | 2018-03-28 | BROKE THE STREET AND EXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOBSITE
201800286001 | 2018-02-02 | LEAD | 2217 | ALMONASTER AV | N MIRO | WMTLK | ML-METER LEAK ACCT#167033-538977 METER#A347228 EXAMINE INLET/ OUTLET SERVICE FOR A LEAK AREA SARURATED /** 1) MN: C028398 SN: 0107873, *TAP: SIZE: C LOC: 128 FEET FROM P LINE AT MIRO N, *MB: CODE: OOO LOC: ON ALMONASTER AVE 127.5' FROM PL N MIRO 9' OUTSIDE ** 2) MN: 000000 SN: 0107873, *TAP: SIZE: B LOC: 3 FEET FROM P LINE AT MIRO N, *MB: CODE: OOO LOC: ON ALMONASTER 4FT FROM PL N MIRO 4FT INSD CURB ****/ | 2018-02-23 | ARRIVED AT ABOVE LOCATION FOUND CUSTOMER HAD ONE METER SERVING 2 APARTM,ENT WITH 2 STOP + WASTE VALVE TID INTO TOGETHER CAUSING OUTLET LEAK IN EMPTY METER REFER BACK TO PROPERTY OWNER TO GET PRIVATE PLUMBER TO FIX PLUMBER UNDER THE HOUSE
201800289001 | 2018-02-03 | LEAD | 5431 | DAUPHINE | FLOOD | WILK | ML METER LEAK ACCT# 109894-425242 METER# A151435 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: SN: 0063086, *TAP: SIZE: A LOC: 337 FEET FROM P LINE AT FLOOD, *MB: CODE: AF LOC: ON DAUPHINE 337FT FROM FLOOD BY FENCE ****/ | 2018-03-16 | ARRIVED AT ABOVE LOCATION FOUND LEAK ON 5/8 INCH CURB COCK + REPAIRED IT BACKFILLED (NEED MATERIAL)
201800289103 | 2018-04-12 | LEAD | 3220 | PALMYRA | S LOPEZ | WMRE | ARRIVED AT ABOVE LOCATION EXAMINED JOB TO FIND METER EXCAVATED ON METER BOX MEASUREMENT UNABLE TO LOCATE NEED MACHINE /** 1) MN: A305967 SN: 0049008, *TAP: SIZE: B LOC: 168 FEET FROM P LINE AT LOPEZ S, *MB: CODE: CFL6 LOC: ON PALMYRA,168.2' FROM U.S.P.L. SO. LOPEZ ****/ | 2018-04-13 | EXCAVATED IN MUD PLOT + LOCATED 5/8 ICH METER BACKFILLED + DRESSED UP AREA
201800289203 | 2018-04-12 | LEAD | 3220 | PALMYRA | S LOPEZ | WMRE | ARRIVED AT ABOVE LOCATION EXAMINED JOB TO FIND METER EXCAVATED ON METR BOX MEASUREMENT UNABLE TO LOCATE /** 1) MN: A305967 SN: 0049008, *TAP: SIZE: B LOC: 168 FEET FROM P LINE AT LOPEZ S, *MB: CODE: CFL6 LOC: ON PALMYRA,168.2' FROM U.S.P.L. SO. LOPEZ ****/ | 2018-04-13 | EXAMINED IN MUD PLOT + LOCATED 5/8 INCH METER BOX BACKFILLED AND DRESSED UP AREA
201800292902 | 2018-02-03 | LEAD | 315 | S ROCHEBLAVE | PALMYRA | WMRE | METER LOCATED IN S/W METER TO BE RESET CANNOT GET TO COCK OR WHEEL. OLD METER BOX LEFT IN HOLE AND NEW BOX PUT IN WITH OLD MATERIAL /** 1) MN: C026257 SN: 0040361, *TAP: SIZE: C LOC: 122 FEET FROM P LINE AT PALMYRA, *MB: CODE: ADL2 LOC: 123FT FROM PL PALMYRA 8' OUTSIDE PL ON S ROCHEBLAV ** 2) MN: SN: 0040361, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT PALMYRA, *MB: CODE: __ LOC: 134' P.L. PALMYRA ****/ | 2018-04-06 | ARRIVED AT ABOVE LOCATION FOUND METER BOX SHIFITED + SET IT CORRECT WHERE THEY CAN GET TO CURB COCK + HANDWHEEL + MARKED
201800300501 | 2018-02-04 | LEAD | 517 | UPPERLINE | TCHOUPITOULAS | WMTLK | ML- METER LEAK AREA FLOODED METER#A213954 ACCT#119026-562129. EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A213954 SN: 0048002, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT TCHOUPITOULAS, *MB: CODE: BEL1 LOC: INSIDE BY GATE 116' P.L. TCHOUPITOULAS ****/ | 2018-05-10 | EXAVATED IN DRIVEWAY ON INLET AND OUTLET LEAK ON LEAD MADE ALL REPAIRS AND RENEW METER BOX COMPLETE BACKFILL WITH RIVERSAND AND COLD MILL REFER TO ZONE 3 TO REMOVE LEAD ************OLD METER INFORMATION******* METER:A213954 FAC:28479906 MAKE:ROCKWELL READ:9654
201800300502 | 2018-05-10 | LEAD | 517 | UPPERLINE | TCHOUPITOULAS | WSNR | UNABLE TO REMOVE METER. TREE ROOTS HAVE TAKEN OVER METER BOX. BOX MAY NEED TO BE RELOCATED. PLEASE REPAIR AND REMOVE METER A334181. LOC ID 152452 RELOCATE METER OUT OF TREE ROOTS /** 1) MN: A213954 SN: 0048002, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT TCHOUPITOULAS, *MB: CODE: BEL1 LOC: INSIDE BY GATE 116' P.L. TCHOUPITOULAS ****/ | 2018-05-30 | GIVE TO CONTRACTOR JOB REFERRED (6500W)
201800300503 | 2018-05-30 | LEAD | 517 | UPPERLINE | TCHOUPITOULAS | WSNR | UNABLE TO REMOVE METER. TREE ROOTS HAVE TAKEN OVER METER BOX. BOX MAY NEED TO BE RELOCATED. PLEASE REPAIR AND REMOVE METER A334181. LOC ID 152452 RELOCATE METER OUT OF TREE ROOTS /** 1) MN: A334181 SN: 0053346, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT THIRD, *MB: CODE: BDHT LOC: ON CHESTNUT 98' FROM PL THIRD 7' OUTSIDE PL 2' INS ****/ /** 1) MN: A213954 SN: 0048002, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT TCHOUPITOULAS, *MB: CODE: BEL1 LOC: INSIDE BY GATE 116' P.L. TCHOUPITOULAS ****/ | 2018-06-30 | REFFERED TO CONTRACTOR CONTRACT 2126 WPR W DRENNAN
201800302701 | 2018-02-05 | LEAD | 1809 | ROBERT | DANNEEL | WILK | ML- METER LEAK ACCT# 129137-578804 MTR# A290371 INLET SERVICE LEAK /** 1) MN: A290371 SN: 0057642, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT DANNEEL, *MB: CODE: CD LOC: ON ROBERT 110.4FT FROM PL OF DANNEEL ****/ | 2018-04-05 | EXCAVATED IN MUD PLOT. REPAIR 5/8 STOP & WASTE LEAD LINE . DRESS UP WITH RIVERSAND. JOB REFER TO ZONE 3 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX.
201800302702 | 2018-04-05 | LEAD | 1809 | ROBERT | DANNEEL | WSNR | JOB REFER TO ZONE 3 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX. /** 1) MN: A290371 SN: 0057642, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT DANNEEL, *MB: CODE: CD LOC: ON ROBERT 110.4FT FROM PL OF DANNEEL ****/ DOTTIE READY 4-23-18 EXP 5-13-18 | 2019-01-06 | EXCAVATED IN TREE ROOTS AND REPLACED 3/4 INCH LEAD FROM CURB TO METER BOX BACKFILLED AREA
201800303501 | 2018-02-05 | LEAD/PLASTIC | 5871 | BELLAIRE DR | W KENILWORTH | WILK | WM LEAK IN THE STREET INLET SERVICE LEAK IN MUDPLOT FLOODING AREA /** 1) MN: C025033 SN: 0142803, *TAP: SIZE: C LOC: 223 FEET FROM P LINE AT SHARON DR, *MB: CODE: CDN1 LOC: 223FT FROM PL SHARON ON BELLAIRE ****/ | 2018-08-03 | EXCAVATED IN MUDPLOT RENEWED 1'' INLET SERVICE FROM METERBOX TO CRUB AND RAISED METER BOX TO GRADE. OUTLET HAS COPPER & INLET HAS PLASTIC AT COUB STREET SIDE. ALSO BACKFILLED DRESSED JOB WITH RIVER SAND.
201800304001 | 2018-02-05 | LEAD/PLASTIC | 417 | DE ARMAS | TECHE | WILK | ML- METER LEAK ACCT#224771-4701457 METER# A352690 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A302292 SN: 0052587, *TAP: SIZE: A LOC: 135 FEET FROM P LINE AT TECHE, *MB: CODE: BD LOC: ON DE ARMAS 135' FROM TEHCE ****/ | 2018-06-14 | EXAMINED AREA OBSERVED LEAK ON INLET SERVICE EXCAVATED METER BOX EXPOSED BOTH INLET AND OUTLET SERVICE NREMOVED LEAD LINE TO PROPERTY LEAD FOUND ON INLET REPAIRED LEAK BACKFILLED CLEANED AREA ALSO RAISED METER BOX TO BRADE
201800304301 | 2018-02-05 | LEAD | 1818 | LAHARPE | N ROMAN | WILK | MI-LEAK IN SIDEWALK CHANGED FROM 1814-16 LAHARPE INLET ON ABANDON SERVICE INFRONT VACANT LOT /** 1) MN: SN: 0032089, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT PRIEUR N, *MB: CODE: ADK LOC: ON LA HARPE 146.5FT FROM ROMAN N ** 2) MN: SN: 0024064, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT PRIEUR N, *MB: CODE: ADK LOC: ON LAHARPE 146' FROM PL N. ROMAN 10' OUTSIDE PL 2' ****/ | 2018-03-12 | EXCAVATED 4 X 4 CONCRETET SIDEWALK FOUND LEAK ON ABANDON 5/8 INCH SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND COLDMILL
201800304701 | 2018-02-05 | LEAD | 5465 | MARAIS | FLOOD | WILK | ML- METER LEAK METER# A369414 ACCT# 211809-423307 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A285481 SN: 0089764, *TAP: SIZE: B LOC: 58 FEET FROM P LINE AT FLOOD, *MB: CODE: CD LOC: ON FLOOD 60'FROM P.L. MARAIS 8' OUTSIDE 3'INSIDE ****/ | 2018-03-14 | ARRIVED AT ABOVE LOCATION EXCAVATED IN GUTTER BOTTOM FOUND 5/8 INCH CURB COCK LEAKING + REPAIRED IT BACKFILL + CLEANED AREA
201800305501 | 2018-02-05 | LEAD/PLASTIC | 7322 | WILLOW | LOWERLINE | WMTLK | MI-LEAK AT CURB NEAR CATCHBASIN ON DOWNTOWN SIDE OF STREET EXAMINE INLET & OUTLET SERVICE ON A LARGE METER IN THE MANHOLE FOR A LEAK /** 1) MN: D005584 SN: 0133203, *TAP: SIZE: C LOC: 17 FEET FROM P LINE AT WILLOW, *MB: CODE: CDHP LOC: IN MANHOLE ON LOWERLINE 16FT FROM PL WILLOW ****/ | 2018-02-16 | EXCAVATED IN MUD PLOT THROUGH DEBRIS TO REPAIR A 1.50 SERVICE FROM THE CURB TO REPLACE 4 FT OF 1.50 LEAD FROM CURB TO METER INSIDE MANHOLE
201800307401 | 2018-02-05 | LEAD | 3318 | N RAMPART | PIETY | WOLK | ML METER LEAK METER# A426786 ACCT# 222293-428095 EXAMINE OUTLET SERVICE FOR LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-03-07 | ARRIVED AT ABOVE LOCATION AND REPAIRED 5/8 INCH HANDWHEEL "CLEANED AREA"
201800307801 | 2018-02-05 | LEAD/PLASTIC | 4708 | GEN MEYER AV | RIVER OAKS DR | WILK | ML- METER LEAK ACCT#235257-410722 METER#A314332 INLET SERVICE LEAK IN DITCH /** 1) MN: A314332 SN: 0160321, *TAP: SIZE: C LOC: 129 FEET FROM P LINE AT RIVER OAKS DR, *MB: CODE: OOOO LOC: 162' PL RIVER OAKS - 3' OUT - 10' IN CURB ****/ | 2018-04-04 | EXAMINED JOB EXCAVATED BY HAND ON INLET SIDE OF METER DISCOVERED SPLIT IN PLASTIC FIXED ADDING STOP COCK AND RECONNECTING TO STOP LEAK
201800307901 | 2018-02-05 | LEAD/PLASTIC | 309 | HENDEE |  | WILK | ML METER LEAK ACCOUNT #236376403547 METER #A386554 INLET SERVICE LEAK @ METER IN GRASS /** 1) MN: A117525 SN: 0166469, *TAP: SIZE: B LOC: 23 FEET FROM P LINE AT ALIX, *MB: CODE: __ LOC: ON HENDEE, 4' FROM D.P.L. ALIX, 12' INSIDE CURB ****/ | 2018-03-14 | FIX THE LEAK PUIT IN 1 STOP COCK AND 1 CAN I GO BACK DRESS UP
201800308001 | 2018-02-05 | LEAD | 1409 | ST ANTHONY AV |  | WILK | MI- LEAK AT THE SIDEWALK INLET SERVICE LEAK FLOODING SIDEWALK/CURB /** 1) MN: B021803 SN: 0074184, *TAP: SIZE: B LOC: 78 FEET FROM P LINE AT VILLERE N, *MB: CODE: CDLM LOC: 78' P.L. N VILLERE ****/ | 2018-03-12 | EXCVAVTED 2 X 8 CONCRETET SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY TIE INTO GALVANIZE PIPE BACKFILLED JOB WITH RIVERSAND COLDMILL
201800308701 | 2018-02-05 | LEAD | 4508 | ST CLAUDE AV | KENTUCKY | WMTBG | MI: RAISE METER TO GRADE ACCT# 301907-486132 METER# A428829 ADJUST METER BOX TO PROPER GRADE /** 1) MN: SN: 0060115, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT KENTUCKY, *MB: CODE: AFL LOC: ON ST. CLAUDE AVE.,71.4' FROM L.R.P.L. KENTUCKY ****/ | 2018-03-02 | EXCAVTED 3 X 3 MU DPLOT RAISED METER BOX UP TO GRADE BACKFILL AND CLEANED THE AREA
201800308801 | 2018-02-05 | LEAD | 2219 | N BROAD | A P TUREAUD AV | WILK | ML- METER LEAK METER#A254697 ACCT#154527-492532 INLET SERVICE LEAK /** 1) MN: A254697 SN: 0090819, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT AGRICULTURE, *MB: CODE: AGMF LOC: 131' FROM PL AGRICULTURE 1.5' OUTSIDE PL 11' INSID ****/ | 2018-03-08 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201800315501 | 2018-02-06 | LEAD | 3961 | LAUREL | CONSTANTINOPLE | WILK | ML- METER LEAK ACCT # 122271-557264 METER # A354533 INLET SERVICE LEAK IN THE MUD PLOT FLOODING MUD PLOT & SIDEWALK 05/14/18 CUSTOMER STATES LEAK IS GETTING WORSE (KSW) /** 1) MN: A128510 SN: 0040422, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT CONSTANTINOPLE, *MB: CODE: AGM LOC: ON LAUREL 130.6FT FROM PL OF CONSTANTINOPLE ****/ | 2018-06-12 | REPLACED 5/8 CURB COCK TIED INTO LEAD.
201800315502 | 2018-06-13 | LEAD | 3961 | LAUREL | CONSTANTINOPLE | WSNR | WSNR WATER -SERVICE - NEEDS REPAIR (TRUCK 594 REPLACED BAD CURB COCK BUT LEAD NEEDS TO BE REMOVED FROM MAIN TO METER BOX.)(DOTTIE IS NEEDED) /** 1) MN: A128510 SN: 0040422, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT CONSTANTINOPLE, *MB: CODE: AGM LOC: ON LAUREL 130.6FT FROM PL OF CONSTANTINOPLE ****/ | 2019-01-06 | EXCAVATED IN MUD PLOT AND REPLACED 3/4 INCH OUTLET TO PROPERTY BACKFILLED AREA
201800315601 | 2018-02-06 | LEAD | 2117 | FOUCHER | S SOLOMON | WILK | WM LEAK ON THE SIDEWALK INLET SERVICE LEAK IN THE MUD PLOT FLOODING MUD PLOT & GUTTER BOTTOM WITH SOME WATER GETTING OFF IN THE DCB 02/14/18 LEAK HAS GOTTEN WORSE PER SR#12831860 (AJR) 02/19/18 LEAK IN THE STREET HAS GOTTEN WORSE (KSW) 02/23/18 CUSTOMER STATES LEAK IS GETTING WORSE (KSW) 03/02/18 LEAK HAS GOTTEN WORSE PER RR#12834059 (AJR) 03/26/18 AREA FLOODED CUSTOMER NOW OUT OF WATER JOB UPGRADED TO PRIORITY -A- SENT TO ZONE 7 PRINTER PER INSP B BOURNES *CHANGED TO 2117-19 FOUCHER (FCP) /** 1) MN: A259111 SN: 0039841, *TAP: SIZE: A LOC: 173 FEET FROM P LINE AT LOYOLA AVE, *MB: CODE: CFLM LOC: ON FOUCHER ST 173.7' FROM LRPL LOYOLA AVE ****/ | 2018-03-26 | EXCAVATED IN MUDPLOT. REPAIR 3/4 LEAD LINE. DRESS UP WITH RIVERSAND ALSO RESET 5/8 METER A427973 REFER TO ZONE 3 TO TAKE LEAD LINE FROM THE WATER MAIN TO METER BOX OLD METER INFO: A295548 FACT: 50332317 MAKE: SENSUS READ:19722
201800315602 | 2018-03-26 | LEAD | 2117-19 | FOUCHER | LOYOLA AV | WSNR | REFER TO ZONE 3 TO TAKE LEAD LINE FROM THE WATER MAIN TO METER BOX /** AT 2117: 1) MN: A259111 SN: 0039841, *TAP: SIZE: A LOC: 173 FEET FROM P LINE AT LOYOLA AVE, *MB: CODE: CFLM LOC: ON FOUCHER ST 173.7' FROM LRPL LOYOLA AVE ****/ DOTTIE READY 4-2-18 EXP 4-22-18 | 2018-04-15 | EXCAVATED IN ASPHALT STREET AND MUD PLOT AND REMOVED 25 FT. OF 3/4 LEAD INLET AND OUTLET SERVICE LINES. ALSO RELOCATEDE 5/8 METER BOX FROM BUSHES TO MUDPLOT. COMPACTED BACKFILLED AND DRESSED UP AREA.
201800316501 | 2018-02-06 | LEAD | 5932 | MAGAZINE | ELEONORE | WOLK | ML-METER LEAK ACCT#105599-564471 METER#A423852 OUTLET SERVICE LEAK BEHIND HANDWHEEL FLOODING SIDEWALK, ALSO A DEPRESSION IN FRONT BOTH METERS WHERE PREVIOUS REPAIRS WAS MADE. /** 1) MN: A248738 SN: 0007454, *TAP: SIZE: A LOC: 114 FEET FROM P LINE AT ELEONORE, *MB: CODE: CM LOC: 114' P.L. ELEONORE ****/ DOTTIE READY 2-12-18 EXP 3-4-18 | 2018-02-12 | ARRIVED AT THE ABOVE LOCATION MADE REPAIRS ON THE INLET AND ALSO REPLACE 3/4 LEAD LINE ON THE OUTLET TO CUSTOMER PIPE ,INSIDE A 4 X 4 SIDEWALK CUT CUSTOMER PIPE IS LEAKING ALSO.
201800319701 | 2018-02-06 | LEAD/PLASTIC | 309 | WALLACE DR | PELOPIDAS | WILK | ML- METER LEAK ACCT#165937-501428 METER#A356024 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A311511 SN: 0106504, *TAP: SIZE: B LOC: 198 FEET FROM P LINE AT ST ANTHONY, *MB: CODE: AD LOC: ON WALLACE DR., 198' FROM P.L. ST. ANTHONY, 7' OUT ****/ | 2018-03-05 | EXCAVATED A 7 X 5 MUD PLOT CUT TO REPAIR INLET SERVICE ALSO FOUND LEAD ON INLET SERVICE RENEWE OUTLET SERVICE FROM METER TO P.L JOB CONT TO REMOVE LEAD ON INLET
201800320001 | 2018-02-06 | LEAD/PLASTIC | 4419 | ANNUNCIATION |  | WMRE | SERVICE BURIED. PLEASE LOCATE AND CHANGE METER A240964 LOC ID 106793 LOCATE WATER SERVICE & CHANGE ONE 5/8 METER /** 1) MN: A240964 SN: 0008506, *TAP: SIZE: B LOC: 185 FEET FROM P LINE AT NAPOLEON AVE, *MB: CODE: AEW2 LOC: AT 23 HPL SIDEWALK ON ANNUNCIATION 185' FROM USPL ****/ | 2018-06-10 | CHANGED 5/8 METER COCK TIED BACK INTO LEAD .CHANGED 5/8 HANDWHEEL TIED INTP COOPER.MADE 3X 5 CUT IN SIDEWLK.SET 5/8 METER REMOVE OLD METER .RAISED TO GRADE. OLD METER INFO: A240964 FACT:32258241 MAKE: ROCKWELL READ: 4825
201800321201 | 2018-02-06 | LEAD | 5914 | N RAMPART | GORDON | WILK | MI- LEAK IN THE SIDEWALK INLET SERVICE LEAK AT CURB /** 1) MN: A260314 SN: 0103680, *TAP: SIZE: A LOC: 50 FEET FROM P LINE AT GORDON, *MB: CODE: AD LOC: LPL CURB 50FT FROM PL GORDON 7' OUTSIDE ****/ | 2018-03-13 | EXCAVATED 4 X 4 MUD PLOT RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILL JOB WITH RIVERSAND NO LEAK ON INLET
201800321301 | 2018-02-06 | LEAD | 2311 | CONTI | N MIRO | WILK | ML METER LEAK ACCT# 207669-702849 METER# A428291 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A329123 SN: 0052349, *TAP: SIZE: __ LOC: 9 FEET FROM P LINE AT TONTI N, *MB: CODE: __ LOC: ON CONTI 8FT FROM D.P.L. N TONTI 9FT OUTSIDE P.L. ****/ | 2018-03-08 | ARRIVED AT AOVE EXCAVATED IN MUD PLOT FOUND 5/8 INCH CURB LEAKING BACKFILLED
201800325201 | 2018-02-07 | LEAD/PLASTIC | 525 | WHITNEY AV | ELIZA | WILK | ML- METER LEAK METER# A352904 ACCT# 227371-403331 INLET SERVICE LEAK IN SIDEWALK /** 1) MN: A290418 SN: 0114017, *TAP: SIZE: B LOC: 228 FEET FROM P LINE AT ELIZA, *MB: CODE: AE LOC: ON WHITNEY AVE., 28' FROM P.L. ELIZA, 5' OUTSIDE ****/ | 2018-03-29 | EXAMINED METER USED AIR GUN TO BREAK CONCRETE AROUND METER EXCAVATED ON INLET AND OUTLET SERVICE OBSERVED LEAK ON BOTH INLET AND OUTLET SERVICE REPAIRED LEAD BACKFILLED AND CLEANED SITE
201800326501 | 2018-02-07 | LEAD/PLASTIC | 121 | PINEWOOD CT | CYPRESS ACRES DR | WILK | ML- METER LEAK METER # A400891 ACCT # 235925-407228 ********S.SLACK @ 12:54PM********* INLET SERVICE LEAK IN MUDPLOT FLOODING AREA CUSTOMER OUT OF WATER /** 1) MN: A220670 SN: 0164441, *TAP: SIZE: A LOC: 8 FEET FROM P LINE AT CYPRESS ACRES DR, *MB: CODE: OOO LOC: ON PINWOOD 8FT FROM PL CYPRESS ACRES 9FT OUTSD ****/ | 2018-02-07 | EXAMINE JOB FOUND CAR ROLLED OVER METER BOX SEPARATED 5/8 BOX COCK FROM 5/8 METER PUSH METER BACK IN CHANGE 5/8 WASHERS
201800326601 | 2018-02-07 | LEAD/PLASTIC | 2367 | LAUREL | 1ST | WILK | ML METER LEAK ACCOUNT #113697-429798 ,METER #A120346 INLET SERVICE LEAK BAD BLEEDER VALVE LEAK FLOODING GRASS & SIDEWALK /** 1) MN: A120346 SN: 0045710, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT 1ST, *MB: CODE: CEL LOC: BET 1ST AND PHILIP 64FT FR PL 1ST ****/ | 2018-03-12 | EXAMINED METER REMOVED BRICKS EXCAVATED METER OBSERVED LEAK ON INLETR SERVICE REPAIRED LEAK LEAD FOUND ON INLET SERVICE BACKFILLED SAND AND COLDMILL
201800330001 | 2018-02-07 | LEAD/PLASTIC | 2134 | ST NICK | COPERNICUS | WILK | ML METER LEAK ACCT# 230873-409897 METER# A259708 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A259708 SN: 0141083, *TAP: SIZE: C LOC: 139 FEET FROM P LINE AT COPERNICUS, *MB: CODE: C LOC: ON ST NICK DR 139' FORM PL COPERNICUS 7' OUTSIDE P ****/ | 2018-03-12 | EXAMINED METER EXCAVATED METER EXPOSED INLET AND OUTLET SERVICE OBSERVED LEAK ON INLET SERVICE REPAIRED INLET SERVICE LEAK BACKFILLED AND CLEANED AREA
201800330301 | 2018-02-07 | LEAD | 810 | ESPLANADE AV | BOURBON | WILK | MI-LEAK IN THE STREET INLET SERVICE LEAK IN CONCRETE STREET 05/09/18 LEAK GETTING WORSE (KSW) /** 1) MN: D006031 SN: 0030348, *TAP: SIZE: D LOC: 74 FEET FROM P LINE AT BOURBON, *MB: CODE: ADM5 LOC: ON ESPLANADE AVE 73' FROM PL BOURBON 3' OUTSIDE PL ** 2) MN: SN: 0030348, *TAP: SIZE: A LOC: 66 FEET FROM P LINE AT BOURBON, *MB: CODE: __ LOC: ON ESPLANADE AVE 66' FROM URPL BOURBON ****/ | 2018-06-14 | MADE TWO CUT IN ASPHALT STREET IN SEARCH OF LEAK MADE REPAIR ON 3/4 INCH INLET SERVICE LINE IN SECOND CUT COMPACTED BACKFILL + DRESSED UP AREA
201800331401 | 2018-02-08 | LEAD | 2025 | DAUPHINE | TOURO | WILK | ML- METER LEAK ACCT# 120592-485494 MTR# A241610 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A241610 SN: 0036452, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT FRENCHMEN, *MB: CODE: CELD LOC: METER ON DAUPHINE 112 FT FROM PL FRENCHMEN ****/ | 2018-02-22 | EXCAVATED 4 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INELT SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND COLDMILL
201800333301 | 2018-02-08 | LEAD | 1837-39 | SONIAT | UPPERLINE | WILK | ML-METER LEAK ACCOUNT #125762-558943 METER #A355627 INLET SERVICE LEAK IN THE MUD PLOT IN FRONT OF METER FLOODING MUD PLOT & GUTTER BOTTOM /** AT 1837: 1) MN: A229758 SN: 0048208, *TAP: SIZE: A LOC: 80 FEET FROM P LINE AT UPPERLINE, *MB: CODE: ADHO LOC: ON SONIAT ST 80' FROM UPL UPPERLINE ** AT 1839: 2) MN: A302312 SN: 0048208, *TAP: SIZE: A LOC: 79 FEET FROM P LINE AT SONIAT, *MB: CODE: ADHO LOC: ON SARATOGA ST 78.7' FROM LPL SONIAT ****/ DOTTIE READY 8-16-18 EXP 9-5-18 | 2018-08-19 | EXCAVATED AND MADE REPAIR ON 3/4 INCH INLET SERVICE MADE 4 X 5 MUD PLOT CUT BACKFILL HOLE.
201800334301 | 2018-02-08 | LEAD/PLASTIC | 1812 | SHIRLEY DR |  | WILK | ML - METER LEAK ACCT#226450-405360 METER#B041548 INLET SERVICE LEAK IN BOX /** 1) MN: B028069 SN: 0129780, *TAP: SIZE: C LOC: 205 FEET FROM P LINE AT VESPASIAN, *MB: CODE: BE24 LOC: ON SHIRLEY DR., 182' FROM P.L. VESPASIAN, 5' OUT- ****/ | 2018-03-12 | EXAMINED METER EXCAVATED METER UNDERMAINED UNDER SIDEWALK OBSERVED LEAK ON INLET SERVICE LINE BACKFILLED AND CLEANED AREA
201800334402 | 2018-03-07 | LEAD/PLASTIC | 1813 | SHIRLEY DR |  | WOLK | CUT THICK CONCRETE IN DRIVEWAY WITH AIR GUN AND CUT WIRES EXPOSED PROPERTY AND FOUND LEAK ON PROPERTY SIDE LEAD NEED TO BE REMOVED FROM BOX TO PROPERTY GIVE JOB TO ZONE 7 HOLE OPEN AND BARRICADED OFF /** 1) MN: B029131 SN: 0122856, *TAP: SIZE: __ LOC: 143 FEET FROM P LINE AT VESPASIAN, *MB: CODE: BDN5 LOC: ON SHIRLEY DR., 161' FROM P.L. VESPASIAN, 5.5' OUT ****/ | 2018-03-07 | ARRIVED ON JOBSITE EXAMINED FOUND LEAK ON OUTLET BROKE UP CONCRETE EXCAVATYED BY HAND REPAIRED LEAK AND BACKFILLED
201800334501 | 2018-02-08 | LEAD | 2333 | ST ROCH AV | PEACE CT | WILK | ML - METER LEAK METER#A315272 INLET SERVICE LEAK IN BOX /** 1) MN: A315861 SN: 0076036, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT PEACE CT, *MB: CODE: CDMN LOC: ON ST ROCH AVE 76FT FROM PL OF PEACE CT ****/ | 2018-02-22 | EXCAVATED 4 X 3 SIDEWALK CUT RENEWED OUTLET SERVICE LINE UP TO PROPERTY AND RELOCATED METER BOX TO SIDEWALK BACKFILLED AND CLEANED THE AREA
201800337301 | 2018-02-08 | LEAD | 7718 | NELSON | ADAM | WILK | ML - METER LEAK METER#A414601 INLET SERVICE LEAK /** 1) MN: A130461 SN: 0088578, *TAP: SIZE: B LOC: 126 FEET FROM P LINE AT ADAMS, *MB: CODE: AD LOC: ON NELSON,126' FROM P.L. ADAMS,10' OUTSIDE P.L., ****/ | 2018-07-01 | ARRIVED AT ABOVE LOCATION EXCAVATED IN MUDPLOT FOUND 5/8 CURB COCK LEAKING ON LEAD LINE AND REPAIRED. BACKFILLED **************OLD METER INFO********** METER:A414601 FAC:14120363 MAKE:HERSEY READ:756
201800340301 | 2018-02-09 | LEAD | 526 | ST PETER |  | WILK | ML-- METER LEAK METER #A 306010 ACCT# 212002-528168 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A296957 SN: 0029254, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT CHARTRES, *MB: CODE: CEL1 LOC: 2ND METER ** 2) MN: A316961 SN: 0029254, *TAP: SIZE: B LOC: 207 FEET FROM P LINE AT DECATUR, *MB: CODE: CEL1 LOC: ON ST PETER 207' FROM PL OF DECATUR THERE ARE 2 MORE NOT LISTED. ****/ | 2018-02-27 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILL AND CLEAN ED THE AREA LEFT ONE SAFETY CONE ON JOB FOR SAFETY
201800342901 | 2018-02-09 | LEAD/PLASTIC | 1638 | HERO BL | WAGNER | WMTBG | MI- METER BOX ABOVE GRADE METER#C027419 ACCT#238786-406016 METER BOX ABOVE GRADE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-03-28 | EXCAVATED METER BIOX AND FOUND CONCRETE SLAB UNDER METER DUG AROUND SLAB AND BROKE IT WITH SLEDGE HAMMER LOWERED METER BOX TO PROPER GRADE AND BACKFILLED WITH RIVER SAND
201800344701 | 2018-02-10 | LEAD | 1419 | N VILLERE | ESPLANADE AV | WMTLK | ML- METER LEAK METER# A125446 ACCT# 125908-486427 EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: A142437 SN: 0048495, *TAP: SIZE: A LOC: 140 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: ADM6 LOC: 139FT FROM LSPL ESPLANADE ON N VILLERE ****/ | 2018-02-22 | CLEAN OUT DEBRIS INSIDE METER BOX FOUND NO CONSTRANT REGISTRATION NOR INSIDE METER BOX
201800345301 | 2018-02-10 | LEAD | 4318 | N RAMPART | LESSEPS | WOLK | PP-POOR PRESSURE METER # A428073 ACCT # 145651-704988 EXAMINE OUTLET SERVICE UP TO PROPERTY LINE FOR A LEAK (15 PSI ON OUTSIDE FAUCET) 2/19/18 CUSTOMER'S PRESSURE GETTING WORSE. PER S/R #12832633 ************1ST AM TUESDAY*********** /** 1) MN: A345048 SN: 0077369, *TAP: SIZE: A LOC: 163 FEET FROM P LINE AT LESSEPS, *MB: CODE: CEL LOC: ON N RAMPART 148FT FROM PL LESSEPS ****/ | 2018-02-20 | EXCAVATED 2 X 8 CONCRETE SIDEWALK RENEW OUTLET SERVICE FROM METER TO PROPERTY CUSTOMER STILL HAS POOR PRESURE REFER TO ZONE 4 TO RENEW INLET IN STREET BACKFILL JOB WITH RIVERSAND COLDMILL TIE INTO 3/4 INCH PLASTIC LINE
201800345401 | 2018-02-10 | LEAD | 1207 | BARTHOLOMEW | MARAIS | WMTLK | MI- LEAK IN SIDEWALK NEAR VACANT LOT EXAMINE INLET/OUTLET SERVICE FOR A LEAK AREA SATURATED /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-02-20 | EXCVAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON ABANDON 5./8 INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND COLDMILL
201800346001 | 2018-02-10 | LEAD/PLASTIC | 1111 | SHIRLEY DR | GEN MEYER AV | WILK | ML- METER LEAK CAUSING POOR PRESSURE METER#A393520 ACCT#225952-405182 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A124350 SN: 0095132, *TAP: SIZE: C LOC: 193 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: BE35 LOC: ON SHIRLEY DR., 252.5' FROM P.L. GEN. MEYER AVE., ****/ | 2018-03-07 | ARRIVED ON JOBSITE EXAMINED METER FOUND LEAK ON INLET EXCAVATED BY HAND AND REPAIRED LEAK
201800347901 | 2018-02-11 | LEAD | 5101 | METROPOLITAN DR |  | WMTLK | *************PICKUP JOB************** EXAMINE INELT & OUTLET SERVICE FOR A LEAK. "CUSTOMER IS NOTICING AN INFLUCTUATION IN THEIR BILL" /** 1) MN: A336281 SN: 0112300, *TAP: SIZE: A LOC: 697 FEET FROM P LINE AT MIRABEAU AVE, *MB: CODE: BDLM LOC: ON METROPOLITAN DR 697FT FROM PL OF MIRABEAU AVE ****/ | 2018-02-26 | EXAMINE LOCATION FOUND HAND WHEEL LEAKING & METER WAS BELOW GRADE. EXCAVATED DOWN ON INLET & OUTLET SERVICE'S. FOUND LEAD SERVICE'S. MADE REPAIRS BY REPLACING HAND WHEEL WASHER'S UPPER CASING & OUTLET SERVICE FROM METER TO PROPERTY. ALSO RAISED METER TO GRADE. BACKFILLED DRESS UP.
201800354201 | 2018-02-12 | LEAD | 3709 | DUMAINE | WILSON DR | WILK | ML- METER LEAK ACCT# 140074-514868 METER# B032136 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: B032136 SN: 0070953, *TAP: SIZE: B LOC: 45 FEET FROM P LINE AT WILSON DR, *MB: CODE: BD LOC: BY DRIVE - 45' P.L. WILSON DR ****/ | 2018-02-20 | EXCAVATED 2 X 2 DRIVEWAY CUT AND ALSO 3 X 2 MUD PLOT RENEWED OUTLET SERVICE LINE TO PROPERTY BACKFILL AND CLEANED THE AREA **********************OLD METER INFORMATION************* METER:B032136 FAC:59813326 MAKE:SENSUS READ:814
201800354402 | 2018-02-17 | LEAD | 3709 | DUMAINE | WILSON DR | WILK | /** 1) MN: B032136 SN: 0070953, *TAP: SIZE: B LOC: 45 FEET FROM P LINE AT WILSON DR, *MB: CODE: BD LOC: BY DRIVE - 45' P.L. WILSON DR ****/ | 2018-02-22 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK ON 3/4 ICH INLET SERVICE MADE REPAIR ON INLET RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILL JOB WITH RIVERSAND TIE INTO 3/4 PLASTIC LINE
201800361601 | 2018-02-14 | LEAD | 1830 | ALABO | N ROMAN | WMTLK | ML-METER LEAK ACCT#173551-422100 METER#A3894756 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** 1) MN: A119748 SN: 0159590, *TAP: SIZE: A LOC: 224 FEET FROM P LINE AT NO. ROMAN, *MB: CODE: __ LOC: ON ALABO, 224' FROMP.L. NO. ROMAN, 7' OUTSIDE P.L. ****/ | 2018-02-19 | EXCAVATED 3 X 2 MUD PLOT RAISED METER BOX TO GRADE AND REPAIRED LEAK ON OUTLET SERVICE LINE
201800364801 | 2018-02-14 | LEAD | 1475 | N ROBERTSON | COLUMBUS | WILK | ML METER LEAK ACCT# 112184-486269 METER# A386064 INLET SERVICE LEAK NO METER IN BOX /** 1) MN: A306972 SN: 0037814, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT COLUMBUS, *MB: CODE: BFLM LOC: 76FT FROM USPL COLUMBUS ON ROBERTSON ****/ | 2018-03-01 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH METER BOX TO STOP LEAK BACKFILL AND CLEANED THE AREA
201800367201 | 2018-02-14 | LEAD | 1318 | MAZANT | N VILLERE | WILK | ML - METER LEAK METER#A317114 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A317114 SN: 0119159, *TAP: SIZE: B LOC: 161 FEET FROM P LINE AT URQUHART, *MB: CODE: CDL1 LOC: ON MAZANT 162'FROM P L URQUHART 7' OUTSIDE PL 7' O ****/ | 2018-02-27 | EXCAVATED 4 X 4 SIDEWALK CUT ALSO 2 X 2 GUTTER BOTTOM RELOCATED METER B0X TO SIDEWALK AND RENEWED OUTLET SERVICE LINE TO PROPERTY BACKFILOL AND CLEANED THE AREA
201800372801 | 2018-02-15 | LEAD | 2246 | MENDEZ | MARIGNY | WILK | ML-METER LEAK MN:A411680 ACCT#162660-471311 INLET SERVICE LEAK /** 1) MN: A303664 SN: 0102417, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT MARIGNY, *MB: CODE: CDM7 LOC: ON MENDEZ, 81.5' FROM P.L. MARIGNY, 7' OUTSIDE ****/ | 2019-01-23 | EXCV 10 X 6 CUT IN MUDPLOT AND CONCRETE BASE STREET CUT. FOUND LEAK INSIDE METER BOX ON BOX COCK CHANGE BOX COCK LEAK STOP. ALSO FOUND LEAD LINE BUT DUE TO RAIN DID NOT REPLACE. BACKFILLED AND DRESS CUT WITH SAND AND LIMESTONE.
201800375002 | 2018-03-21 | LEAD/PLASTIC | 5850 | RHODES AV | WOODLAND DR | WOLK | CHOPPED THROUGH TRUE ROOTS TRIED TO EXCAVATE OUTLET TURNED METER OFF AND WATER WAS STILL COMING FAST BROKEN WATER MAIN NEED EXCAVATOR BACKHOE MACHINE /** 1) MN: A291271 SN: 0144659, *TAP: SIZE: B LOC: 55 FEET FROM P LINE AT WOODLAND, *MB: CODE: BDL2 LOC: ON RHODES 5.5' FROM DPL WOODLAND 1.5' INSIDE CURB ****/ | 2018-04-03 | BROKE THE SIDEWALK AND EXCAVATED ON THE WATER MAIN AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOBSITE
201800375301 | 2018-02-15 | LEAD | 1735 | N CLAIBORNE AV |  | WMTLK | ML- METER LEAK MN:A410173 ACCT #113513-493668 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER BOX UNDER WATER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-03-02 | EXCAVATED 4 X 2 SIDEWALK CUT MADE ON INLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201800376301 | 2018-02-15 | LEAD | 924 | N RENDON | ST PHILIP | WILK | ML- METER LEAK METER # A319892 ACCT # 124902-521616 ******1ST AM****** INLET SERVICE LEAK IN DRIVEWAY FLOODING DRIVEWAY /** 1) MN: A319892 SN: 0054340, *TAP: SIZE: A LOC: 156 FEET FROM P LINE AT ST PHILIP, *MB: CODE: AF LOC: IN DRWAY INS 159' P.L. ST PHILIP ****/ | 2018-02-16 | EXCAVATED 2 X 6 CONCRETE DRIVEWAY FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET OUTLET SERVICE HAS PLASTIC LINE UP TO PROPERTY BACKFILL JOB WITH RIVERSAND COLDMILL
201800381801 | 2018-02-16 | LEAD/PLASTIC | 505 | PARK BL | NUNEZ | WILK | ML- METER LEAK MTR# A351803 ACCT# 224917-401514 INLET SERVICE LEAK IN THE MUD PLOT NEAR DRIVEWAY /** 1) MN: A113660 SN: 0059808, *TAP: SIZE: A LOC: 60 FEET FROM P LINE AT NUNEZ, *MB: CODE: CD LOC: ON LAWRENCE, 61' FROM P.L. NUNEZ ****/ | 2018-06-20 | BROKE THE DRIVEWAY AND EXCAVATED ON THE INLET AND OUTLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOB SITE
201800381901 | 2018-02-16 | LEAD | 2166 | ESPLANADE AV |  | WMTLK | ML METER LEAK ACCOUNT #129947-524466 METER #A320350 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A212214 SN: 0008627, *TAP: SIZE: C LOC: 71 FEET FROM P LINE AT MIRO N, *MB: CODE: CEL1 LOC: ****/ | 2018-03-07 | ARRIVED AT ABOVE LOCATION EXACAVTED IN SID3WALK AND REPIARED 5/8 CURB COCK BACKFILLED
201800382301 | 2018-02-16 | LEAD/PLASTIC | 435 | NEWTON | NUNEZ | WMTLK | ML- METER LEAK MTR# A 395415 ACCT# 224962-558534 EXAMINE INLET & OUTLET SERVICE FOR ALEAK INSIDE METER BOX IN SIDEWALK /** 1) MN: A154623 SN: 0061533, *TAP: SIZE: A LOC: 62 FEET FROM P LINE AT NUNEZ, *MB: CODE: BEKL LOC: ON NEWTON, 62' FROM P.L. NUNEZ ****/ | 2018-06-06 | EXAMINED AREA BROKE OUT CONCRETE OBSERVED REMOVED ON INLET AND OUTLET SERVICE MADE REAPIRS REMOVED LEAD TO PROPERTY BACKFILLED NEED SAND AND COAL MILL LEFT CONE ON SITE NEED ROCKS PICKED UP CLEANED SITE
201800383201 | 2018-02-16 | LEAD | 3227 | BELFORT AV | CRETE | WILK | MI- LEAK IN THE SIDEWALK NEAR GRASSY AREA INLET SERVICE LEAK /** 1) MN: A122966 SN: 0090675, *TAP: SIZE: A LOC: 393 FEET FROM P LINE AT CRETE, *MB: CODE: ADKN LOC: ON BELFORT 393FT FROM PL CRETE ****/ | 2018-03-06 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK INSIDE OF BOX ON BAD 5/8 INCH HANDWHEEL RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY ALSO RAISED METER BOX UP TO GRADE BACKFILL JOB WITH RIVERSNAD CLEAN UP JOB SITE
201800383301 | 2018-02-16 | LEAD | 846-48 | WILSON DR |  | WILK | MI-METER LEAK MGTR.# A 229515 ACCT.# 142572-514362 EXAMINE INLET SERVICE FOR ALEAK /** AT 846: 1) MN: A229515 SN: 0073767, *TAP: SIZE: A LOC: 136 FEET FROM P LINE AT ELAINE, *MB: CODE: CDL3 LOC: 136FT. FRM PL ELAINE ****/ | 2018-03-06 | EXAMINED JOB AT ABOVE LOCATION FOUND NO LEAK OUTLET SERVICE HAS BEEN RENEW FROM METER BOX TO PROPERTY
201800385201 | 2018-02-16 | LEAD | 2433 | TOURO | N DORGENOIS | WOLK | ACCT# 133592-44537 METER# A367757 CONSTANT REGISTRATION PLEASE REPAIR. /** 1) MN: A345851 SN: 0068034, *TAP: SIZE: A LOC: 241 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: BDL2 LOC: ON TOURO ST 241.4' FROM PL N DORGENOIS ****/ | 2018-03-05 | REPLACED 5/8 INCH WASHERS
201800389201 | 2018-02-16 | LEAD | 3716 | ROBERT |  | WMTLK | ML-- METER LEAK METER # A337898 ACCT# 156345-574366 EXAMINE INLET/OUTLET SERVICE FOR LEAK 03/01/18 LEAK HAS GOTTEN WORSE PER SR#12833926 (AJR) /** 1) MN: A245664 SN: 0093313, *TAP: SIZE: B LOC: 82 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: ADM3 LOC: ON ROBERT 89FT FROM PL ROCHEBLAVE 8FT OUTSIDE PL ****/ | 2018-05-10 | EXCAVATED IN MUDPLOT ON INLET ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND ALSO REFER TO ZONE 3 TO REMOVE LEAD
201800389202 | 2018-05-10 | LEAD | 3716 | ROBERT | S ROCHEBLAVE | WSNR | REFER TO ZONE TO REMOVE LEAD SERVICE ON INLET /** 1) MN: A245664 SN: 0093313, *TAP: SIZE: B LOC: 82 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: ADM3 LOC: ON ROBERT 89FT FROM PL ROCHEBLAVE 8FT OUTSIDE PL ****/ DOTTIE READY 6-4-18 EXP 6-24-18 | 2018-06-17 | REPLACED 3/4 SERVICE FROM 6'' WATER MAIN TO PROPERTY LINE. *************OLD METER INFO**************** METER:A337898 FAC:57289752 MAKE:SENSUS READ:9031
201800393601 | 2018-02-17 | LEAD | 1218 | BARTHOLOMEW | MARAIS | WILK | ML METER LEAK ACCT# 127868-712469 METER# A422194 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A124666 SN: 0054558, *TAP: SIZE: A LOC: 142 FEET FROM P LINE AT MARAIS, *MB: CODE: CDK1 LOC: 143' P.L. MARAIS ****/ | 2018-03-09 | EXCAVATED 2 X 8 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH OUTLET SERVICE INSIDE OF BOX RENEW OUTLET SERVICE FROM METER BOX TO LEAD LINE GOIN UNDER PORCH BACKFILL JOB WITH RIVERSAND COLDMILL LEFT PILE TO BE PICKED UP WITH 1 BARREL
201800393801 | 2018-02-17 | LEAD | 2615 | ROFFIGNAC | FLORIDA AV | WILK | WM LEAK IN THE STREET INLET SERVICE LEAK ON SIDEWALK FLOODING STREET & SIDEWALK /** 1) MN: A321109 SN: 0132312, *TAP: SIZE: B LOC: 112 FEET FROM P LINE AT LAW, *MB: CODE: CDM LOC: RES ON ROFFIGNAC 112' FROM PL LAW 6' OUTSIDE PL ****/ | 2018-03-16 | ARRIVED AT ABOVE LOCATION FOUND WASHERS WAS BAD AND REPLACED THEM
201800395401 | 2018-02-17 | LEAD | 1914 | ONZAGA |  | WILK | /** 1) MN: A304187 SN: 0079163, *TAP: SIZE: A LOC: 119 FEET FROM P LINE AT PRIEUR N, *MB: CODE: BDK LOC: ON ONZAGA, 119' FROM P.L. NO. PRIEUR, 9' OUTSIDE ****/ | 2018-02-16 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET SERVICE RENEW OUTLET SERVICE FROM METER BOX TO PROOERTYBACKFILL JOB WITH RIVERSAND
201800395601 | 2018-02-17 | LEAD/PLASTIC | 1812 | SHIRLEY DR | VESPASIAN BL | WMBK | ***********PICKUP JOB********** **************1ST AM*********** UPPER METER BOX CASING SHIFTED OVER CURB COCK, UNABLE TO CLOSE OFF METER DUE TO BROKEN PIPES INSIDE PROPERTY /** 1) MN: B028069 SN: 0129780, *TAP: SIZE: C LOC: 205 FEET FROM P LINE AT VESPASIAN, *MB: CODE: BE24 LOC: ON SHIRLEY DR., 182' FROM P.L. VESPASIAN, 5' OUT- ****/ | 2018-02-18 | ARRIVED ON JOB SITE AND RAISE METER BOX TO GRDAE AND ADJUST CASING LEFT THE METER OFF UNTIL CUSTOMER MAKE REPAIRS ON STOP AND WASTE VALVE OUTLET
201800408401 | 2018-02-19 | LEAD/PLASTIC | 7810 | BELFAST | BURDETTE | WILK | ML- METER LEAK MTR.# A 230705 ACCT.# 131533-560254 INLET SERVICE LEAK IN THE MUD PLOT IN FRONT METER /** 1) MN: A230705 SN: 0062233, *TAP: SIZE: A LOC: 46 FEET FROM P LINE AT BURDETTE, *MB: CODE: CD LOC: ON BELFAST ST 45.5' FROM URPL BURDETTE ****/ | 2018-07-01 | ARRIVED AT ABOVE LOCATION EXCAVATED IN MUDPLOT FOUND 3/4 LRAD LINE LEAKING.BACKFILLED CLEANED UP AREA.
201800410801 | 2018-02-19 | LEAD | 2730 | ST ANN |  | WMTLK | MI LEAK ON THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER, IN LOWLINE AREA /** 1) MN: A333209 SN: 0038776, *TAP: SIZE: B LOC: 231 FEET FROM P LINE AT BROAD N, *MB: CODE: CDL LOC: ON ST ANN 230FT PL N BROAD 7' OUTSIDE ****/ | 2018-03-23 | EXCAVATED 4 X 4 LIMESTONES GUTTER BOTTOM FOUND LEAK ON 5/8 INCH ADANDON INLET SERVICE MADE REPAIRS ON INELT BACKFILL JOB WITH RIVERSAND AND COLDMILL
201800411001 | 2018-02-19 | LEAD | 2318 | ROYAL | MARIGNY | WILK | ML METER LEAK METER# A255261 ACCT# 129713-480577 INLET SERVICE LEAK INSIDE BOX LOCATED IN DRIVEWAY /** 1) MN: A255261 SN: 0062079, *TAP: SIZE: A LOC: 136 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: ADLK LOC: 137' P.L. MANDEVILLE ****/ | 2018-03-13 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING IN DRIVEWAY + REPAIRED UNDER CURB ON LEAD LINE
201800411401 | 2018-02-19 | LEAD | 1133 | N VILLERE | GOV NICHOLLS | WILK | MI- CLOSE FOR REPAIRS BROKEN OUTSIDE METER# A397247 ACCT# 123230-701800 CURB COCK PASSING IN OFF POSITION,FOUND OFF LEFT OFF /** 1) MN: A334560 SN: 0042780, *TAP: SIZE: A LOC: 129 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: ADEM LOC: 130' P.L. GOV NICHOLLS ****/ | 2018-03-08 | EXCAVATED IN CONCRTE SIDEWALK + REPLACED 5/8 INCH CURB COCK + REPLACED 3/4 INCH LEAD OUTLET SERVICE LINE FROM METER BOX TO PROPERTY INLET SERVICE LINE IS LEAD REFER BACK TO ZONE 4 TO REPLACED 3/4 INCH LEAD INLET
201800411501 | 2018-02-19 | LEAD | 1927 | PIETY |  | WILK | MI- LEAK AT THE SIDEWALK FLOODING AREA EXAMINE INLET SERVICE FOR LEAK 02/28/18 LEAK ON THE SIDEWALK GETTING WORSE (KSW) /** 1) MN: A334377 SN: 0084779, *TAP: SIZE: A LOC: 119 FEET FROM P LINE AT JOHNSON N, *MB: CODE: BE5L LOC: ON PIETY, 119' FROM L.R.P.L. NO. JOHNSON ****/ | 2018-03-13 | EXCAVATED 4 X 4 MUD PLOT FOUND LEK ON 5/8 INCH INLET SERVICE MADE ON INLET RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILL JOB WITH RIVERSAND ALSO RAISE METER BOX UP GRADE
201800415101 | 2018-02-19 | LEAD/PLASTIC | 1014 | JOSEPHINE | CONSTANCE | WILK | MI METER BOX LEAKING INLET SERVICE LEAK IN THE SIDEWALK FLOODING SIDEWALK & GUTTER BOTTOM /** 1) MN: SN: 0050189, *TAP: SIZE: B LOC: 25 FEET FROM P LINE AT CONSTANCE, *MB: CODE: __ LOC: ON JOSEPHINE 24FT FROM PL CONSTANCE ****/ | 2018-04-08 | BROKEN UP CONCRETE STREET EXCAVATED OVER 12" WATER MAIN AN FOUND LEAK ON LEAD LINE AND TAP CREW MADE ALL REPAIR SERVICE AND TAP AND BACKFILL WITH RIVERSAND AND COLDMILL REFERRED TO ZONE 6 TO REMOVE LEAD LINE FORM MAIN TO METER BOX
201800416601 | 2018-02-19 | LEAD | 1413 | MAZANT | ROBERTSON | WILK | WM- LEAK ON THE SIDEWALK INLET LEAK IN THE MUDPLOT /** 1) MN: A303968 SN: 0094866, *TAP: SIZE: B LOC: 64 FEET FROM P LINE AT VILLERE N, *MB: CODE: BDK1 LOC: XXX 64'FROM P L NO VILLERE 9' OUTSIDE P/L ****/ | 2018-03-09 | EXAMINED JOB AT ABOVE LOCATION FOUND 5/8 INCH INLET WASHERS LEAK REPLACEDBOTH INLET AND OUTLET WASHERS OUTLET HAS PLASTIC LINE GOIN UP TO PROPERTY
201800417101 | 2018-02-19 | LEAD | 3227 | GRAND RTE ST JOHN | HAGAN AV | WILK | ML METER LEAK ACCT# 118156-522087 METER# A412456 INLET LEAK IN THE METER BOX (D) /** 1) MN: A342040 SN: 0027394, *TAP: SIZE: A LOC: 122 FEET FROM P LINE AT HAGAN AVE, *MB: CODE: BDK2 LOC: 120' P.L. HAGAN AVE ****/ | 2018-03-19 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH HANDWHEEL + REPAIRED IT IN MUD PLOT BACKFILL
201800418601 | 2018-02-19 | LEAD | 4726 | PERRIER | VALENCE | WMTLK | ML- METER LEAK METER#A320027 ACCT#144368-561290 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A333526 SN: 0057100, *TAP: SIZE: A LOC: 214 FEET FROM P LINE AT VALENCE, *MB: CODE: CDLM LOC: ON PERRIER 212FT FROM VALENCE ****/ | 2018-05-14 | EXCAVATED IN CONCRETE SIDEWALK. REPAIR 5/8 STOP AND WASTE LEAD DRESS UP WITH RIVERSAND AND COLD MILL.
201800419001 | 2018-02-19 | LEAD/PLASTIC | 3711 | RUE NADINE | CARLISLE CT | WOLK | MI - LEAK BETWEEN THE SIDEWALK AND THE CURB OUTLET SERVICE LEAK ON SIDEWALK /** 1) MN: A290962 SN: 0146763, *TAP: SIZE: B LOC: 188 FEET FROM P LINE AT CARLISLE CT, *MB: CODE: ADKL LOC: RES. ON RUE NADINE 189' FORM PL CARLISLE CT 7' OUT ****/ | 2018-03-20 | EXCAVATED OUTLET SERVICE AND INLET SERVICE WHILE CHOPPED TREE ROOTS INLET SERVICE WAS CHOPPED AS WELL MADE REPAIRS ON BOTH LINE REPAIRED LEAK ON OUTLET
201800419101 | 2018-02-19 | LEAD/PLASTIC | 1121 | RICHLAND RD |  | WOLK | MI-- LEAK IN DRIVEWAY NEAR SIDWALK EXAMINE OUTLET SERVICE UP TO PROPERTY LINE FOR A LEAK /** 1) MN: A249032 SN: 0158012, *TAP: SIZE: B LOC: 252 FEET FROM P LINE AT PATTERSON RD, *MB: CODE: ADK LOC: 250'FRM PL PATTERSON 5'FRM THE PATTERSON DIV PL ****/ | 2018-03-02 | ARRIVED ON JOBSITE EXAMINED METER FOUND LEAK ON OUTLET BROKE CONCRETE IN DRIVEWAY EXCAVATED BY HAND REPAIRED
201800423301 | 2018-02-20 | LEAD | 2500 | LOUISIANA AV | FRERET | WILK | MI- CUT SERVICE BY CORLEE ***CALLER IS UNAWARE IF ANYONE IS WITHOUT WATER.*** *******DAMGE CLAIM******** (L.THOMPSON @ 11:44AM) CUT 1" INLET SERVICE UNKNOWN IF ANYONE OUT OF WATER, INTERFERING WITH CONTRACTORS WORK 02/22/18 PER S/R 12833105 BROKEN WATER LINE IN DRIVEWAY NEEDS TO BE REPAIRED - CUT SERVICE (KSW) /** 1) MN: E004930 SN: 0133342, *TAP: SIZE: E LOC: 100 FEET FROM P LINE AT LOUISIANA AVE, *MB: CODE: AEHP LOC: ON FRERET, 99' FROM P.L. LOUISIANA AVE.,5' OUTSIDE ****/ | 2018-02-23 | EXCAVATED IN MUDPLOT. AND PUT A STOCK ON 1". LINE THAT WAS ABANDON.
201800425001 | 2018-02-20 | LEAD/PLASTIC | 4517 | ELBA | S RENDON | WILK | MI- LEAK IN THE SIDEWALK INLET SERVICE LEAK BAD CURB COCK FLOODING MUD PLOT ALSO RENEW OUTLET. ***HOUSE UNDER RENOVATIONS*** 03/01/18 LEAK NOW FLODING AREA ALSO SET 5/8 METER PER SR#12833907 (AJR0 /** 1) MN: A117840 SN: 0076265, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT RENDON S, *MB: CODE: BDL1 LOC: ON ELBA 134FT FROM PL OF S RENDON ****/ | 2018-05-26 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 CURB COCK ALSO UNDER MINED SIDEWALK TO REMOVE LEAD AND REPLACED WITH 3/4 PLASTIC TUBING TO PROPERTY TIED INTO COPPER PIPE BACKFILLED AREA
201800426301 | 2018-02-20 | LEAD | 618 | PIETY | CHARTRES | WILK | ML METER LEAK ACCT# 150039-427516 METER# C022047 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: 000000 SN: 0060788, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT CHARTRES, *MB: CODE: CD LOC: ON PIETY 116FT FROM CHARTRES 6FT OUTSIDE 2FT ** 2) MN: SN: 0060788, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT CHARTRES, *MB: CODE: E24 LOC: ON PIETY 11134FT FROM CHARTRES ****/ | 2018-03-27 | EXCAVATED IN SIDEWALK MADE 3 X 3 CUT FOUND 5/8 INCH CURB COCK LEAKING + REPAIRED IT
201800426401 | 2018-02-20 | LEAD | 2730 | ST BERNARD AV |  | WMBK | ML METER LEAK ACCOUNT #134220-577990 METER #A427014 BROKEN LOWER METER BOX CASING /** 1) MN: A339718 SN: 0064967, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT DUPRE N, *MB: CODE: BD LOC: ON ST BERNARD AVE 43' FROM URPL N DURPE ****/ | 2018-03-09 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING + REPAIRED IT REPLACED BROKEN CASING WITH METER BOX COMPLETE
201800426501 | 2018-02-20 | LEAD | 2623 | ALMONASTER AV | LAW | WILK | ML - METER LEAK ACCOUNT NUMBER - 210151 - 479601 METER NUMBER - A273030 INLET SERVICE LEAK /** 1) MN: A271016 SN: 0170901, *TAP: SIZE: C LOC: 17 FEET FROM P LINE AT LAW, *MB: CODE: AEL2 LOC: ON ALMONSATER 15FT. FROM DIV. PL LAW 10FT OUTSIDE ** 2) MN: A345460 SN: 0170901, *TAP: SIZE: C LOC: 17 FEET FROM P LINE AT LAW, *MB: CODE: BEL2 LOC: ON ALMONASTER 17FT. FROM DIV. PL LAW 10FT OUTSIDE ****/ | 2018-03-13 | REPLACED 5/8 INCH HANDWHEEL + GUT IN METER BOX
201800427201 | 2018-02-20 | LEAD | 2514 | MILAN | FRERET | WMTLK | ML: METER LEAK METER# A220117 ACCT# 131468-553552 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A220117 SN: 0062316, *TAP: SIZE: A LOC: 118 FEET FROM P LINE AT FRERET, *MB: CODE: CDN LOC: ON MILAN,119' FROM U.S.P.L. FRERET ****/ | 2018-05-09 | EXCAVAED IN MUDPLOT ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOPLEAK BACKFILL WITH RIVERSAND REFER TO ZONE 3 TO REMOVE LEAD
201800429401 | 2018-02-20 | LEAD | 4727 | CLEVELAND AV | S ST PATRICK | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK IN MUDPLOT FLOODING CURB/STREET /** 1) MN: A293259 SN: 0062188, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT BERNADOTTE S, *MB: CODE: BDN3 LOC: ON CLEVELAND AVE.,117.5' FROM L.R.P.L. ****/ | 2018-03-22 | EXAMINE INLET, EXCAVATED BY HAND, FOUND LEAK MADE ALL REPAIRS. BACKFILLED WITH RIVERSAND REFER TO ZONE TO REMOVE LEAD ON INLET.
201800429601 | 2018-02-20 | LEAD | 2029 | CONGRESS | N GALVEZ | WILK | ML METER LEAK ACCT# 148549-713125 METER# A389548 INLET SERVICE LEAK INSIDE METER BOX CAUSING OVERFLOW ALSO RAISE METER TO GRADE /** 1) MN: A276752 SN: 0086264, *TAP: SIZE: A LOC: 277 FEET FROM P LINE AT JOHNSON N, *MB: CODE: BD LOC: METER ON CONGRESS 277 FT FROM PL N JOHNSON ****/ | 2018-03-14 | ARRIVED AT ABOVE LOCATION FOUND LEAK ON 5/8 INCH CURB COCK + REPAIRED IT RAN PLASTIC TO PROPERTY WITH METER BOX COMPLETE IN SIDEWALK BACKFILLED CLEANED AREA
201800429901 | 2018-02-20 | LEAD | 108 | ROYAL | CANAL | WILK | ML- METER LEAK ACCT# 201939-527109 METER# C020156 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: C020156 SN: 0006012, *TAP: SIZE: C LOC: 120 FEET FROM P LINE AT CANAL, *MB: CODE: OOO LOC: 1ST METER ON ROYAL 119FT FRM PL CANAL ****/ | 2018-03-22 | EXCAVATED IN BRICK SIDEWALK + REPLACED 1 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201800430001 | 2018-02-20 | LEAD | 3010 | PAUGER | N TONTI | WILK | MI METER BOX LEAKING INLET SERVICE LEAK INSIDE METER BOX FROM BAD BLEEDER VALVE /** 1) MN: A114907 SN: 0060870, *TAP: SIZE: A LOC: 87 FEET FROM P LINE AT TONTI N, *MB: CODE: CDLM LOC: ON PAUGER 86.6' FROM LPL N TONTI ****/ | 2018-03-13 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING + REPAIRED IT
201800434401 | 2018-02-21 | LEAD | 1307 | PENISTON | PERRIER | WILK | ML - METER LEAK ACCOUNT NUMBER - 107494-566658 METER NUMBER - A278446 INLET SERVICE LEAK IN THE GRASS IN FRONT METER FLOODING GRASS & GUTTER BOTTOM /** 1) MN: A278446 SN: 0003371, *TAP: SIZE: A LOC: 56 FEET FROM P LINE AT PERRIER, *MB: CODE: BDL1 LOC: LS WLK ON PENISTON 56 FT FROM PL PERRIER ****/ | 2018-02-22 | EXCAVATED IN MUDPLOT ON INLET AND OUTLET LEAK RENEW METER BOX COMPLETE ALSO RENEW LEAD LINE FROM METER BOX TO PROPERTY BACKFILL WITH RIVERSANDREFERRE TO ZONE 3 TO REMOVE LEAD LINE FROM MAIN TO METER BOX
201800434801 | 2018-02-21 | LEAD | 1229 | LOWERLINE | PLUM | WILK | WM LEAK IN THE STREET INLET SERVICE LEAK IN AN ASPHALT STREET ***LEAKING IN 2 SPOTS*** /** 1) MN: A321509 SN: 0041915, *TAP: SIZE: B LOC: 90 FEET FROM P LINE AT PLUM, *MB: CODE: AFM LOC: LS LOWER INSIDE 90' P.L. PLUM ****/ | 2018-06-03 | EXCAVATED IN STREET ON INLET ON LEAD MADE ALL REPAIR TO STOP LEAK WAS NOT ABLE TO REMOVE ALL LEAD TRUCK ON TOP JOB BACKFILL WITH RIVERSAND AND COLDMILL REFER TO ZONE TO REMOVE LEAD ON INLET
201800434802 | 2018-06-03 | LEAD | 1229 | LOWERLINE | PLUM | WSNR | REFER TO ZONE TO REMOVE LEAD ON INLET /** 1) MN: A321509 SN: 0041915, *TAP: SIZE: B LOC: 90 FEET FROM P LINE AT PLUM, *MB: CODE: AFM LOC: LS LOWER INSIDE 90' P.L. PLUM ****/ | 2019-05-28 | ZONE 1 WILL REVISIT THIS JOB AT A LATER DATE DO TO THE RIVER LEVEL
201800436301 | 2018-02-21 | LEAD | 120 | N MIRO | IBERVILLE | WILK | ML - METER LEAK ACCOUNT NUMBER - 115708-522769 METER NUMBER - A392130 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A312047 SN: 0020012, *TAP: SIZE: B LOC: 133 FEET FROM P LINE AT IBERVILLE, *MB: CODE: CFM1 LOC: 137' P.L. IBERVILLE ****/ | 2018-03-12 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING + REPAIRED *BACKFILLED*
201800436901 | 2018-02-21 | LEAD | 122 | N MIRO | IBERVILLE | WILK | ML - METER LEAK ACCOUNT NUMBER - 115709-475584 METER NUMBER - A401331 BAD BLEEDER VALVE /** 1) MN: A151786 SN: 0020013, *TAP: SIZE: B LOC: 133 FEET FROM P LINE AT IBERVILLE, *MB: CODE: CFM1 LOC: 136' P.L. IBERVILLE ****/ | 2018-03-05 | EXCAVATED IN CONCRTE SIDEWALK + REPLACED 5/8 INCH CURB COCK + 3/4 INCH LEAD OUTLET SERVICE LINE FROM METER BOX TO PROPERTY INLET IS LEAD + NEED TO BE REPLACED FROM MAIN TO METER BOX
201800437201 | 2018-02-21 | LEAD/PLASTIC | 4521 | ST PETER | N MURAT | WILK | LOCATION ID-113552 MTR-A427049 BAD LEAK AROUND MTR/TURN MTR ON CUST NOT GETTING WATER/CUST WAITING ON WATER TURN MTR BACK OFF/AREA FLOODED OUTLET SERVICE LEAK, CUSTOMER OUT OF WATER HOUSE UNDER RENOVATION /** 1) MN: A299803 SN: 0036118, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT MURAT N, *MB: CODE: CDL1 LOC: 130' P.L. N MURAT ****/ | 2018-02-27 | EXCAVATED IN MUDPLOT THROUGH TRASH & DEBRIS OVER MULTIPLE LEAKS ON A 5/8 INLET SERVICE THAT WAS ALSO LEAKING ON ABANDON SERVICE THAT WAS TEED OFF TO AN OLD SERVICE STOP THE LEAKS RAISE METER BOX UP TO GRADE BACKFILLED AND DRESS UP WITH RIVER SAND REPLACED FROM CURB TO PROPERTY. PLASTIC ON OUTLET LEAD ON INLET. JOB COMPLETE JEG
201800437301 | 2018-02-21 | LEAD | 730 | ESPLANADE AV | BOURBON | WMTLK | MI--LEAK ON THE SIDEWALK ***AREA MARKED WITH FLAGS*** EXAMINE INLET/OUTLET SERVICE INSIDE METER BOX /** 1) MN: B026820 SN: 0009863, *TAP: SIZE: B LOC: 106 FEET FROM P LINE AT BOURBON URPL, *MB: CODE: CD5 LOC: 106' FROM URPL BOURBON ****/ | 2018-03-16 | EXACAVATED 4 X 4 MUD PLOT FOUND LEAK ON 3/4 INCH INLET SERVICE MADE REPAIR ON INELT BACKFILL JOB WITH RIVERSAND
201800437701 | 2018-02-21 | LEAD/PLASTIC | 405 | HOMER | TECHE | WILK | ML- METER LEAK ACCT# 236088-401323 MTR# A364719 INLET SERVICE LEAK IN MUDPLOT NEAR SIDEWALK /** 1) MN: SN: 0165162, *TAP: SIZE: A LOC: 14 FEET FROM P LINE AT TECHE, *MB: CODE: OOOO LOC: ON HOMER, 13' FROM D.P.L. TECHE, 8' OUTSIDE, 4' ****/ | 2018-05-21 | EXCAVATED METER BOX AND FOUND BAD HAND WHEEL REPLACED HAND WHEEL TO REPAIR LEAK
201800439101 | 2018-02-21 | LEAD/PLASTIC | 2631 | CHELSEA DR | ABBEY DR | WILK | ML- METER LEAK METER # A386752 ACCT # 231716-418093 INLET SERVICE LEAK /** 1) MN: A122041 SN: 0143347, *TAP: SIZE: B LOC: 122 FEET FROM P LINE AT ABBEY DR, *MB: CODE: BD1M LOC: ON CHELSEA DR 121' FROM PL ABBEY DR 7' OUTSIDE PL ****/ | 2018-03-01 | EXCAVATED ON THE INLET AND OUTLET SERVICE AND REPAIR LEAK AND RAISE METER BOX TO THE GRADE AND WE MARK THE METER BOX AND THEN WE BACKFILL AND CLEAN UP JOB SITE
201800442201 | 2018-02-22 | LEAD/PLASTIC | 3700 | BEHRMAN PL |  | WILK | PER RAY SWALLEY, UNDERGROUND LK ABT 200' AWAY (TOWARD BERHMAN HW) FLOODING AREA. LOC & RAISE TO GD INLET VALVE FOR MTR G-1385 FOR REMOVAL (REQUESTED BY TIMOTHY LAVELLE PARKS & PARKWAYS, DUE TO VANDALISM IN PARK). CONTACT RAY SWALLEY M/SHOP WHEN GOING TO COMPLETE JOB FOR HIM TO REMOVE METER. LOC ID 291603 RENEW INLET SVC & REMOVE METER CONTACT METER SHOP UPON REMOVING METER** 06/11/18 LEAK NOW FLOODING AREA PER SR#12843489 (AJR) /** 1) MN: A295843 SN: 0000000, *TAP: SIZE: B LOC: 747 FEET FROM P LINE AT BEHRMAN PL, *MB: CODE: OOO LOC: ON TULLIS,747' FROM COR.P.L. BEHRMAN PL.,5' OUT- THERE ARE 2 MORE NOT LISTED. ****/ | 2018-06-29 | USED MACHINE TO CHOP THROUGH TREES ROOTS GOT THROUGHT TREE ROOTS AND BEGAN TO EXCAVATE BY HAND FOUND BROKEN 2 SERVICE REPAIRED LINE TO STOP LEAK BACKFILLED WITH RIVER SAND
201800444101 | 2018-02-22 | LEAD | 1804 | ST FERDINAND |  | WILK | LOCATION ID-169311 MTR-B041897 METER LEAK INLET SERVICE LEAK IN BOX /** 1) MN: B020188 SN: 0075466, *TAP: SIZE: B LOC: 43 FEET FROM P LINE AT ROMAN N, *MB: CODE: CD4 LOC: ON ST FERDINAND 43' FROM PL N ROMAN 9' OUTSIDE PL ****/ | 2018-04-03 | EXCAVATED 3 X 2 SIDEWALK CUT ALSO AN ADDITIONAL 3 X 3 GUTTER BOTTOM RENEWED OUTLET TO PROPERTY AND RELOCATED METER BOX TO SIDEWALK BACKFILLED AND CLEANED TEH AREA
201800444601 | 2018-02-22 | LEAD | 200 | WESTCHESTER PL | GEN MEYER AV | WOLK | ML- METER LEAK MTR# C027126 ACCT # 228870-419656 ( LEAD WHIP IS LEAKING ALSO) CHECK OUTLET SERVICE FOR LEAK @ PROPERTY LINE, FLOODING AREA /** 1) MN: C027126 SN: 0124683, *TAP: SIZE: C LOC: 105 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: CF LOC: ON WESTCHESTER PL 105FT FROM P.L. GEN MEYER AVE ****/ | 2018-02-22 | ARRIVE AT ABOVE LOCATION EXAMINE AND FOUND JOB IN TREE NEED TO BE REROUTE REFERRED TO ZONE 6
201800448101 | 2018-02-23 | LEAD | 2319 | N CLAIBORNE AV | SPAIN | WILK | ML-METER LEAK METER#A366762 ACCT#133416-482407 INLET SERVICE LEAK /** 1) MN: A265438 SN: 0064296, *TAP: SIZE: A LOC: 138 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: CFL LOC: ON CLAIBORNE 138FT FROM MANDEVILLE ****/ | 2018-03-13 | ARRIVED AT ABOVE LOCATION FOUND NO LEAK + EXCAVATED IN SIDEWALK ON OUTLET (PLASTIC) MAYBE LEAK ON PROPERTY
201800448201 | 2018-02-23 | LEAD | 7823 | FIG | FERN | WMTLK | ML - METER LEAK MTR# A431146 ACCT# 139148 578324 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER BOX UNDER WATER GRASS & SIDEWALK FLOODED 03/05/18 PER S/R 12834327 POOR PRESSURE (KSW) /** 1) MN: A189936 SN: 0069798, *TAP: SIZE: B LOC: 164 FEET FROM P LINE AT BURDETTE, *MB: CODE: BD LOC: ON FIG 164' FROM PL OF BURDETTE ****/ DOTTIE READY 4-20-18 EXP 5-10-18 | 2018-04-23 | ARRIVED ON JOB EXCAVATED IN MUD PLOT FOUND 5/8 METER BOX COCK LEAKING MADE REPAIRS TIED INTO LEAD AND BACKFILLED. JOB COMPLETE.
201800451701 | 2018-02-23 | LEAD | 7028 | MAGAZINE |  | WOLK | MI- NEED OUTLET TIE IN HOLE IS EXPOSED MTR# A 247561 ACCT# 129117-585477 **********L THOMPSON 12:57*********** OUTLET TIE IN CUSTOMER WAITING ON WATER /** 1) MN: A247561 SN: 0058086, *TAP: SIZE: A LOC: 74 FEET FROM P LINE AT WALNUT, *MB: CODE: BDM3 LOC: ON MAGAZINE 72FT FROM PL OF WALNUT ****/ | 2018-02-23 | ARRIVED ON JOB EXCAVATED SIDEWALK FOUND LEAD SERVICE UNDER CHAIN WALL GAVE TEMPORARY WATER BUT NEED TO COME BACK TO GO UNDER CHAIN WALL LEFT CONES AROUND JOB.
201800452201 | 2018-02-23 | LEAD | 808 | SOLOMON PL |  | WILK | ML- METER LEAK ACCT# 138131-701397 MTR# A288392 INLET SERVICE LEAK /** 1) MN: A288392 SN: 0068781, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT MAQUEDA, *MB: CODE: CDLM LOC: ON SOLOMON 12FT FROM DIV P/L ORLEANS 4FT INSIDE ****/ | 2018-02-23 | EXCAVATED IN MUDPLOT ON INLET LEAK MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND REFER TO ZONE 1 TO REMOVE LEAD FROM MAIN TO METER BOX.
201800452301 | 2018-02-23 | LEAD | 2421 | EADS |  | WILK | METER LEAK INLET SERVICE LEAK /** 1) MN: A220051 SN: 0117403, *TAP: SIZE: B LOC: 171 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: OOO LOC: 168' P/L N ROCHEBLAVE 8' OUTSIDE ****/ | 2018-03-20 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH HANDWHEEL LEAKING MUD PLOT + REPAIRED IT (PLASTIC)
201800452701 | 2018-02-23 | LEAD | 3306 | N GALVEZ | PIETY | WMTLK | MI--LEAK ON THE SIDEWALK RUNNING INTO THE STREET EXAMINE INLET AND OUTLET SERVICE FOR LEDAK @ CURB, CUB FLOODED LEFT 1 CONE FOR SAFTY /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-03-20 | EXCAVTED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET ABANDON MADE REPAIR ON NLET BACKFILL JOB WITH RIVERSAND
201800453701 | 2018-02-23 | LEAD | 713 | GEN PERSHING | LAUREL | WILK | ML METER LEAK ACCT# 126814-556384 METER# A363596 INLET SERVICE LEAK /** 1) MN: A152420 SN: 0051348, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT LAUREL, *MB: CODE: CDN3 LOC: 110FT FROM PL LAUREL ****/ DOTTIE READY 5-7-18 EXP 5-27-18 | 2018-05-08 | EXCVATED IN BRICK SIDEWALK REPAIR 5/8 STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND JOB REFER TO ZONE 3 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201800453702 | 2018-05-08 | LEAD | 713 | GEN PERSHING | LAUREL | WSNR | JOB REFER TO ZONE 3 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX /** 1) MN: A152420 SN: 0051348, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT LAUREL, *MB: CODE: CDN3 LOC: 110FT FROM PL LAUREL ****/ | 2018-08-17 | REFERRED TO CONTRACTOR
201800454201 | 2018-02-23 | LEAD | 1029 | ORLEANS AV | N RAMPART | WILK | ML- METER LEAK ACCT# 101159-528431 MTR# A442459 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A276175 SN: 0020016, *TAP: SIZE: B LOC: 119 FEET FROM P LINE AT RAMPART N, *MB: CODE: BE21 LOC: ON ORLEANS AVE.,119' FROM L.R.P.L. NO. RAMPART ****/ | 2018-03-20 | ARRIVED AT ABOVE LOCATION EXCAVATED IN SIDEWALK REPAIRED 5/9 INCHCURB COCKBACKFILL CLEAR AREA
201800454501 | 2018-02-23 | LEAD | 3045 | ST PHILIP | S SALCEDO | WILK | ML- METER LEAK MTR# A 407131 ACCT# 109053-712235 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A340917 SN: 0049269, *TAP: SIZE: A LOC: 70 FEET FROM P LINE AT SALCEDO N, *MB: CODE: CD LOC: ON ST PHILIP 70FT FROM N SALCEDO ****/ | 2018-03-14 | EXCAVATED 4 X 6 MUD PLOT LEAK ON 3/4 INCH INLET SERVICE MADE REPAIR ON INLET UNABLE TO RENEW OUTLET CAUSE OF MATERIAL ON SIDEWALK BACKFILL JOB 5/8 INCH METER WITH NEW METER OLD METER INFO: METER:A368555 FACT:70697770 MAKE: SENSUS READ:383798
201800455101 | 2018-02-23 | LEAD/PLASTIC | 30 | TENNYSON PL | WOODLAND DR | WMTLK | ML- METER LEAK ACCT# 232831-706150 MTR# A292044 EXAMINE INLET AND OUTLET SERVICE AT SIDEWALK FOR A LEAK /** 1) MN: A292044 SN: 0147795, *TAP: SIZE: B LOC: 378 FEET FROM P LINE AT WOODLAND DR, *MB: CODE: ADKM LOC: ON TENNYSON PL., 28.10' FROM D.P.L. WOODLAND DR., ****/ | 2018-05-30 | EXCAVATED METER BOX ON INLET AND OUTLET SIDE METER SAT DEEP SO WE RAISED TO GRADE ALSO WE REPLACED BUD CURB COCK AND RAN PLASTIC TO PROPERTY
201800456101 | 2018-02-24 | LEAD/PLASTIC | 2423 | HYMAN PL | GALLATIN | WMTLK | MI - LEAK ON SIDEWALK EXAMINE INLET & OUTLET SERVICE @ SIDEWALK FOR A LEAK SIDEWALK FLOODED /** 1) MN: A307407 SN: 0134108, *TAP: SIZE: B LOC: 186 FEET FROM P LINE AT GALLATIN, *MB: CODE: BD LOC: ON HYMAN PL., 188' FROM P.L. GALLATIN, 7' OUTSIDE, ****/ | 2018-03-14 | EXCAVATED METER BOX AND FOUND LEAK ON HANDWHEEL REPLACED HAND WHEEL TO STOP LEAK LEAD ON INLET NEEDS TO BE REMOVED BACKFILLED WITH RIVER SAND
201800456701 | 2018-02-24 | LEAD | 6005 | WILTON DR | BURBANK DR | WILK | REPAIR INLET SERVICE 2333-B INGA EMERGENCY DRENNAN /** 1) MN: A323968 SN: 0107551, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT BURBANK DR, *MB: CODE: BDK5 LOC: ON WILTON DR., 54' FROM P.L. BURBANK DR., 9' OUT- ****/ | 2018-01-19 | EXCAVATED AND FOUND LEAK ON INLET SERVINE LINE REMOVED AND REPLACED 40FT OF LEAD WITH 40" OF 1" TUBINGALSO CHANGED OUT (1) 5/8 METER BOX WITH COMPLETE NEW SET. BACKFILLED WITH RIVERSAND AND 610 ROCK CUT IS WITHIN 65FT FROM P/L OF BURBANK INSPECTOR TERRY FLOWERS
201800457401 | 2018-02-24 | LEAD/PLASTIC | 4316 | N RAMPART | LESSEPS | WILK | MI SEE WHY NO WATER MTR# A368606 ACCT# 145650-428942 ***************1ST AM************ INLET SERVICE LEAK FOUND 10PSI @ FAUCET /** 1) MN: A337035 SN: 0077369, *TAP: SIZE: A LOC: 163 FEET FROM P LINE AT LESSEPS, *MB: CODE: CFL LOC: ON N RAMPART 146.5FT FROM PL OF LESSEPS ****/ | 2018-02-25 | EXCAVATED AND MADE REPAIR ON 1" INLET AT 6" WATER MAIN MADE 5X5 MUDPLOT BACKFILL HOLE
201800465401 | 2018-02-26 | LEAD/PLASTIC | 8223 | COHN |  | WILK | INLET SERVICE LEAK IN MUDPLOT. /** 1) MN: A279282 SN: 0014656, *TAP: SIZE: A LOC: 193 FEET FROM P LINE AT DUBLIN, *MB: CODE: CDLM LOC: ON COHN 191.7FT FROM DUBLIN ****/ | 2018-02-20 | EXCAVATED AND MADE REPAIRS ON A 5/8 INLET SERVICE LEAK LEAD ON THE INLET PLASTIC ON THE OUTLET. JOB COMPLETE JEG
201800468001 | 2018-02-26 | LEAD | 4520 | DOWNMAN RD |  | WILK | BLEEDER VALVE NEED TO BE REPLACED AND PLEASE CH./ A363087 LOCATION #153779 INLET SERVICE LEAKING FROM BLEEDDER VALVE IN SIDEWALK /** 1) MN: A340685 SN: 0133195, *TAP: SIZE: A LOC: 175 FEET FROM P LINE AT HYDT, *MB: CODE: BF LOC: 22-C DHEF 176'R/S HYDT 6 DRUG STORE ****/ | 2018-03-16 | MADE A 3X3 CUT IN SIDEWALK. EXCAVATED DOWN ON INLET SERVICE. FOUND LEAD. MADE REPAIR'S BY REPLACING WASHER'S, COCK. BACKFILLED DRESS UP.
201800468401 | 2018-02-26 | LEAD | 3147 | N TONTI | LOUISA | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK ON ABANDON SERVICE IN FORNT VACANT LOT /** 1) MN: A224817 SN: 0102820, *TAP: SIZE: B LOC: 384 FEET FROM P LINE AT CLOUET, *MB: CODE: ADK1 LOC: 384' P.L. CLOUET ****/ | 2018-03-15 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING ON ABANDON SERVICEIN MUD PLOT + REPAIRED IT (NO METER ) BACKFILLED
201800469002 | 2018-02-27 | LEAD | 428 | CALHOUN | LAUREL | WSNR | REFER TO ZONE 3 TO REMOVE LEAD LINE FROM INLET SIDE WATER MAIN TO METER BOX /** 1) MN: A331012 SN: 0012663, *TAP: SIZE: A LOC: 111 FEET FROM P LINE AT LAUREL, *MB: CODE: BDL3 LOC: 111' P.L. LAUREL ****/ | 2018-08-30 | EXCAVATED OVER WATER MAIN .REMOVED LEAD FROM WATER MAIN TO THE METER BOX. REPPLACED WITH 3/4 PLASTIC FROM WATER MAIN TO THE METER BOX.RAISED METER TO GRADE. LEFT CONES ON WET COLDMILL.
201800470501 | 2018-02-26 | LEAD | 3939 | ELYSIAN FIELDS AV | MONTEREY | WILK | ML-METER LEAK ACCOUNT #153664-494950 METER #A156864 INLET SERVICE LEAKING FROM BLEEDER VALVE IN MUDPLOT, FLOODING DRIVEWAY AND GRASS /** 1) MN: A156864 SN: 0089532, *TAP: SIZE: A LOC: 215 FEET FROM P LINE AT MONTEREY, *MB: CODE: BDKL LOC: 215FT FROM PL MONTEREY 10' OUTSIDE P/L 3' INSIDE ****/ | 2018-02-26 | EXACAVATED IN MUDPLOT. REPAIR 5/8 STOP & WASTE LEAD LINE. DRESS UP WITH RIVERSAND. ALSO REF TO ZONE5 TO TAKE LEAD LINE OUT ON INLET SIDE JOB COMPLETE
201800471701 | 2018-02-26 | LEAD | 729 | N RENDON | ORLEANS AV | WILK | ML-METER LEAK ACCT#132802-520289 METER#A401099 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A269011 SN: 0053200, *TAP: SIZE: A LOC: 80 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: CENM LOC: ON N RENDON ST 80' FORM PL ORLEANS AVE ****/ | 2018-03-23 | EXCAVATED 2 X 6 CONCRETE SIDEWALK RENEW 5/8 INCH OUTLET SERVICE FROM METER BOX TO LEAD LINE GOING UNDER STEPS BACKFILL JOB WITH RIVERSAND AND CILDMILL ALSO NEED CONCRETE PILE TO BE PICK UP ANS REPLACE BAD REPLACE BAD 5/8 INCH METER WITH NEW ONE *********OLD METER INFO******* METER:A401099 FAC:14106860 MAKE:HERSEY READ:183
201800472001 | 2018-02-26 | LEAD | 3427 | ROYAL | GALLIER | WILK | MI- CUT SERVICE INSIDE WALK UNSURE IF ANYONE IS WITHOUT WATER. SIMARRON UNDER GROUND 7822 CHEF MENTUER HWY 504-1241-6831 *******CUSTOMER OUT OF WATER******** **********DAMAGE CLAIM*********** C MALLET @ 16:02PM CUT INLET SERVICE BY CIMARRON UNDER GROUND /** 1) MN: A278440 SN: 0062150, *TAP: SIZE: B LOC: 37 FEET FROM P LINE AT GALLIER, *MB: CODE: BFKO LOC: INSIDE BY STEPS METER ON ROYAL 37 FT FROM PL ****/ | 2018-02-26 | EXCAVATED IN SIDEWALK ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK.REFERRED ZONE 4 REMOVE LEAD LINE
201800472401 | 2018-02-26 | LEAD | 2522-24 | URSULINES AV | N ROCHEBLAVE | WILK | MI--LEAK BET THE SIDEWALK AND THE CURB /** AT 2522: 1) MN: 000000 SN: 0056487, *TAP: SIZE: A LOC: 183 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: AFM LOC: 1FT LS STEPS INSIDE ** AT 2524: 2) MN: A321842 SN: 0056487, *TAP: SIZE: A LOC: 186 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: AFM LOC: 1FT LS STEPS ****/ | 2018-03-23 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND
201800473201 | 2018-02-26 | LEAD | 2321 | A P TUREAUD AV | N TONTI | WILK | ***********PICKUP JOB********** INLET SERVICE LEAK BETWEEN CURB & STREET FLOODING STREET /** 1) MN: A339235 SN: 0999999, *TAP: SIZE: A LOC: 168 FEET FROM P LINE AT N TONTI, *MB: CODE: __ LOC: ON A. P. TUREAUD AVE 168FT FROM P.L. N TONTI 12FT ****/ | 2018-03-14 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201800473901 | 2018-02-27 | LEAD | 1800 | DUELS | LONDON AV | WOLK | ACCT# 166773-495630 METER# A403787 CONSTANT REGISTRATION PLEASE REPAIR. /** 1) MN: A313843 SN: 0107577, *TAP: SIZE: B LOC: 39 FEET FROM P LINE AT DUELS, *MB: CODE: CDHM LOC: ON LONDON AVE., 39' FROM P.L. DUELS, 8.5' OUTSIDE ****/ | 2018-03-16 | EXAMINED JOB AT ABOVE LOCATION FOUND CONSTANT REGISTRATION ON METER EXCAVATED 4 X6 MUD PLOT AND RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY NO REGISTRATION ON METER BACKFILL JOB WITH RIVERSAND ALSO 5/8 INCH METER WAS DAMAGE REPLACE WITH NEW METER *********OLD METER INFO************* METER:A403787 FAC:14109549 MAKE:HERSEY READ:1146
201800474801 | 2018-02-27 | LEAD | 417 | ALABO |  | WILK | ML- METER LEAK ACCT# 163267-425999 MTR# A386197 INLET SERVICE LEAKING INTO METER BOX /** 1) MN: 000000 SN: 0048144, *TAP: SIZE: B LOC: 107 FEET FROM P LINE AT BIENVENUE, *MB: CODE: CDL7 LOC: 107FT FROM PL BIENVENUE 8' OUTSIDE PL ****/ | 2018-03-20 | REPLACE BOTH INLET AND OUTLET WASHER AT ABOVE LOCATION LSO HAD TO REPLACE BAD METER WITH NEW ONE OLD METER INFO: METER: A386197 FACT:74971815 MAKE: SENSUS READ: 1308
201800476201 | 2018-02-27 | LEAD/PLASTIC | 2017 | DE ARMAS | BEHRMAN AV | WMTLK | ML- METER LEAK METER# A337097 ACCT # 225033-404542 EXAMINE INLET & OUTLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A249695 SN: 0090096, *TAP: SIZE: A LOC: 136 FEET FROM P LINE AT BEHRMAN AVE, *MB: CODE: CFT1 LOC: ON DE ARMAS, 135.5' FROM P.L. BEHRMAN AVE., 1' ****/ | 2018-03-09 | EXAMINED JOB DUG UP BY HAND DETERMINED THAT LEAK WAS CONING FROM COCK REPLAC BOX COCK AND NCHANGED WASHERS STOP LEAK
201800479301 | 2018-02-27 | LEAD/PLASTIC | 42 | ALLARD BL | DUMAINE | WILK | MI CHECK FOR LEAK @ P/L INLET SERVICE LEAK IN MUDPLOT FLOODING GRASSY AREA 06/25/18 CUSTOMER STATES LEAK FLOODING YARD PER SR#12844752 (AJR) /** 1) MN: B025479 SN: 0012692, *TAP: SIZE: B LOC: 80 FEET FROM P LINE AT DUMAINE, *MB: CODE: CFL1 LOC: BY STEPS 80' P.L. DUMAINE ****/ | 2018-08-25 | EXCAVATED A 3 X 4 MUD CUT AND MADE REPAIRS ON THE INLET SERVIC AND STOP THE LEAK RAISE TO GRADE AND BACKFILL N CLEAN UP. LEAD ON INLET SERVICE AND PLASTIC ON OUTLET SERVICE. JOB COMPLETE
201800480201 | 2018-02-27 | LEAD/PLASTIC | 1900 | MAGAZINE | ST MARY | WOLK | ML- LEAK AT WHEEL ON METER/LOW PRESSURE METER# A 378062 ACCT# 154740 - 543484 OUTLET SERVICE LEAK AT HANDWHEEL /** 1) MN: SN: 0012920, *TAP: SIZE: C LOC: 83 FEET FROM P LINE AT MAGAZINE, *MB: CODE: BJ7 LOC: 83FT PL MAGAZINE 1' OUTSIDE 10' INSIDE CURB ** 2) MN: E004860 SN: 0091248, *TAP: SIZE: E LOC: 42 FEET FROM P LINE AT MAGAZINE, *MB: CODE: CEH5 LOC: ON ST MARY 42FT FROM P.L. MAGAZINE 4FT OUTSIDE P.L ****/ | 2018-04-08 | EXCAVATED ON INLET AND OUTLET SERVICE AND FOUND LEAK ON OUTLET SERVICE CREW MADE ALL REPAIR OUTLET SERVICE WITH METER BOX COMPLETE AND DRESSED JOB WITH RIVER SAND AND COLDMILL
201800482101 | 2018-02-28 | LEAD | 3309 | MARAIS |  | WILK | LOCATION: 125886 HOUSE UNDER RENOVATIONS AREA FLOODED, PLEASE REPAIR AND SET 5/8 METER EXAMINE INLET SERVICE FOR A LEAK CONTRACTORS ROLLING OVER SERVICE /** 1) MN: A244046 SN: 0054734, *TAP: SIZE: A LOC: 72 FEET FROM P LINE AT PIETY, *MB: CODE: CD LOC: 74' P.L. PIETY ****/ | 2018-04-24 | EXCAVATED 2 X 8 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET RENEW OUTLET OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILLED JOB WITH RIVERSAND
201800483401 | 2018-02-28 | LEAD/PLASTIC | 606 | OLIVIER | EVELINA | WILK | WM-LEAK IN STREET CHANGED FROM 608 OLIVIER INLET SERVICE LEAK IN AN ASPHALT STREET FLOODING AREA GETTING OFF IN THE DCB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-04-05 | BROKE THE STREET EXCAVATED ON THE WATER MAIN AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOBSITE ALSO WE BROKE THE CUSTOMER FAUCET OUTLET BECAUSE WE WAS TRYING TO BLOW OUT THE LINE SO I TRY TO LET THE CUSTOMER KNOW BUT NOBODY WAS NOT HOME SO I LEFT A NOTE WITH CLAIMS NUMBER ON IT
201800483501 | 2018-02-28 | LEAD/PLASTIC | 6039 | WARWICK CT | WESTCHESTER PL | WOLK | LOCATION# 229077 CUSTOMER# 418456 METER# A209286 INSPECTOR DID AN INSIDE/OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION ON METER, CAN'T DETERMINE WHERE LEAK IS COMING FROM......PLEASE REPAIR /** 1) MN: A209286 SN: 0126221, *TAP: SIZE: B LOC: 309 FEET FROM P LINE AT WESTCHESTER, *MB: CODE: ADLM LOC: ON WARWICK CT 309' FROM PL WESTCHESTER 9' OUTSIDE ****/ | 2018-03-08 | CHANGED WASHER AND ADJUSTED METER BOX CASING
201800483901 | 2018-02-28 | LEAD | 1632 | LOUISIANA AV | ST CHARLES AV | WOLK | MI- LEAK ON THE SIDEWALK ************L.THOMPSON @ 10:28AM************* OUTLET SERVICE LEAK IN SIDEWALK FLOODIG SIDEWALK AND STREET INTERFERING WITH CONTRACTORS WORK /** 1) MN: SN: 0002585, *TAP: SIZE: D LOC: 62 FEET FROM P LINE AT CARONDELET, *MB: CODE: __ LOC: IN M/H ON LOUISIANA 62' FROM PL CARONDELET 11' OUT ****/ | 2018-02-28 | ARRIVED ON JOB EXCAVATED IN MUD PLOT FOUND LEAK AT PROPERTY ON 1 1/2 LEAD SERVICE MADE REPAIRS AND HAVE TO COME BACK TO REMOVE LEAD SERVICE
201800484601 | 2018-02-28 | LEAD/PLASTIC | 1230 | CONSTANCE | THALIA | WILK | MI- METER BOX LEAK CURB COCK PASSING IIOFF POSITION, NO METER IN BOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-03-21 | BROKE COCNCRETE WITH SLEDGE HAMMER EXCAVATED INLET SERVICE TO CHANGE BOX COCK NEEDS BACKFILL AND DRESS UP ROCKS NEED TO BE PICKED UP ALSO LEAD NEEDS TO BE REMOVED FROM INLET
201800484701 | 2018-02-28 | LEAD | 909-07 | CLOUET | BURGUNDY | WILK | WM SIDEWALK LEAK INLET SERVICE LEAK INSIDE METER BOX /** AT 907: 1) MN: A278365 SN: 0046103, *TAP: SIZE: A LOC: 61 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CDM7 LOC: 60FT FROM LSPL BURGUNDY ON LCOUET ****/ | 2018-03-14 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING IN BRICK SIDEWALK + REPAIRED BACKFILLED
201800484801 | 2018-02-28 | LEAD/PLASTIC | 1225 | BELLEVILLE | BELLEVILLE CT | WILK | WM- LEAK IN ALLEY ON BELLEVILLE CT **********1ST AM********** INLET SERVICE LEAK IN THE COURTYARD FLOODING AREA & WALKWAY ON BELLEVILLE CT /** 1) MN: A278941 SN: 0109989, *TAP: SIZE: A LOC: 216 FEET FROM P LINE AT DE ARMAS, *MB: CODE: CD LOC: ON BELLEVILLE 216FT FROM P.L. 7FT OUTSIDE P.L. ****/ | 2018-03-01 | TRIED TO LOCATE CONTROLLING LINE BY HAND FOR HOURS LOCATED LINE WITH MACHINE REDUCER WAS BAD REPLACED REDUCER AND RAN LINE NEED BACKFILL
201800484901 | 2018-02-28 | LEAD | 4439-41 | GEN PERSHING | S RENDON | WMTLK | ML - METER LEAK ACCT#153372-576998 METER#A388727 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER BOX UNDER WATER, GRASSY AREA FLOODD /** AT 4439: 1) MN: A247458 SN: 0066141, *TAP: SIZE: B LOC: 17 FEET FROM P LINE AT RENDON S, *MB: CODE: CDN LOC: CURB 18FT FROM PL S RENDON 7' OUTSIDE PL 3' INSDDE ** AT 4441: 2) MN: A228833 SN: 0066141, *TAP: SIZE: A LOC: 17 FEET FROM P LINE AT RENDON S, *MB: CODE: CDN LOC: ON GENL PERSHING 17' FROM PL S RENDON ****/ | 2018-03-05 | EXCAVATED IN MUDPLOT . REPAIR 5/8 STOP & WASTE LEAD LINE ALSO REPLACE 5/8 BOTTOM DRESS UP WITH RIVERSAND REFER TO ZONE 3 TO TAKE LEAD LINE OUT ON INLET SIDE
201800484902 | 2018-03-05 | LEAD | 4439-41 | GEN PERSHING | S RENDON | WSNR | REMOVE LEAD LINE FROM WATER MAIN TO METER /** AT 4439: 1) MN: A247458 SN: 0066141, *TAP: SIZE: B LOC: 17 FEET FROM P LINE AT RENDON S, *MB: CODE: CDN LOC: CURB 18FT FROM PL S RENDON 7' OUTSIDE PL 3' INSDDE ** AT 4441: 2) MN: A228833 SN: 0066141, *TAP: SIZE: A LOC: 17 FEET FROM P LINE AT RENDON S, *MB: CODE: CDN LOC: ON GENL PERSHING 17' FROM PL S RENDON ****/ DOTTIE READY 4-20-18 EXP 5-10-18 | 2018-05-14 | GIVE TO CONTRACTOR
201800489901 | 2018-02-28 | LEAD | 2741 | IBERVILLE | N WHITE | WILK | MI-METER BOX LEAKING METER#A277831 INLET SERVICE LEAK IN MUDPLOT COMING FROM BAD BLEEDER VALVE /** 1) MN: A277831 SN: 0090808, *TAP: SIZE: A LOC: 168 FEET FROM P LINE AT WHITE N, *MB: CODE: BDM1 LOC: 169' P.L. N WHITE ****/ | 2018-03-14 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET RENEW OUTLET SERVICE FROM METER BOX TO LEAD GOING UNDER GARDEN BACKFILL JOB WITH RIVERSAND
201800490901 | 2018-02-28 | LEAD | 330 | EXCHANGE PL | BIENVILLE | WILK | WM LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET /** 1) MN: A252444 SN: 0024126, *TAP: SIZE: A LOC: 102 FEET FROM P LINE AT CONTI, *MB: CODE: AEWN LOC: SERVES 1ST FL ANNEX MAIN GALLERY SERVED BY HC# ** 2) MN: A291831 SN: 0027172, *TAP: SIZE: A LOC: 904 FEET FROM P LINE AT CONTI, *MB: CODE: BEN LOC: ON EXCHANGE ALLEY 192.5' FROM PL OF BIENVILLE 7' THERE IS 1 MORE NOT LISTED. ****/ | 2018-06-13 | REPLACED 5/8 INCH HANDWHEEL + GUTS THAT WAS FLODDING ALLEY
201800493801 | 2018-03-01 | LEAD | 2839 | MAUREPAS | CRETE | WILK | ML- METER LEAK MTR# A 272819 ACCT# 128257-514747 EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A272819 SN: 0055224, *TAP: SIZE: A LOC: 119 FEET FROM P LINE AT CRETE, *MB: CODE: BDLM LOC: 120FT FROM LSPL CRETE ****/ | 2018-03-22 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INELT SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND OUTLET HAS PLASTIC LINE GOIN UP TO PROPERTY
201800494401 | 2018-03-01 | LEAD | 2116 | MAGNOLIA | JOSEPHINE | WMTLK | ML- METER LEAK MTR.# A-359575 ACCT # 119353-545033 METER LEAKING INSIDE BOX PER INSPECTOR /** 1) MN: A275537 SN: 0031518, *TAP: SIZE: A LOC: 136 FEET FROM P LINE AT JOSEPHINE, *MB: CODE: BDM3 LOC: ON MAGNOLIA 134.4FT FROM PL OF JOSEPHINE ****/ | 2018-03-07 | EXCAVATED IN SIDEWALK ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND AND COLD MILL REFER TO ZONE 3 TO REMOVE LEAD
201800494402 | 2018-03-06 | LEAD | 2116 | MAGNOLIA | JOSEPHINE | WSNR | REFER TO ZONE TO REMOVE LEAD LINE FROM WATER MAIN TO METER /** 1) MN: A275537 SN: 0031518, *TAP: SIZE: A LOC: 136 FEET FROM P LINE AT JOSEPHINE, *MB: CODE: BDM3 LOC: ON MAGNOLIA 134.4FT FROM PL OF JOSEPHINE ****/ | 2018-03-24 | REPLACED 3/4 SERVICE FROM 6"WATER MAIN TO PROPERTY LINE TIED INTO COPPER.(SOC3FT. 5FT. S/W ; 8FT. X 30 FT.CONCRETE.)
201800497101 | 2018-03-01 | LEAD/PLASTIC | 4311 | FIELDS | JOYCELYN DR | WILK | WM-LEAK IN SIDEWALK EXAMINE INLET SERVICE BETWEEN STREET & CURB /** 1) MN: C017022 SN: 0149242, *TAP: SIZE: C LOC: 26 FEET FROM P LINE AT JOYCELYN DR, *MB: CODE: BDM LOC: ON FIELDS 26' FROM DPL KATHY CT 2.5' INSIDE CURB ****/ | 2018-03-21 | ARRIVED ON JOBSITE EXAMINED METER FOUND LEAK ON OUTLET EXCAVATED BY HAND REPAIRED AND BACKFILLED *****************OLD METER INFO************* METER:C017022 FAC:31654247 MAKE:ROCKWELL READ:52145
201800504701 | 2018-03-02 | LEAD | 2934 | GRAND RTE ST JOHN | N DUPRE | WILK | WM- LEAK IN THE SIDEWALK EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A301404 SN: 0024793, *TAP: SIZE: B LOC: 50 FEET FROM P LINE AT DUPRE N, *MB: CODE: CDM LOC: 50FT FROM URPL DUPRE N ****/ | 2018-03-22 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH ABANDON INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201800504801 | 2018-03-02 | LEAD | 2824 | ST LOUIS | N DUPRE | WMTLK | ML- METER LEAK ACCT# 126553-519741 MTR# A426577 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A260150 SN: 0068285, *TAP: SIZE: A LOC: 121 FEET FROM P LINE AT DUPRE N, *MB: CODE: AEO2 LOC: ON ST LOUIS 123.5' FROM URPL N DUPRE ****/ | 2018-03-28 | ARRIVED AT ABOVE LOCATION EXCAVATED IN 3 X 3 CUT IN SIDEWALK + REPAIRED 5/8 CURB COCK BACKFILLED
201800507601 | 2018-03-02 | LEAD/PLASTIC | 502 | RIVER OAKS DR | ANSON | WOLK | ML- METER LEAK METER# A149754 ACCT # 227879-416133 CHECK OUTLET SERVICE FOR A LEAK @ PROPERY LINE /** 1) MN: A149754 SN: 0118120, *TAP: SIZE: B LOC: 84 FEET FROM P LINE AT ANSON, *MB: CODE: CDL LOC: ON RIVER OAKS DR., 84' FROM P.L. ANSON, 7' OUTSIDE ****/ | 2018-03-13 | ARRIVED ON JOBSITE EXAMINED METER FOUND LEAK ON OUTLET EXCAVATED HAND REPAIRED OUTLET LEAK AND THERE IS A LEAK ON PROPERTY
201800508001 | 2018-03-02 | LEAD | 609-11 | FRENCHMEN |  | WILK | ML-- METER LEAK METER # A427253 ACCT# 127013-717104 EXAMINE INLET SERVICE FOR A LEAK /** AT 611: 1) MN: A134598 SN: 0030189, *TAP: SIZE: A LOC: 69 FEET FROM P LINE AT CHARTRES, *MB: CODE: BENF LOC: ON FRENCHMEN,68' FROM L.S.P.L. CHARTRES ****/ | 2018-04-04 | EXCAVATED 3 X 2 SIDEWALK CUT RENEWED OUTLET TO PROPERTY AND REPLACED 5/8 INCH METER BOX BACKFILLED AND CLEANED THE AREA
201800510201 | 2018-03-02 | LEAD | 1718 | COLUMBUS |  | WMRE | LOCATION ID-208123 MTR-A425876 MTR BURIED/PLEASE LOCATE CUST WAITING ON WATER LOCATE WATER MEATER AND RAISE TO GRADE CUSTOMER WAITING ON WATER /** 1) MN: A297276 SN: 0057671, *TAP: SIZE: A LOC: 137 FEET FROM P LINE AT ROMAN, *MB: CODE: OOO LOC: ON COLUMBUS 137FT FROM PL N ROMAN 9FT OUTSD PL ****/ | 2018-03-07 | ARRIVED AT ABOVE LOCATION LOCATED METER RAISED TO GRADE
201800511301 | 2018-03-02 | LEAD/PLASTIC | 174 | PINEWOOD CT | CYPRESS ACRES DR | WILK | ML- METER LEAK MTR# A 426466 ACCT# 236011-407309 INLET SERVICE LEAK AT CURB LEFT ONE (1) CONE /** 1) MN: A261011 SN: 0164449, *TAP: SIZE: A LOC: 12 FEET FROM P LINE AT CYPRESS ACRES DR, *MB: CODE: __ LOC: ON PINEWOOD CT 12FT FROM PL CYPRESS ACRES ****/ | 2018-03-28 | EXCAVATED METER BOX TO CHANGE BOX COCK
201800512601 | 2018-03-03 | LEAD/PLASTIC | 731 | NAPOLEON AV | CONSTANCE | WILK | PP - POOR PRESSURE ACCT#107628-556160 METER#A297804 (((CUSTOMER STATED LEAK ON SIDEWALK NEAR DRIVEWAY ME BE CAUSING PRESSURE ISSUES))) INLET LEAK IN DRIVEWAY CAUSING POOR PRESSURE (C) /** 1) MN: A297804 SN: 0026777, *TAP: SIZE: A LOC: 113 FEET FROM P LINE AT CONSTANCE, *MB: CODE: BF25 LOC: IN DRIVEWAY ON NAPOLEON AVE 110FT FROM PL OF ****/ | 2018-03-12 | EXAMINE WATER LOOK AT ABOVE LOCATION FOUND 1" CONTROLLING LINE LEAKING CAUSING POOR PRESSURE,REPLACED 20 FT OF 1" TUBING TIED INTO LEAD DUR TO LINE CROSSING NAPOLEON AVE
201800513302 | 2018-03-03 | LEAD/PLASTIC | 3420 | ADRIAN |  | WMTBG | ACCT#236100-411049 MET#A355238 PLEASE LOCATE & RAISE TO GRADE /** 1) MN: A325238 SN: 0165203, *TAP: SIZE: B LOC: 0 FEET FROM P LINE AT , *MB: CODE: OOO LOC: ON ADRAIN ON CORNER OF BAILEY 9FT OUTSD PL ****/ /** 1) MN: A325238 SN: 0165203, *TAP: SIZE: B LOC: 0 FEET FROM P LINE AT , *MB: CODE: OOO LOC: ON ADRAIN ON CORNER OF BAILEY 9FT OUTSD PL ****/ | 2018-06-11 | EXAMINED AREA LOCATED METER BOX EXCAVATED THROUGH TREE ROOTS RAISED TO GRADE WITH NEW METER BOX COMPLETE NO LEAKS OBSERVED BACKFILLED AND DRESSED UP AREA
201800513402 | 2018-03-03 | LEAD | 500 | 1ST | ROUSSEAU | WMRE | ACCT#106072031 MET#A356172 PLEASE LOC & RASE TO GRADE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ UNABLE TO LOCATE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-05-19 | EXCAVATED IN THE MUD PLOT EXPOSE 5/8 BOX METER AND RAISE METER BOX UP TO GRADE AND REPLACE METER BOX COMPLETE FOUND PLASTIC ON THE OUTLET IN LEAD ON THE INLET SERVICE BACKFILL,,,JOB COMPLETE
201800514801 | 2018-03-03 | LEAD/PLASTIC | 309 | RIVER OAKS DR | COPERNICUS | WILK | ML METER LEAK ACCT# 227839-416088 METER# A120527 INLET SERVICE LEAK @ THE METER IN GRASS /** 1) MN: A120527 SN: 0117782, *TAP: SIZE: B LOC: 251 FEET FROM P LINE AT COPERNICUS, *MB: CODE: CDL LOC: ON RIVER OAKS DR., 251' FROM P.L. COPERNICUS, 7' ****/ | 2018-03-21 | ARRIVED ON JOBSITE EXAMINED FOUND LEAK ON INLET EXCAVATED BY HAND AND REPAIRED LEAK AND BACKFILLED
201800515301 | 2018-03-03 | LEAD | 1129 | PORT | MARAIS | WILK | WM LEAK IN THE STREET CHANGED FROM 1100BLK PORT INLET SERVICE LEAK IN THE GUTTER BOTTOM FLOODING STREET /** 1) MN: A234824 SN: 0062173, *TAP: SIZE: A LOC: 61 FEET FROM P LINE AT PORT, *MB: CODE: ADHK LOC: ON MARAIS,60.5' FROM P.L. PORT ****/ | 2018-03-26 | EXCAVATED IN GUTTER BOTTOM AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201800518002 | 2018-03-04 | LEAD/PLASTIC | 3834 | GEN MEYER AV | RICHLAND RD | WMRE | ACCT#205561119 METER#A410226 NEED MACHINE METER BURIED,LOCATE & RAISE /** 1) MN: A337290 SN: 0132619, *TAP: SIZE: A LOC: 268 FEET FROM P LINE AT RICHLAND PL., *MB: CODE: ADL5 LOC: ON GEN. MEYER AVE., 268' FROM P.L. RICHLAND PL., ****/ /** 1) MN: A337290 SN: 0132619, *TAP: SIZE: A LOC: 268 FEET FROM P LINE AT RICHLAND PL., *MB: CODE: ADL5 LOC: ON GEN. MEYER AVE., 268' FROM P.L. RICHLAND PL., ****/ | 2018-03-10 | EXAMINED LEAKING AREA TRACED LINE TO PROERTY OBSERVED LEAK OF OUTLET SERVICE REPAIRES LEAK RAISED METER BOX TO GRADE BACKFILLED WITH SAND JOB REPAIRED
201800521201 | 2018-03-05 | LEAD | 2623 | CHOCTAW | LAW | WILK | METER LEAK A-409416 ACCT #186502-421664 INLET SERVICE LEAK IN BOX /** 1) MN: A254784 SN: 0141446, *TAP: SIZE: B LOC: 184 FEET FROM P LINE AT LAW, *MB: CODE: BD25 LOC: MTR ON CHOCTAW 183FT FROM PL LAW 5FT OUTSD PL ****/ | 2018-04-03 | ARRIVED AT ABOVE LOCATION EXCAVATED IN 3 X 3 CUT IN SIDEWALK + FOUND 5/8 INCH CURB COCK LEAKING + REPAIRED IT
201800521701 | 2018-03-05 | LEAD | 615 | MARENGO | ANNUNCIATION | WILK | ML- METER LEAK ACCT# 156476-556496 MTR# A280170 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A280170 SN: 0045116, *TAP: SIZE: A LOC: 108 FEET FROM P LINE AT ANNUNCIATION, *MB: CODE: BD25 LOC: 108FT FROM PL ANNUNCIATION 11' OUTSIDE PL 4' INSI ****/ | 2018-03-05 | EXCAVATED IN MUD PLOT ON INLET LEAK MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND ON LEAD REFER TO ZONE 3 TO REPLACE LEAD
201800521702 | 2018-03-05 | LEAD | 615 | MARENGO | ANNUNCIATION | WSNR | REFER TO THE ZONE TO REMOVE LEAD LINE FROM MAIN TO METER /** 1) MN: A280170 SN: 0045116, *TAP: SIZE: A LOC: 108 FEET FROM P LINE AT ANNUNCIATION, *MB: CODE: BD25 LOC: 108FT FROM PL ANNUNCIATION 11' OUTSIDE PL 4' INSI ****/ | 2018-05-30 | CANCEL WORK ORDER, JOB SHOULD BE UNDER CONTRACTOR WORK NOT SERVICE REQUEST
201800521901 | 2018-03-05 | LEAD | 510 | N LOPEZ |  | WMTLK | MI-LEAK BETWEEN THE SIDEWALK AND THE STREET EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: B020418 SN: 0128285, *TAP: SIZE: B LOC: 96 FEET FROM P LINE AT LOPEZ N, *MB: CODE: AK3 LOC: 94FT. FRM PL LAFITTE ON LOPEZ ****/ | 2018-04-02 | EXCAVATED 3 X 3 GUTTER AND ADDITIONAL 3 X 2 MUD PLOT RENEWED OUTLET SERVICE LINE TO PROPRTY BACKFILLED AND CLEANED THE AREA REFER BACK TO ZONE 4 TO REMOVE LEAD LINE FROM THE STREET
201800524801 | 2018-03-05 | LEAD/PLASTIC | 1000 | THAYER | NEWTON | WILK | ML- METER LEAK METER# A307658 ACCT# 225981-403587 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A330713 SN: 0098653, *TAP: SIZE: A LOC: 19 FEET FROM P LINE AT NEWTON, *MB: CODE: CD LOC: ON THAYER AVE., 18.5' FROM P.L. NEWTON, 6' OUTSIDE ****/ | 2018-03-26 | EXAMINED METER EXCAVATED ON OUTLET SERVICE OBSERVED LEAK ON OUTLET SERVICE OBSERVED LEAD ON OUTLET SERVICE LEAD ON INLET SERVICE ALSO TRACED LINE UNABLE TO DIG THROUGH BRICKS IN GROUND REPAIRED LEAK UNABLE TO FINISH DUE TO TIME
201800525001 | 2018-03-05 | LEAD | 4308 | CLIO | S SALCEDO | WILK | WM LEAK IN SIDEWALK INLET SERVICE LEAK IN SIDEWALK FLOODING SIDEWALK 05/25/18 UPGRADE TO B LEAVE IN SYSTEM PER INSPC B BOURNES (AJR) 06/26/18 PER S/R 12844907 LEAK AT THE SIDEWALK (KSW) /** 1) MN: A219520 SN: 0090005, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT GAYOSO S, *MB: CODE: BD LOC: ON CLIO 72FT FROM PL OF S GAYOSO 4FT OUTSIDE PL ****/ | 2018-07-13 | REPLACED 5/8 CUCRB COCK IN METER BOX .NO METER RAISED BOX TO GRADE.TIED INTO LEAD.
201800527501 | 2018-03-05 | LEAD | 1626 | TOURO | N CLAIBORNE AV | WILK | ML-METER LEAK ACCT#194231-493926 METER #A412255 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A329387 SN: 0043071, *TAP: SIZE: B LOC: 110 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: CEL1 LOC: ON TOURO 108' FROM PL N CLAIBORNE AVE 8' OUTSIDE P ****/ | 2018-03-28 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA REFER BACK TO ZONE 4 TO RENOVE LEAD FROM THE STREET
201800528401 | 2018-03-05 | LEAD | 606 | BIENVILLE | CHARTRES | WILK | ML- METER LEAK ACCT# 100822-563084 MTR# A225010 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A225010 SN: 0003245, *TAP: SIZE: B LOC: 49 FEET FROM P LINE AT CHARTRES, *MB: CODE: CE LOC: ON BIENVILLE,49' FROM U.P.L. CHARTRES ****/ | 2018-03-27 | EXCAVATED IN BRICK SIDEWALK + REPLACED CURB COCK BACKFILLED + DRESSED UP AREA
201800529001 | 2018-03-05 | LEAD/PLASTIC | 333 | ELIZA |  | WLPR | PP-POOR PRESSURE ACCT#226280-400865 METER#A342113 EXAMINE INLET FOR POOR PRESSURE /** 1) MN: SN: 0036417, *TAP: SIZE: A LOC: 81 FEET FROM P LINE AT SEGUIN, *MB: CODE: CFLM LOC: ON ELIZA 78FT FROM P.L. SEGUIN 1FT OUTSIDE P.L. ****/ | 2018-05-24 | ARRIVED ON JOBSITE EXAMINED INLET AND OUTLET FOUND NO LEAK ALSO EXAMINED STOP AND WASTE ON PROPERTY FOUND PRESSURE WAS GOOD
201800529301 | 2018-03-05 | LEAD | 2812 | BRUXELLES | PARIS AV | WILK | ML METER LEAK ACCT# 129704-713993 METER# A417878 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: 000000 SN: 0058675, *TAP: SIZE: A LOC: 118 FEET FROM P LINE AT INDUSTRY, *MB: CODE: CDL LOC: 117' P.L. INDUSTRY ****/ | 2018-03-14 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201800530401 | 2018-03-06 | LEAD/PLASTIC | 4615 | EASTERN | LOMBARD | WILK | ML- METER LEAK MTR# A 129495 ACCT# 152937-479057 EXAMINE INLET SERVICE INSIDE METER BOX /** 1) MN: A129495 SN: 0088751, *TAP: SIZE: A LOC: 81 FEET FROM P LINE AT LOMBARD, *MB: CODE: BDR5 LOC: ON EASTERN, 80.5' FROM P.L. LOMBARD,10.5' OUTSIDE ****/ | 2018-03-15 | EXCAVATED IN A 4X4 MUD PLOT BY HAND. FOUND LEAD ON INLET AND PLASTIC ON OUTLET WITH 5/8 HAND WHEEL LEAKING. REPLACE 5/8 HAND WHEEL. RAISED METER TO GRADE BACKFILL WITH RIVER SAND. JOB COMPLETE.
201800530801 | 2018-03-06 | LEAD | 5418 | ANNUNCIATION | JEFFERSON AV | WILK | ML--METER LEAK ACCT# 178681-566736 METER# A260834 INLET SERVICE LEAK INSIDE METER BOX, FOUND METER OFF LEFT OFF /** 1) MN: A260834 SN: 0124458, *TAP: SIZE: A LOC: 145 FEET FROM P LINE AT JEFFERSON AVE, *MB: CODE: AEK7 LOC: 147FT PL JEFFERSON AV 4' OUTSIDE 4' INSIDE CURB ****/ | 2018-07-06 | MADE 3X 5 CUT IN SIDEWALK .REPLACED 5/8 CURB COCK TIED IN TO LEAD.REMOVED LEAD FROM HAND WHEEL TO PROPERTY REPLACE WITH 3/4 PLASTIC.
201800532501 | 2018-03-06 | LEAD/PLASTIC | 5647 | VERMILLION BL | PRENTISS AV | WILK | IINLET LEAK VISIBLE CAUSING PRESSURE PROBLEMS & FLOODING THE GUTTER BOTTOM AREA /** 1) MN: B028896 SN: 0112829, *TAP: SIZE: B LOC: 34 FEET FROM P LINE AT PRENTISS AVE, *MB: CODE: CDM LOC: 34FT FROM PL PRENTISS AVE 9' OUTSIDE PL ****/ | 2018-03-09 | EXCAVATED AND MADE REPAIRS ON A 3/4" INLET SERVICE LEAK LEAD PLASTIC ON THE OUTLET
201800534101 | 2018-03-06 | LEAD | 3702 | N CLAIBORNE AV | INDEPENDENCE | WILK | ML- METER LEAK MN:A399724 ACCT #163653-430495 INLET SERVICE LEAK INSIDE METER BOX CAUSING OVERFLOW /** 1) MN: A307269 SN: 0103173, *TAP: SIZE: A LOC: 13 FEET FROM P LINE AT PAULINE, *MB: CODE: CD LOC: ON CLAIBORNE 13FT FROM DIV P/L PAULINE ****/ | 2018-03-27 | ARRIVED AT ABOVE LOCATION EXCAVATED IN MUD PLOT FOUND 5/8 INCH CURB COCK LEAKING AND REPAIRED
201800534401 | 2018-03-06 | LEAD | 2034 | IBERVILLE | N JOHNSON | WILK | WM LEAK ON GRASSY AREA OF VACANT INLET SERVICE LEAK IN MUDPLOT FLOODING SIDEWALK AT VACANT LOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-03-22 | EXCAVATED AND MADE REPAIR ON ABANDON INLET SERVICE BACKFILL JOB WITH RIVERSAND
201800534601 | 2018-03-06 | LEAD | 1703 | N GALVEZ |  | WILK | BAD LEAK COMING FROM THE CURB COCK PLEASE REPAIR AND SET A 5/8 METER CUSTOMER IS STATES NEED WATER ASAP LOCATION #157498 INLET SERVICE LEAK IN METER BOX BAD BLEEDER VALVE 3/9/18 CUSTOMER OUT OF WATER, WAITING TO MOVE IN. PER S/R # 12834795 (PET) /** 1) MN: A231083 SN: 0140040, *TAP: SIZE: __ LOC: 62 FEET FROM P LINE AT AUBRY, *MB: CODE: ADH LOC: 62FT FROM PL AUBRY 7FT OUTSD PL 3FT INSD ****/ | 2018-03-12 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201800534901 | 2018-03-06 | LEAD/PLASTIC | 5925 | TULLIS DR | WOODLAND DR | WILK | MI - LEAK ON SIDEWALK INLET SERVICE LEAK IN MUD @ CURB /** 1) MN: A308112 SN: 0162775, *TAP: SIZE: A LOC: 192 FEET FROM P LINE AT WOODLAND PL, *MB: CODE: OOOO LOC: ON TULLIS 203FT FROM PL WOODLAND 9FT OUTSD PL ****/ | 2018-04-06 | ARRIVED ON JOBSITE EXAMINED METER FOUND LEAK ON OUTLET EXCAVATED BY HAND AND REPAIRED AND BACKFILLED
201800536101 | 2018-03-07 | LEAD | 2804 | ORLEANS AV |  | WDSM | DECREASE EXISTING 2 INCH WATER METER TO A 5/8 INCH WATER METER IN SAME LOCATION FOR 2804 ORLEANS AVE FOR THE FLAT SUM OF $200.00 SWBNO APP#122596 WFA 2562 /** 1) MN: E004755 SN: 0048232, *TAP: SIZE: E LOC: 61 FEET FROM P LINE AT WHITE N, *MB: CODE: BDK LOC: ON ORLEANS 61FT FROM PL N WHITE 8FT OUTSD PL ****/ | 2018-04-18 | REDUCE 2 INCH METER TO 5/8 INCH METER INSIDE MANHOLE OLD MTR INFO: MTR#:E008456 FAC#:14099008 MAKE:HERSEY READ:000004
201800536201 | 2018-03-07 | LEAD/PLASTIC | 513 | OLIVIER | ELIZA | WILK | WM-LEAK IN BETWEEN STREET AND SIDEWALK INLET SERVICE LEAK IN MUDLOT /** 1) MN: A301282 SN: 0019311, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT ELIZA, *MB: CODE: CDLM LOC: ON OLIVIER, 112' FROM U.S.P.L. ELIZA ****/ | 2018-03-16 | ARRIVED ON JOBSITE EXAMINED METER FOUNDLEAK ON INLET EXCAVATED BY HAND AND REPAIRED LEAD IS ON INLET
201800536401 | 2018-03-07 | LEAD/PLASTIC | 2968 | GEN COLLINS AV |  | WDSM | DECREASE EXISTING SERVICE FROM A 1 1/2 WATER METER TO A 5/8 INCH WATER METER IN SAME LOCATION FOR 2968 GEN COLLINS AV, FOR THE FLAT SUM OF $200.00 SWBNO APP#122578 WFA 2560 /** 1) MN: D004058 SN: 0163378, *TAP: SIZE: D LOC: 335 FEET FROM P LINE AT GEN DE GAULLE DR, *MB: CODE: OOO LOC: ON GEN COLLINS 335FT FROM PL GEN DE GAULLE ****/ | 2018-03-22 | EXAMINED MANHOLE WITH METER BROKE OUT CONCRETE IN WHICH METER WAS SET INTO REPLACE METER WITH NEW METER CLEAN SITE *************OLD METER INFO************* METER:D004058 FAC:30165659 MAKE:SENSUS READ:29894
201800539201 | 2018-03-07 | LEAD | 502 | ST PETER | DECATUR | WILK | ML-METER LEAK ACCT# 211820-429148 METER # A356948 BAD CURB COCK, NO METER IN BOX /** 1) MN: A278617 SN: 0025491, *TAP: SIZE: D LOC: 47 FEET FROM P LINE AT DECATUR, *MB: CODE: CD LOC: ON ST PETER 47' FROM P.L. DECATUR 6' OUTSIDE 3' ** 2) MN: A278618 SN: 0025491, *TAP: SIZE: C LOC: 48 FEET FROM P LINE AT DECATUR, *MB: CODE: CD LOC: ON ST PETER 48' FROM P.L. DECATUR 6' OUTSIDE 3' THERE IS 1 MORE NOT LISTED. ****/ | 2018-06-05 | EXCAVATED IN FLAGSTONE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201800539701 | 2018-03-07 | LEAD | 3219 | GRAVIER | S LOPEZ | WMTLK | ML-METER LEAK ACCT#109747-702046 METER#A295370 EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN BOX /** 1) MN: A251720 SN: 0049849, *TAP: SIZE: A LOC: 145 FEET FROM P LINE AT LOPEZ S, *MB: CODE: CFL2 LOC: ON GRAVIER 142FT FROM LOPEZ S ****/ | 2018-03-07 | EXCAVATED IN MUD PLOT. REPAIR 5/8 STOP & WASTE ON LEAD LINE. DRESS UP RIVERSAND. JOB REF TO ZONE 3 TO TAKE LEAD LINE OUT ON INLET SIDE
201800540601 | 2018-03-07 | LEAD/PLASTIC | 1620 | FERN | BIRCH | WILK | ML- METER LEAK MTR# A302597 ACCT # 142664-582267 INLET SERVICE LEAK IN THE GRASS IN FRONT METER FLOODING GRASSY AREA /** 1) MN: A302597 SN: 0073961, *TAP: SIZE: B LOC: 138 FEET FROM P LINE AT BIRCH, *MB: CODE: AD25 LOC: 138' P.L. BIRCH ****/ | 2018-04-09 | EXCAVATED AND MADE REPAIRS ON A 5/8" INLET SERVICE LEAK LEAD LINE PLASTIC OUTLET JOB COMPLETE
201800543401 | 2018-03-07 | LEAD/PLASTIC | 24 | VIVIAN CT | HUNTLEE DR | WILK | ML-METER LEAK ACCT#227102-416000 METER#A259101 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A195101 SN: 0123308, *TAP: SIZE: A LOC: 525 FEET FROM P LINE AT HUNTLEE DR, *MB: CODE: BFL LOC: ON VIVIAN CT.,523' FROM P.L. HUNTLEE DR., 4' OUT- ****/ | 2018-04-03 | PICKED UP MUD AND BACKFILLED WITH RIVER SAND THE MUD LEFT ON SIDEWALK IS THE RESULT OF SINKING SIDEWALK AND NOT RELATED TO JOB
201800544301 | 2018-03-08 | LEAD | 2801 | JOSEPHINE | CLARA | WILK | ML- METER LEAK ACCT# 119781-576998 METER# A345300 INLET SERVICE LEAK BAD BLEEDER VALVE /** 1) MN: A265206 SN: 0033592, *TAP: SIZE: A LOC: 325 FEET FROM P LINE AT JOSEPHINE, *MB: CODE: CEHL LOC: ON CLARA,33.5' FROM L.S.P.L. JOSEPHINE ****/ | 2018-07-07 | REPLACED 3/4 SERVICE FROM METER TO PROPERTY LNE ALSO REPLACED 5/8 CURB COCK TIED INTO LEAD.(SOC 3FT X 4 FT S/W)
201800546301 | 2018-03-08 | LEAD | 1641 | CRETE | FULTON | WILK | ML-- METER LEAK METER# A282220 ACCT#124050-491223 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A282220 SN: 0044556, *TAP: SIZE: A LOC: 36 FEET FROM P LINE AT CRETE, *MB: CODE: BDHM LOC: ON FORTIN 33.5' FROM USPL CRETE ****/ | 2018-03-19 | ARRIVED AT ABOVE LOCATOION EXCAVATED IN SIDEWALK + REPAIRED 5/8 INCH CURB COCK + HANDWHEEL + RAN PLASTIC TO PROPERTY
201800547101 | 2018-03-08 | LEAD | 1705 | 8TH |  | WMTLK | BAD MTR LEAK EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: A248464 SN: 0132090, *TAP: SIZE: B LOC: 26 FEET FROM P LINE AT EIGHTH, *MB: CODE: BF LOC: ON CARONDELET 25' FROM PL EIGHT 2' OUTSIDE PL 8' I ** 2) MN: A311210 SN: 0132090, *TAP: SIZE: B LOC: 25 FEET FROM P LINE AT EIGHTH, *MB: CODE: BF LOC: SEC METR ON CARONDELET 24' FROM PL EIGHTH 2' OUTSI THERE ARE 2 MORE NOT LISTED. ****/ DOTTIE READY 5-14-18 EXP 6-3-18 | 2018-05-17 | ARRIVED AT THE ABOVE LOCATION EXAMINED THE JOB, FOUND LEAK ON 5/8 LEAD INLET, MADE A 3X3 SIDEWALK CUT THEN MADE REPAIRS. THEN BACKFILLED AND CLEANED THE AREA REFER TO CREW TO RENEW THE INLET FROM THE METER TO THE MAIN. NEED PAVING
201800548901 | 2018-03-08 | LEAD | 2419 | CHARTRES | MANDEVILLE | WILK | MI- CUT SERVICE ENTERGY GAS BROKE A LINE IN SIDEWALK ABOVE ADDRESS WITHOUT WATER CUT INLET AT MAIN BY ENTERGY GAS CUSTOMERS OUT OF WATER ALSO AFFECTING HOUSE ACROSS STREET AT 2412 CHARTRES **DAMAGE CLAIM** /** 1) MN: A258357 SN: 0057716, *TAP: SIZE: A LOC: 144 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: BFKN LOC: 144' P.L. MANDEVILLE ****/ | 2018-03-08 | EXCAVATED IN MUDPLOT OVER 6INCH WATER MAIN REPAIR 6INCH WATER MAIN WITH 6INCH 3/4 TAP FULL CIRCLE CLAMP TIRED IN LEAD LINE JOB REFERRED ZONE 4 TO TAKE LEAD OUT FROM WATER MAIN TO METER
201800552101 | 2018-03-09 | LEAD/PLASTIC | 2035 | ROBERT E LEE BL | CAMERON BL | WILK | ML METER LEAK METER# B033196 ACCT# 164787-504753 INLET SERVICE LEAK /** 1) MN: B030460 SN: 0101382, *TAP: SIZE: B LOC: 39 FEET FROM P LINE AT ROBERT E LEE BL, *MB: CODE: __ LOC: 39' P/L ROBERT E LEE BL 7' OUTSIDE 4' INSIDE CURB ****/ | 2018-06-23 | EXCAVATED A 6 X 25 CUT IN CONCRETE STREET & 4 X 10 TRECH IN MUDPLOT TO REPAIR ON A 3/4 INLET SERVICE LEAK REPLACE 26FT OF LEAD WITH PVC PIPE FROM CURB TO METERBOX AND ADJUST UP TO GRADE BACKFILLED AND DRESSUP WITH RIVERSAND & COLDMILL PAVING 6 X 25 CUT CB/S JOB COMPLETE
201800552201 | 2018-03-09 | LEAD/PLASTIC | 2521 | ROBERT | MAGNOLIA | WILK | ML-METER LEAK ACCT# 134634-569769 METER#A355633 INLET SERVICE LEAK BEHIND CURB COCK FLOODING GRASSY AREA 03/27/18 LEAK HAS GOTTEN WORSE PER R#12836530 (AJR) /** 1) MN: A126809 SN: 0065344, *TAP: SIZE: A LOC: 158 FEET FROM P LINE AT MAGNOLIA, *MB: CODE: CDKM LOC: 158' P.L. MAGNOLIA ****/ | 2018-07-04 | EXCAVTED IN MUDPLOT OVER INET SERVICE.REPLACED 5/8 CURB COCK.MADE REPAIR ON LEAD SERVICE TIED BACK INTO LEAD.
201800555701 | 2018-03-10 | LEAD | 2546 | JONQUIL | FRANKLIN AV | WILK | IN-LET LEAK INSTREET CAUSING POOR PRESSUE.. /** 1) MN: A271157 SN: 0084925, *TAP: SIZE: A LOC: 315 FEET FROM P LINE AT IRIS, *MB: CODE: CD2 LOC: ON JONQUIL 315' FROM PL IRIS ****/ | 2018-03-11 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 5/8 TAIL PIECE LEAKING AT 4" WATER MAIN REPLACED 4FT OF 3/4 TUBING TIED IN TO LEAD UNABLE TO REPLACED SERVICE DUE TO CAR PARKED ON METER REFERRED TO ZONE 5 TO REMOVE LEAD
201800555901 | 2018-03-10 | LEAD | 1605 | MANDEVILLE | N CLAIBORNE AV | WMTLK | LOCATIONID#127403-700577 METER#A294245 LEAK INSIDE METERBOX /** 1) MN: A234017 SN: 0052725, *TAP: SIZE: A LOC: 42 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: BDN LOC: ON MANDEVILLE,41.5' FROM L.S.P.L. NO. CLAIBORNE ****/ | 2018-04-02 | RRIVED AT ABOVE LOCATION EXCAVATED IN SIDEWALK FOUND 5/8 INCH CURB COCK LEAKING + REPAIRED IT
201800561701 | 2018-03-11 | LEAD | 925 | N DERBIGNY | DUMAINE | WILK | ML- METER LEAK METER#A288979 ACCT#106800-525102 INLET SERVICE LEAK IN BOX /** 1) MN: A288979 SN: 0031715, *TAP: SIZE: A LOC: 141 FEET FROM P LINE AT ST PHILIP, *MB: CODE: BFL LOC: ON N DERBIGNY 142.5' FROM PL ST PHILIP ****/ | 2018-04-10 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING ON LEAD LINE + REPAIRED FOUND OUTLET EXPOSED + RAN PLASTIC TO PLSTIC
201800563401 | 2018-03-12 | LEAD | 723 | GALLIER | DAUPHINE | WILK | WM- LEAK IN THE STREET INLET SERVICE LEAK IN HOLE ON PREVIOUS CUT JUST REPAIRED /** 1) MN: A340336 SN: 0055058, *TAP: SIZE: A LOC: 139 FEET FROM P LINE AT DAUPHINE, *MB: CODE: BDKO LOC: ON GALLIER,141' FROM L.S.P.L. DAUPHINE ****/ | 2018-05-31 | EXAMINE JOB ABOVE LOCATION FOUND NO LEAK JOB COMPLETE
201800563801 | 2018-03-12 | LEAD/PLASTIC | 1102 | VALENCE | CHESTNUT | WILK | ML - METER LEAK ACCT#109766-714746 METER#A378663 INLET SERVICE LEAK BEHIND CURB COCK /** 1) MN: A284175 SN: 0011340, *TAP: SIZE: B LOC: 66 FEET FROM P LINE AT VALENCE, *MB: CODE: AGH LOC: ON CHESTNUT 66FT FROM VALENCE 2ND MTR ****/ | 2018-07-05 | EXCAVTED OVER 5/8 INLET SERVICE IN SIDEWALK MADE 3X5 CUT .INLET SERVICE IS LEAD NEED TO BE REMOVED FROM METER BOX TO WATER MAIN .REPLACED 5/8 METER BOX COCK.
201800564101 | 2018-03-12 | LEAD | 1137 | LIZARDI |  | WMRE | MI- LEAK AT THE SIDEWALK THERE IS NO ACCT AT THE ADDRESS BUT CUT INSIST THERE IS WATER COMING FROMT THE METER. LOCATE & CLOSE ABANDON SERVICE AREA FLOODED /** 1) MN: A213518 SN: 0077773, *TAP: SIZE: A LOC: 3 FEET FROM P LINE AT MARAIS, *MB: CODE: BDK LOC: ON LIZARDI 3' FROM PL MARAIS 8' OUTSIDE PL 2' INS ****/ | 2018-05-02 | EXCAVATED AND LOCATED METER BOX IN MUD PLOT BACKFILL JOB WITH RIVERSAND MADE REPAIR ON INLET SERVICE JOB COMPLETE
201800565401 | 2018-03-12 | LEAD | 2229 | MARIGNY | N MIRO | WILK | WM - LEAK IN THE SIDEWALK CHANGED FROM 2223 MARIGNY EXAMINE INLET SERVICE FOR A LEAK. CARS ROLLING OVER SIDEWALK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-04-27 | EXCAVATED 5 X 2 SIDEWALK CUT RENEWED OUTLET UP TO PROPERTY BACKFILLED AND CLEANED THE AREA
201800565501 | 2018-03-12 | LEAD/PLASTIC | 3352 | PLYMOUTH PL | DOVER PL | WILK | MI- LEAK IN THE SIDE WALK INLET SERVICE LEAK IN THE MUD PLOT FLOODING SIDEWALK /** 1) MN: A317383 SN: 0125607, *TAP: SIZE: C LOC: 385 FEET FROM P LINE AT DOVER PL, *MB: CODE: ADKM LOC: ON PLYMOUTH PL., 395' FROM P.L. DOVER PL., 8' OUT- ****/ | 2018-03-19 | EXCAVATED INLET AND OUTLET AND FOUND LEAK ON LED OUTLET ALSO FOUND BAD BOX COCK RAN PLASTIC FROM METER BOX TO PROPERTY AND CHANGED BOX COCK LEAD NEEDS TO BE REMOVED FROM INLET NEEDS RIVER SAND
201800565901 | 2018-03-12 | LEAD | 2134 | BARTHOLOMEW | N GALVEZ | WILK | MI I LEAK IN THE STREET EXAMINE INLET SERVICE FOR A LEAK @ THE MAIN /** 1) MN: SN: 0084749, *TAP: SIZE: A LOC: 295 FEET FROM P LINE AT GALVEZ N, *MB: CODE: ADLM LOC: ON BARTHOLOMEW 268' FROM PL N GALVEZ 7' OUTSIDE PL ****/ | 2018-04-21 | EXCAVATED 4 X 2 STREET CUT ALSO 4 X 3 MUD PLOT MADE REPAIR ON ABANDON INLET SERVICE TO STOP LEAK BACKFILLED ND CLEANED THE AREA
201800567901 | 2018-03-12 | LEAD/PLASTIC | 5847 | LOUISVILLE | KENILWORTH | WILK | WM LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET FLOODING STREET /** 1) MN: C013446 SN: 0086467, *TAP: SIZE: C LOC: 193 FEET FROM P LINE AT KENILWORTH, *MB: CODE: BDM7 LOC: ON LOUISVILLE 193FT FROM PL KENILWORHT 9FT OUTSIDE ****/ | 2018-06-21 | EXCAVATED IN MUDPLOT OVER A 1' OUTLET SERVICE LEAK NEAR PROPERTY CHANGED 1' HANDWHEEL AND RENEW 1' PVC FROM METERBOX TO PROPERTY BACKFILLED AND DRESSUP [ NEED TO REPLACE LEAD FROM MAIN TO METERBOX
201800571001 | 2018-03-13 | LEAD/PLASTIC | 2211 | KRAFT PL | LAURADALE DR | WILK | ML- METER LEAK ACCT# 230096-408937 MTR# A128063 INLET SERVICE LEAK IN THE MUD PLOT FLOODING CURB /** 1) MN: A128063 SN: 0134884, *TAP: SIZE: B LOC: 68 FEET FROM P LINE AT RUCK, *MB: CODE: OOOO LOC: ON KRAFT PL 69' FROM PL RUCK 7' OUTSIDE PL 4'INSID ****/ | 2018-03-23 | EXAMINED LEAKING METER EXCAVATED INLET AND OUTLET SERVICE OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK BACKFILLED WITH SAND
201800572401 | 2018-03-13 | LEAD/PLASTIC | 627 | OPELOUSAS AV | VERRET | WILK | METER LEAK A-419851 ACCT # 223971-40056 INLET SERVICE LEAK ON THE SIDEWALK /** 1) MN: A336827 SN: 0088966, *TAP: SIZE: A LOC: 206 FEET FROM P LINE AT OPELOUSAS AVE, *MB: CODE: AF LOC: INSIDE 206'FROM CORNER P L VERRET STORE ****/ | 2018-03-27 | ARRIVED ON JOBSITE EXAMINED METER FOUND LEAK ON OUTLET BROKE CONCRETE EXCAVATED BY HAND AND REPAIRED
201800574801 | 2018-03-13 | LEAD/PLASTIC | 1312 | ODEON AV |  | WILK | MI- METER BOX LEAKING INLET SERVICE LEAK IN THE MUD PLOT FLOODING CURB GETTING OFF IN THE DCB /** 1) MN: 000000 SN: 0122601, *TAP: SIZE: A LOC: 157 FEET FROM P LINE AT LAMARQUE, *MB: CODE: CEK LOC: ON ODEON 157FT FROM LAMARQUE ****/ | 2018-04-03 | EXCAVATED METER BOX TO EXAMINE LEAK AND FOUND LEAK ON COCK REPAIRED LEAK ON COCK BY REPLACING COCK
201800578201 | 2018-03-13 | LEAD/PLASTIC | 1724 | MURL | LAWRENCE ST | WILK | ML METER LEAK ACCT# 226154-406734 METER# A384097 ILET SERVICE LEAK AT DRIVEWAY FLOODING CURB /** 1) MN: A288899 SN: 0135964, *TAP: SIZE: B LOC: 153 FEET FROM P LINE AT MAGELLAN, *MB: CODE: BDK2 LOC: ON MURL 153' FROM PL MAGELLAN 8' OUTSIDE PL 4' IN ****/ | 2018-04-04 | EXCAVATED METER BOX AND REPLACED BAD BOX COCK
201800578401 | 2018-03-13 | LEAD/PLASTIC | 5654 | ABBEY DR | CHELSEA DR | WILK | ML- METER LEAK ACCT# 231764-418109 MTR# C020069 INLET SERVICE LEAK IN GRASS AT METER FLOODING CURB /** 1) MN: C020069 SN: 0143405, *TAP: SIZE: C LOC: 340 FEET FROM P LINE AT CHELSEA DR, *MB: CODE: AD6 LOC: RES. 343FT FROM PL CHELSEA ****/ | 2018-03-22 | ARRIVED ON JOBSITE EXAMINED METER FOUND LEAK INLET EXCAVATED BY HAND HAD TO CHANGE METER AND REPAIR OLD METER INFO: METER:C020069 FACT:38452088 MAKE:SENSUS READ:17314
201800583001 | 2018-03-14 | LEAD | 1701 | N GALVEZ |  | WILK | /** 1) MN: SN: 0170457, *TAP: SIZE: B LOC: 58 FEET FROM P LINE AT N GALVEZ, *MB: CODE: ENF1 LOC: ON N GALVEZ 31' FROM PLN GALVEZ 6' OUTSIDE PL 9' I ****/ | 2018-03-09 | EXCAVATED 4 X 4 LIMESTONES GUTTER BOTTOM FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS MADE REPAIRED ON INLET SET A 5/8 INCH METER FOR ABOVE LOCATION BACKFILL JOB WITH RIVERSAND COLDMILL
201800583801 | 2018-03-14 | LEAD | 4827 | NIGHTHART |  | WILK | ML- METER LEAK MTR# A 312735 ACCT# 175895-436492 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A312735 SN: 0119516, *TAP: SIZE: A LOC: 557 FEET FROM P LINE AT PRENTISS AVE, *MB: CODE: BDK2 LOC: RES 563FT FROM PL PRENTISS AVE 9' OUTSIDE PL 2' IN ****/ | 2018-03-28 | EXCAVATED IN INLET AND OUTLET SERVICE. FOUND INLET LEAD AND OUTLET PLASTIC TUBING. MADE REPAIRS BY REPLACING COCK, WASHERS AND HAND WHEEL. BACKFILLED DRESSED UP. NO MACHINE.
201800585201 | 2018-03-14 | LEAD | 739 | GOV NICHOLLS | ROYAL | WOLK | ML METER LEAK METER# A318995 EXAMINE OUTLET SERVICE FOR A LEAK WITH CONSTANT REGISTRATION /** 1) MN: A315784 SN: 0010067, *TAP: SIZE: A LOC: 98 FEET FROM P LINE AT BOURBON, *MB: CODE: CE LOC: 3APTS ON GOV NOCHOLLS 100FT FROM PL OF BOURBON ****/ | 2018-03-21 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201800585301 | 2018-03-14 | LEAD/PLASTIC | 335 | WHITNEY AV | ALIX | WILK | ML- METER LEAK MTR# A405937 ACCT# 303613-519222 INLET SERVICE LEAK IN THE MUD PLOT FLOODING CURB & SURROUNDING AREA /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-04-13 | FOUND WATER GUSHING IN FRONT OF THE METER BOX REPLACED LINE AND FITTING THE LINE CAME OUT OF
201800585501 | 2018-03-14 | LEAD | 2627-25 | ST ANTHONY |  | WILK | MI CUT SSERVICE BY ENTERGY AREA WITHOUT WATER *****MS ELAINE 504 593 3439********* **********DAMAGE CLAIM********** J GILLIAM 13:25 **********CUSTOMER OUT OF WATER********** CUT INLET SERVICE BY ENTERGY /** AT 2625: 1) MN: A330929 SN: 0064679, *TAP: SIZE: B LOC: 112 FEET FROM P LINE AT HOPE, *MB: CODE: __ LOC: MTR ON ST ANTHONY 210FT FRM PL HOPE 8FT OUTSD PL ** AT 2627: 2) MN: B029901 SN: 0079272, *TAP: SIZE: A LOC: 111 FEET FROM P LINE AT HOPE, *MB: CODE: CDL LOC: ON ST ANTHONY AVE 211FT FROM PL OF HOPE 8FT OUT- ****/ | 2018-03-14 | ARRIVED AT ABOVE LOCATION + FOUND ENTERGY PULLED 3/4 INCH LEAD LINE IN STREET + REPAIRED
201800585601 | 2018-03-14 | LEAD | 3432 | DERBY PL |  | WILK | ML--METER LEAK METER # B039446 ACCT#155030-492936 EXAMINE INLET SERVICE FOR A LEAK CARS ROLLING OVER METER /** 1) MN: B032039 SN: 0091653, *TAP: SIZE: B LOC: 231 FEET FROM P LINE AT SALCEDO N, *MB: CODE: ADLM LOC: ON DERBY PL.,230.5' FROM P.L. NO. SALCEDO,5.5' OUT ****/ | 2018-04-02 | EXCAVATED 3 X 2 GUTTER BOTTOM AND 3 X 3 MUD PLOT RELOCATED METER BOX TO MUD PLOT AND RENEWED OUTLET TO PROPERTY BACKFILLED AND CLEANED THE AREA REFER BACK TO ZONE 4 TO REMOVE LEAD LINE FROM STREET
201800586701 | 2018-03-14 | LEAD | 6207 | N CLAIBORNE AV |  | WILK | ML-METER LEAK ACCT#301091-454212 METER#A422520 INLET SERVICE LEAK CARS ROLLING OVER METER /** 1) MN: A331262 SN: 0127356, *TAP: SIZE: A LOC: 68 FEET FROM P LINE AT ST MAURICE, *MB: CODE: AFM LOC: RES ON CLAIBORNE 75FT FROM PL ST MAURICE ****/ | 2018-04-10 | ARRIVED AT ABOVWE FOUND 5/8 INCH CURB COCK LEAKING ON LEAD LINE /5/8 INCH HANDWHEEL LEAKING REPAIRED + RAN PLASTIC TO PROPERTY BACKFILLED
201800587001 | 2018-03-14 | LEAD/PLASTIC | 2506 | JASMINE |  | WILK | ML-METER LEAK MTR.# A 427355 ACCT.# 148292-476556 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A177122 SN: 0086212, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT IRIS, *MB: CODE: ADM LOC: 54' P.L. IRIS ****/ | 2018-03-26 | ARRIVED AT ABOVE LOCATION AND FOUND 5/8 CURB COCK LEAKING IN THE METER BOX. EXCAVATED BY HAND IN TREE ROOTS AND CUT ROOTS WITH THE CHAIN SAW AND ALSO CHANGED 5/8 CURB COCK ON LEAD LINE.
201800590702 | 2018-03-15 | LEAD | 1303 | REYNES |  | WMRE | ACCT#170697176 METER#A289854 -- NEED MACHINE METER BURIED,LOCATE & RAISE /** 1) MN: A278953 SN: 0091004, *TAP: SIZE: __ LOC: 41 FEET FROM P LINE AT REYNES, *MB: CODE: __ LOC: ON REYNES 42FT /** 1) MN: A278953 SN: 0091004, *TAP: SIZE: __ LOC: 41 FEET FROM P LINE AT REYNES, *MB: CODE: __ LOC: ON REYNES 42FT FROM PL REYNES ****/ | 2018-04-05 | EXCAVATED IN MUD PLOT + LOCATED TWO 5/8 INCH METER AT ABOVE LOCATION REPLACED ONE DAMAGED METER RAISED BOTH METER BOX BOTTOMS TO GRADE + MARKED WITH BLUE PAINT BACKFILLED + DRESSED UP AREA
201800591001 | 2018-03-15 | LEAD/PLASTIC | 4051 | CLERMONT DR | VINCENT | WMTLK | ML- METER LEAK ACCT#155075-475463 METER#A288557 EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN BOX /** 1) MN: A288557 SN: 0091742, *TAP: SIZE: A LOC: 118 FEET FROM P LINE AT ST VINCENT, *MB: CODE: ADM2 LOC: ON CLERMONT DR 118' FROM PL ST VINCENT 9' OUTSIDE ****/ | 2018-03-27 | ARRIVED AT THE ABOVE LOCATION AND FOUND CURB COCK LEAKING IN METER BOX. EXCAVATED IN MUD PLOT BY HAND REPLACED 5/8 CURB COCK. WE ALSO FOUND LEAD ON THE INLET AND PLASTIC ON THE OUT LET. CUT LEAD LINE TO THE CURB AND RAN PLASTICC FROM THE CURVE TO THE METER BOX AND ALSO RAISED METER TO GRADE. BACKFILLED WITH SAND.
201800592701 | 2018-03-15 | LEAD/PLASTIC | 1209 | SHIRLEY DR | DE ARMAS | WMTLK | MI- METER LEAK METER# A429814 ACCT# 225951-405181 EXAMINE INLET & OUTLET SERVICE FOR A LEAK IN METER BOX /** 1) MN: A312895 SN: 0095125, *TAP: SIZE: B LOC: 38 FEET FROM P LINE AT DE ARMAS, *MB: CODE: BD25 LOC: ON SHIRLEY DR., 50.5' FROM P.L. DE ARMAS, 6' OUT- ****/ | 2018-04-05 | EXAMINED JOB FOUND WATER IN METER BOX EXCAVATED ON INLET AND OUTLET BY HAND NO LEAK ON PLASTIC REPLACE HAND WHEEL AND CHANGED WASHERS
201800593601 | 2018-03-15 | LEAD | 1414 | N CLAIBORNE AV |  | WILK | WM SIDEWALK LEAK CHANGED FROM 1414 N CLAIBORNE AV INLET SERVICE LEAK IN DRIVEWAY CAR ROLLING OVER SERVIIE NEAR GAS PUMP /** 1) MN: A273086 SN: 0026252, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: BEM2 LOC: ON CLAIBORNE 82FT FORM ESPLANADE ****/ | 2018-04-04 | ARRIVED AT ABOVE LOCATION EXCAVATED IN CUT ALREADY MADE + RENEWED OUTLET TO PROPERTY
201800595202 | 2018-03-29 | LEAD | 3220 | CLOUET | BENEFIT | WMTLK | EXAMINE AREA FOE LEAK IN GRASSY AREA. UNABLE TO LOCATE VLEAK BECAUSE OF HIGH GRASS. NEED A MACHINE TO CLEAR AREA. /** 1) MN: A242644 SN: 0100399, *TAP: SIZE: A LOC: 123 FEET FROM P LINE AT BENEFIT, *MB: CODE: FKL LOC: ON CLOUET 137FT FROM PL OF BENEFIT 2FT OUTSIDE PL ****/ | 2018-04-03 | ARRIVED AT LOCATION, FOUND WATER COMING FROM GRASSY AREA. EXCAVATED IN GRASS WITH BACKHOE AND FOUND A 5/8 CURB COCK LEAKING IN METER BOX.. REPAIRED CURB COCK AND LEFT A COMPLETE 5/8 SET UP. ALSO FOUND LEAD ON INLET. (ABANDON SERVICE)
201800595601 | 2018-03-15 | LEAD | 2653 | N ROCHEBLAVE |  | WILK | WM-- LEAK IN BETWEEN STREET AND CURB INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A237789 SN: 0103783, *TAP: SIZE: A LOC: 72 FEET FROM P LINE AT ARTS, *MB: CODE: ADMK LOC: ON N ROCHEBLAVE 71.5' FROM PL ARTS 8.5' OUTSIDE PL ****/ | 2018-04-02 | ARRIVED AT ABOVE LOCATION EXCAVATED IN MUD PLOT FOUND 5/8 INCH CURB COCK LEAKING +REPAIRED IT
201800595701 | 2018-03-15 | LEAD | 846 | WILSON DR |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 142572-514362 METER NUMBER - A229515 INLET SERVICE LEAK BEHIND CURB COCK /** 1) MN: A229515 SN: 0073767, *TAP: SIZE: A LOC: 136 FEET FROM P LINE AT ELAINE, *MB: CODE: CDL3 LOC: 136FT. FRM PL ELAINE ****/ | 2018-04-02 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 METER BOX COCK TO STOP LEAK
201800597201 | 2018-03-15 | LEAD | 3225 | GRAND RTE ST JOHN | HAGAN AV | WILK | ML: METER LEAK ACCT# 118155-522086 METER# A252022 INLET SERVICE LEAK IN GRASS AT CURB /** 1) MN: A346167 SN: 0027394, *TAP: SIZE: A LOC: 122 FEET FROM P LINE AT HAGAN AVE, *MB: CODE: BDKP LOC: 124' P.L. HAGAN AVE ****/ | 2018-03-28 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING + REPAIRED BACKFILLED
201800599301 | 2018-03-16 | LEAD | 1635 | ARTS | N DERBIGNY | WILK | ML- METER LEAK MTR# A 302633 ACCT# 125189-482264 EXAMINE INLET SERVICE NO S&WV VISIBLE, FOUND CONSTANT REGISTRATION /** 1) MN: A336620 SN: 0056104, *TAP: SIZE: A LOC: 72 FEET FROM P LINE AT DERBIGNY S, *MB: CODE: BDM1 LOC: ON ARTS 74FT FROM PL OF S DERBIGNY ****/ | 2018-04-02 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH WATER METER WITH CONSTANT REGISTRATION REMOVED LEAD LINE TO PROPERTY WITH PLASTIC *BACKFILLED
201800599401 | 2018-03-16 | LEAD/PLASTIC | 2056 | N ROCHEBLAVE |  | WMTLK | AREA FLOODED. UNABLE TO SET METER. CANNOT PUMP WATER OUT FAST ENOUGH. PLEASE REPAIR AND SET 5/8 METER. LOC ID 304321 CUSTOMER IS WAITING FOR WATER. EXAMINE INLET & OUTLET SERVICE FOR A LEAK, UNABLE TO SET METER @ LOCATION ***HOUSE UNDER RENOVATIONS*** /** 1) MN: A179882 SN: 0083225, *TAP: SIZE: B LOC: 238 FEET FROM P LINE AT ANNETTE, *MB: CODE: CD LOC: ON ROCHEBLAVE 238FT FROM ANNETTE ****/ | 2018-03-24 | EXCAVATED AND MADE REPAIRS ON A 5/8 INLET SERVICE LEAK ALSO RAISED THE METER TO GRADE AND RENEWED THE OUTLET AND SET A 5/8 METER LEAD ON THE INLET PLASTIC ON THE OUTLET. JOB COMPLETE JEG
201800600001 | 2018-03-16 | LEAD | 3009 | BRUXELLES | ABUNDANCE | WMTLK | ML- METER LEAK ACCT # 135533-492234 METER #A258218 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A258218 SN: 0066368, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT ABUNDANCE, *MB: CODE: CDW2 LOC: ON BRUXELLES, 73' FROM P.L. ABUNDANCE ****/ | 2018-03-29 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH WASHERS WAS CAUSING LEAK + CHANGED THEM ALSO REPLACED BROKEN METER CASING
201800602601 | 2018-03-16 | LEAD | 1308 | CONGRESS | URQUHART | WILK | ML: METER LEAK, MTR # A371133, ACCT # 220639-712816 INLET SERVICE LEAK IN MUDPLOT BETWEEN CURB AND SIDEWALK /** 1) MN: C023507 SN: 0045219, *TAP: SIZE: C LOC: 89 FEET FROM P LINE AT URQUHART, *MB: CODE: BDM4 LOC: ON CONGRESS 89FT FROM PL OF URQUHART 7FT OUTSIDE ****/ | 2018-04-03 | EXCAVATED 3 X 2 GUTTER BOTTOM REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201800602801 | 2018-03-16 | LEAD | 1632 | ST ANTHONY | N DERBIGNY | WILK | MI- LEAK IN SIDEWALK FLOODING AREA INLET SERVICE LEAK IN SIDEWALK FLOODING SIDEWALK /** 1) MN: A240064 SN: 0069865, *TAP: SIZE: B LOC: 242 FEET FROM P LINE AT CLAIBORNE AVE S, *MB: CODE: ADL1 LOC: ON ST ANTHONY 242FT FROM CLAIBORNE S ****/ | 2018-03-28 | EXCAVATED 3 X 3 GUTTER BOTTOM THROUGH BRICK + LIMESTONE ALSO AN ADDITIONAL 3 X 3 MUD PLOT RELOCATED METER FROM GUTTER TO MUD PLOT METER IS UP TO GRADE AND OUTLET RENEWED TO PROPERTY BACKFILLED AND CLEANED THE AREA
201800603001 | 2018-03-16 | LEAD/PLASTIC | 4629 | ERICKSON AV | HUNTLEE DR | WILK | ML-METER LEAK ACCOUNT #227533-415442 METER #A342800 INLET SERVICE LEAK IN GRASS VEHICLES ROLLING OVER METER 05/10/18 CUST STATED LEAK HAS GOTTEN WORSE (KSW) /** 1) MN: A120644 SN: 0115563, *TAP: SIZE: A LOC: 400 FEET FROM P LINE AT HUNTLEE DR, *MB: CODE: CFL LOC: 400FT FROM P.L. HUNTLEE OPP FAUCET ****/ | 2018-05-25 | EXCAVATED ON THE OUTLET SERVICE THROUGHT TREE ROOTS AND RENEW THE SERVICE FROM PROPERTY AND THEN WE BACKFILL AND CLEAN UP JOB SITE
201800608302 | 2018-03-17 | LEAD/PLASTIC | 6005 | ST ANTHONY AV | BURBANK DR | WMRE | ACCT#101322044 METER#A301666 METER BELOW GRADE,RAISE - NEED MACHINE /** 1) MN: A254455 SN: 0096821, *TAP: SIZE: A LOC: 65 FEET FROM P LINE AT BURBANK DR, *MB: CODE: ADLM LOC: ON ST ANTHONY AVE 65FT FROM PL OF BURBANK DR 5FT ****/ /** 1) MN: A254455 SN: 0096821, *TAP: SIZE: A LOC: 65 FEET FROM P LINE AT BURBANK DR, *MB: CODE: ADLM LOC: ON ST ANTHONY AVE 65FT FROM PL OF BURBANK DR 5FT ****/ | 2018-05-26 | EXCUVATED AND RASIED 5/8 METER BOX TO GRADE ALSO REPLACED OUTLET SERVICE FROM METER TO PROPERTY TIED INTO COOPER.
201800621901 | 2018-03-18 | LEAD/PLASTIC | 919 | HOMER | PACIFIC AV | WILK | MI- METER BOX LEAK NO METER IN BOX NO ACTIVE ACCT INLET SERVICE LEAK CURB COCK IN OFF POSITION WATER PASSING THROUGH FLOODING GUTTER BOTTOM /** 1) MN: SN: 0063940, *TAP: SIZE: A LOC: 146 FEET FROM P LINE AT ELMIRA AVE, *MB: CODE: AD LOC: ON HOMER 144FT FROM ELMIRA 7FT OUTSIDE ****/ | 2018-04-04 | EXCAVATED METER BOX AND REPLACED BAD BOX COCK BACKFILLED WITH RIVER SAND
201800623701 | 2018-03-19 | LEAD | 131 | S RENDON |  | WILK | MI- LEAK BETWEEN S/WALK & CURB. INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A335945 SN: 0013382, *TAP: SIZE: B LOC: 111 FEET FROM P LINE AT CLEVELAND AVE., *MB: CODE: CFM4 LOC: ON SO. RENDON,111' L.S.P.L. CLEVELAND AVE. ****/ | 2018-03-29 | ARRIVED AT ABOVE LOCATION EXAMINED JOB WHERE I FOUND NO LEAK
201800624101 | 2018-03-19 | LEAD | 3304 | CANAL | S RENDON | WILK | MI- LEAK BETWEEN S/WALK & CURB. CHANGED FROM 113 S RENDON EXAMINE INLET SERVICE BETWEEN SIDEWALK AND CURB /** 1) MN: D004540 SN: 0055553, *TAP: SIZE: D LOC: 89 FEET FROM P LINE AT CANAL, *MB: CODE: OOO LOC: 89' FROM CANAL ST. 9'OUTSIDE PL 3' INSIDE CURB ****/ | 2018-03-29 | ARRIVED AT ABOVE LOCATION EXAMINED FOR LEAK + FOUND JOB NOT LEAKING SIGNS OF RECENT REPAIRS
201800627501 | 2018-03-19 | LEAD/PLASTIC | 3006 | WALL BL | MURL | WMTLK | ML METER LEAK METER # C026815 ACCOUNT # 231363-712151 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: A300517 SN: 0141890, *TAP: SIZE: A LOC: 29 FEET FROM P LINE AT MURL, *MB: CODE: CD LOC: ON WALL 29FT FROM DIV P/L MURL 8FT OUTSIDE 4FT ****/ | 2018-04-02 | EXAMINED JOB FOUND LEAK ON BOX COCK EXCAVATED BY HAND AND REPALCED BOX COCK
201800627701 | 2018-03-19 | LEAD | 208 | FAIRWAY DR | NATALIE LN | WILK | PP- POOR PRESSURE ACCT#156258-596311 METER#A380696 LEAK BEHIND METER BOX CUSTOMER HAVING VERY POOR PRESSURE PENCIL THIN DRIP /** 1) MN: A138892 SN: 0093212, *TAP: SIZE: A LOC: 194 FEET FROM P LINE AT NATALIE LANE, *MB: CODE: AFM2 LOC: ON FAIRWAY DR., 194' FROM P.L. NATALIE LANE,8' OUT ****/ | 2018-03-19 | EXCAVATED IN CONCRETE SIDEWALK REPAIR ON 1INCH LEADLINE DRESS UP WITH RIVERSAND & COLDMILL JOB REFERRED TO ZONE 1 TO TAKE LEADLINE FROM WATER MAIN TO METERBOX
201800629601 | 2018-03-19 | LEAD | 1226 | DAUPHINE | BARRACKS | WILK | MI- LEAK IN STREET INLET SERVICE LEAK IN ASPHALT STREET FLOODING STREET **CHANGED FROM 1200BLK DAUPHINE** /** 1) MN: A245144 SN: 0032011, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT BARRACKS, *MB: CODE: AE LOC: ON DAUPHINE ST 94' FROM URPL BARRACKS ST ****/ | 2018-03-28 | EXCAVATED IN ASPHALT STREET + MADE REPAIR ON 2 INCH INLET SERVICE LINE COMPACTED BACKFILLED + DRESSED UP AREA
201800630201 | 2018-03-19 | LEAD | 3928 | MARAIS | BARTHOLOMEW | WILK | ML METER LEAK ACCT# 148957-430407 METER# A371824 INLET SERVICE LEAK /** 1) MN: A283130 SN: 0081335, *TAP: SIZE: A LOC: 225 FEET FROM P LINE AT ALVAR, *MB: CODE: DL1 LOC: ON MARAIS,224' FROM P.L. ALVAR ****/ | 2018-04-03 | EXCAVATED 4 X 2 SIDEWALK CUT RENEWED OUTLET TO PROPERTY RELOCATED METER TO SIDEWALK BACKFILLED AND CLEAQNED THE AREA..REFER BACK TO ZONE 4 TO REMOVE LEAD FROM STREET
201800633601 | 2018-03-20 | LEAD | 1735 | N CLAIBORNE AV | ST ANTHONY | WILK | ML- METER LEAK METER STILL LEAKING CAUSING POOR PRESSURE MN:A410173 ACCT #113513-493668 INLET SERVICE LEAK IN BOX 03/20/18 CUSTOMER NOW OUT OF WATER PER SR#1283585 GIVE OUT ***J. GILLIAM @ 13:53PM*** /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-03-22 | REPLACE BOTH INLET AN DOUTLET WSHERS AT ABOVE LOCATION
201800633701 | 2018-03-20 | LEAD | 1634 | ST ANTHONY AV |  | WILK | *****************PICKUP********************* CRUSHED INLET ON ABANDON SERVICE IN FRONT VACANT LOT /** 1) MN: A239627 SN: 0040776, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BFL1 LOC: 45FT FROM PL N DERBIGNY 2' OUTSIDE PL ****/ | 2018-03-26 | EXCAVATED IN CONCRETE SIDEWALK + MADE REPAIR ON ABANDON INLET SERVICE LINE THAT WAS FLOODING AREA BACKFILLED + DRESSED UP AREA
201800640401 | 2018-03-21 | LEAD/PLASTIC | 601 | VALLETTE | EVELINA | WMTLK | METER # A372392 LOC#224357-401776 METER LEAKING /** 1) MN: A315149 SN: 0034999, *TAP: SIZE: A LOC: 68 FEET FROM P LINE AT VALLETTE, *MB: CODE: BFHK LOC: ON EVELINA 68' FROM USPL VALLETTE ****/ | 2018-04-02 | EXAMINED JOB FOUND DETEMINE LEAK COMING FROM WASHERS REPLACED WASHERS METER STOP LEAKING
201800640701 | 2018-03-21 | LEAD/PLASTIC | 2458 | MERCEDES BL | ANSON | WOLK | ML-METER LEAK ACCOUNT #233088-408966 METER #A296298 EXAMINE OUTLET SERVICE FOR LEAK @ PROPERTY CON REG WHEN METER IS TURNED ON, FOUND OFF LEFT OFF /** 1) MN: A296298 SN: 0159664, *TAP: SIZE: __ LOC: 0 FEET FROM P LINE AT MERCEDES BLVD, *MB: CODE: CDM2 LOC: ON MERCEDES 74FT FROM THE ANSON DIV PL 25' LPL ****/ | 2018-04-05 | EXCAVATED METER BOX AND OUTLET SIDE RAN NEW PLASTIC FROM METER BOX TO PROPERTY LEAK FOUND FUTHER BACK ON PROPERTY CUSTOMER WAS NOT HOME TO NOTIFY
201800642201 | 2018-03-21 | LEAD/PLASTIC | 1649 | JOSEPH | DANNEEL | WOLK | MI LEAK BETWEEN THE CURB AND THE STREET ON DANNEEL ST SIDE EXAMINE OUTLET SERVICE UP TO PROPERTY LINE FOR A LEAK /** 1) MN: A287059 SN: 0000000, *TAP: SIZE: A LOC: 43 FEET FROM P LINE AT JOSEPH, *MB: CODE: CD LOC: ON DANNEEL 43FT FROM DIV P/L JOSEPH 3' OUTSIDE 6FT ** 2) MN: D004214 SN: 0046291, *TAP: SIZE: DD LOC: 48 FEET FROM P LINE AT JOSEPH, *MB: CODE: CDH LOC: ON DANNEEL 47FT FROM PL JOSEPH SIDE ****/ DOTTIE READY 4-10-18 EXP 4-30-18 | 2018-04-16 | ARRIVED ON JOB EXCAVATED IN MUDPLOT FOUND LEAD OUTSIDE MANHOLE ON 1 1/2 LEAD SERVICE STOPPED LEAK BUT NEED TO RETURN TO REMOVE LEAD FROM WATER MAIN.
201800642301 | 2018-03-21 | LEAD | 1104 | 3RD |  | WOLK | LOCATION ID-107236 MTR-B027130 LEAK BETWEEN MTR AND STOP & WASTE/CONS REG ON MTR EXAMINE OUTLET SERVICE UP TO PROPERTY LINE FOR A LEAK /** 1) MN: B027130 SN: 0025979, *TAP: SIZE: B LOC: 52 FEET FROM P LINE AT 3RD, *MB: CODE: CDHM LOC: 51FT FROM USPL 3RD ****/ | 2018-03-22 | EXAMINE OUTLET TO PROPERTY, NO LEAKS , THE GROUNDS KEEPER WAS THERE I SHOWED HIM THE LINE. IF A LEAK IT IS ON PROPERTY. REFER TO ZONE 7 TO REMOVE LEAD OUTLET
201800642302 | 2018-03-22 | LEAD | 1104 | 3RD |  | WSNR | REFER TO REMOVE LEAD ON OUTLET /** 1) MN: B027130 SN: 0025979, *TAP: SIZE: B LOC: 52 FEET FROM P LINE AT 3RD, *MB: CODE: CDHM LOC: 51FT FROM USPL 3RD ****/ | 2018-03-23 | EXCAVATED IN MUDPLOT & TREE ROOTS TOOK LEAD LINE OUT RENEW 3/4 OUTLET SERVICE PLASTIC LINE & REPAIR 3/4 STOP & WASTE LEAD LINE ALSO RAISE TO RAISE GRADE DRESS UP WITH RIVERSAND JOB REF TO ZONE 3 TO TAKE LEAD LINE FROM WATER MAIN TO METER BOX
201800643101 | 2018-03-21 | LEAD | 1476 | N GALVEZ |  | WILK | WM LEAK ON THE SIDEWALK INLET SERVICE LEAK IN SIDEWALK FLOODING CURB/STREET /** 1) MN: B033214 SN: 0060053, *TAP: SIZE: B LOC: 86 FEET FROM P LINE AT GALVEZ N, *MB: CODE: BDH LOC: RES FRONT OF 2024 COLUMBUS 84FT FROM PL GALVEZ ****/ | 2018-04-04 | ARRIVED AT ABOVE LOCATION EXCAVATED IN MUD PLOT FOUND 3/4 INCH CURB COCK LEAKING + REPAIRED IT ON LEAD INLET
201800643401 | 2018-03-21 | LEAD | 1727 | MONTEGUT | N DERBIGNY | WILK | WM LEAK IN THE INTERSECTION INLET SERVICE LEAK ON SIDEWALK FLOODING CURB/STREET NEXT TO ADDRESS IN FRONT VACANT LOT **CHANGED FROM 1700BLK MONTEGUT** /** 1) MN: 000000 SN: 0102537, *TAP: SIZE: A LOC: 202 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: AEK LOC: 202' FROM P.L. NO.DERBIGNY METER NEAR PL.1729 L ****/ | 2018-04-09 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK THAT WAS FLOODING AREA BACKFILLED + DRESSED UP AREA
201800643701 | 2018-03-21 | LEAD | 2509 | ANNETTE | N DORGENOIS | WILK | WM LEAK BETWEEN STREET & SIDEWALK INLET SERVICE LEAK BETWEEN STREET/CURB FLOODING STREET /** 1) MN: A187649 SN: 0738427, *TAP: SIZE: B LOC: 78 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CDL LOC: ON ANNETTE, 78' FROM P.L. NO. DORGENOIS, 3' FROM ****/ | 2018-04-04 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE LINE BACKFILLED ND CLEANE DTHE AREA
201800643901 | 2018-03-22 | LEAD/PLASTIC | 480 | WALNUT | HURST | WOLK | WOLK WATER -LEAK OUTLET SERVICE /** 1) MN: B031533 SN: 0075574, *TAP: SIZE: B LOC: 117 FEET FROM P LINE AT HURST, *MB: CODE: ADL7 LOC: ON WALNUT 116.6FT FROM HURST ****/ | 2018-03-21 | ARRIVED ON JOB SITEE AND FOUSDD METER BOX OVERFLOWING PUMP WATER DOWN AND FOUND OUTLET LEAKING EXCAVTED IN MUDPLOT LEAKING EXCAVED IN MUDPLOT AND MADE REPAIR ON OUTLET TIED BACK ONTO LEAD BACKFILL JOB COMPLETE.
201800645701 | 2018-03-22 | LEAD/PLASTIC | 916 | CONSTANTINOPLE |  | WILK | OLD SERVICE HAS TO BE UPDATED CURB COCK OUTSIDE OF BOX A-271766 LOCATION #120146 PLEASE REPAIR AND CHANGE THE METER CHANGE OLD STYLE CURB COCK TO NEW STYLE CURB COCK /** 1) MN: A241763 SN: 0034968, *TAP: SIZE: A LOC: 147 FEET FROM P LINE AT MAGAZINE, *MB: CODE: BLN LOC: INSIDE PL 420 INSIDE - 147' P.L. MAGAZINE ****/ | 2018-07-08 | MADE A 3 X 5 CUT IN SIDEWALK .REPLACED OLDMETER BOX COCK REMOVED OLDMETER SET NEW METER ,RAISEE METER TO GRADE TIED BACK ONTO LEAD ON INLET SERVICE,OUTLET SERVICE IS PLASTIC. ********OLD METER INFO************ METER:A241763 FAC:32259040 MAKE:ROCKWELL READ:6628
201800647401 | 2018-03-22 | LEAD | 3014 | BRUXELLES | ABUNDANCE | WILK | MI - LEAK BETWEEN THE SIDEWALK AND CURB INLET SERVICE LEAK IN DRIVEWAY /** 1) MN: A271104 SN: 0065017, *TAP: SIZE: B LOC: 110 FEET FROM P LINE AT ABUNDANCE, *MB: CODE: OOO LOC: ON BRUXELLES, 112' FROM C.P.L. ABUNDANCE, 7' OUT- ** 2) MN: A332811 SN: 0065017, *TAP: SIZE: B LOC: 110 FEET FROM P LINE AT ABUNDANCE, *MB: CODE: OOO LOC: ON BRUXELLES, 111' FROM C.P.L. ABUNDANCE, 7' OUT- ****/ | 2018-04-06 | EXCAVATED IN CONCRETE SIDEWALK + DRIVEWAY + MADE REPAIR ON 3/4 INCH PLASTIC OUTLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201800648301 | 2018-03-22 | LEAD | 620 | LOUISA | CHARTRES | WMTLK | *********************PICKUP********************** EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-06-08 | EXCAVATED 8 X 2 SIDEWALK CUT RENEWED OUTLET TO PROPERTY ALSO REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILL AND CLEANED THE AREA *******REFER TO ZONE 4 TO HAVE FROM STREET REMOVED *******
201800648501 | 2018-03-22 | LEAD/PLASTIC | 2615 | ATHIS | FRANKLIN AV | WMTLK | LOCATIONID#184732-472422 METER#A413656 LEAK INSIDE METERBOX /** 1) MN: A309376 SN: 0138049, *TAP: SIZE: __ LOC: 110 FEET FROM P LINE AT FRANKLIN AVE., *MB: CODE: ADM1 LOC: ON ATHIS, 110' FROM P.L. FRANKLIN AVE., 8' OUTSIDE ****/ | 2018-03-29 | ARRIVED AT THE ABOVE LOCATION AND FOUND 5/8 METER BELOW GRADE. EXCAVATED IN MUD PLOT AND REMOVED TWO UPPER CASING FROM METER BOX AND PULLED METER OUT OF CONCRETE SIDEWALK FROM BETWEEN SIDEWALK AND MUD PLOT. ALSO FOUND PLASTIC ON INLET AND LED ON OUTLET. RAN PLASTIC FROM BOX TO PROPERTY AND RAISED METER TO GRADE. BACKFILLED WITH SAND AND COALMILL. WE ALSO REPLACED CHOCKED METER. *******OLD METER INFO************ METER:A413656 FAC:14119418 MAKE:HERSEY READ:1062
201800651401 | 2018-03-22 | LEAD/PLASTIC | 2629 | HYMAN PL |  | WILK | ML - METER LEAK METER NUMBER - A290226 ACCOUNT NUMBER - 229379-712477 INLET SERVICE LEAK /** 1) MN: A290226 SN: 0130471, *TAP: SIZE: A LOC: 233 FEET FROM P LINE AT ANSON, *MB: CODE: BDL LOC: ON HYMAN PL., 232' FROM P.L. ANSON, 7' OUTSIDE, 4' ****/ | 2018-04-10 | EXCAVATED METER BOX BY HAND ON EDGE OF TREE ROOTS FOUND LEAK ON INLET AND FOUND LEAD ON OUTLET REMOVED LEAD AND RAISED METER BOX TO GRADE RAN NEW PLASTIC FROM METER TO PROPERTY
201800655401 | 2018-03-23 | LEAD | 316 | JOSEPH | TCHOUPITOULAS | WOLK | MI-LEAK IN THE STREET **********L THOMPSON 10:25********** OUTLET SERVICE LEAK BEHIND METER BOX FLOODING GUTTER BOTTOM & MUD PLOT 2 HOUSES DOWN /** 1) MN: A301479 SN: 0083854, *TAP: SIZE: A LOC: 133 FEET FROM P LINE AT TCHOUPITOULAS, *MB: CODE: ADN5 LOC: RS DRIVE METER AT 316 AND 318 TIED TOGETHER ****/ DOTTIE READY5-17-18 EXP6-618 | 2018-05-22 | ARRIVED ON JOB SITE AND FOUND LEAKING AT CURB MADE A 6 X 6 CUT IN STREET EXCAVTED IN STREET CUTAND MADE REPAIRS FROM STREET TO INLET METER BOX TIED ONTO LEAD NEED TO BE REMOVE BACKFILL AND DRESSED CUT UP. SOC 6FT X 6 FT CONCRETE BASE.)
201800662101 | 2018-03-23 | LEAD/PLASTIC | 7717 | PATTERSON RD | HART | WILK | ML-METER LEAK ACCT#229117-410484 METER#A144894 INLET SERVICE LEAK IN MUDPLOT 05/15/18 LEAK HAS GOTTEN WORSE PER SR#12841186 (AJR) /** 1) MN: A144894 SN: 0169261, *TAP: SIZE: A LOC: 102 FEET FROM P LINE AT HART, *MB: CODE: AD LOC: ON PATTERSON 102' FROM PL HART 16' OUTSIDE PL ****/ | 2018-07-23 | EXAMINED AREA PUMP DOWN METER BOX OBSERVED LEAK ON INLET SERVICE EXCAVATED ON INLET AND OUTLET SERVICE REMOVED LEAD FOUND ON OUTLET SERVICE TO PROPERTY REPAIRED LEAK AND BACKFILLED AND CLEANED AREA
201800662301 | 2018-03-23 | LEAD/PLASTIC | 6712 | FOCH RD | PINES BL | WOLK | ML METER LEAK METER # B030949 ACCOUNT # 181091-451242 BROKEN 3/4 HANDWHEEL NEEDS REPLACING /** 1) MN: B023940 SN: 0128825, *TAP: SIZE: B LOC: 267 FEET FROM P LINE AT PINES BLVD, *MB: CODE: BDM3 LOC: RES ON FOCH 267FT PL PINES BL 8' OUTSIDE 3' IN- ****/ | 2018-03-29 | EXCAVATED IN 4X4 MUD PLOT BY HAND, FOUND LEAD ON INLET AND PLASTIC ON OUTLET WITH 3/4 CURB COCK AND 3/4 HAND WHEEL BROKEN. REPLACED 3/4 COCK AND HANDWHEEL WITH METER BOX COMPLETE. RAISED METER TO GRADE BACKFILLED AND DRESSED WITH RIVER. JOB COMPLETE.
201800662601 | 2018-03-23 | LEAD | 915 | JOURDAN RD | BURGUNDY | WMTLK | ML---METER LEAK METER # C033877 ACCT #186276-424655 EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-03-07 | EXACAVTED IN MUD PLOT AND MADE REPAIRS ON 1 INCH CURB COCK IN METER BOX BACKFILLED AREA
201800667401 | 2018-03-25 | LEAD/PLASTIC | 309 | RIVER OAKS DR | COPERNICUS | WILK | ML- METER LEAK ACCT# 227839-416088 MTR# A120527 INLET SERVICE LEAKING FROM CURB COCK, FLOODING GRASS AND GUTTER /** 1) MN: A120527 SN: 0117782, *TAP: SIZE: B LOC: 251 FEET FROM P LINE AT COPERNICUS, *MB: CODE: CDL LOC: ON RIVER OAKS DR., 251' FROM P.L. COPERNICUS, 7' ****/ | 2018-03-29 | EXCAVATED METER BOX AND CHANGED BOX COCK BACKFILLED WITH RIVER SAND
201800667701 | 2018-03-25 | LEAD/PLASTIC | 3231 | LOWERLINE |  | WILK | WATER LEAK ON INLET FLOODING THE AREA /** 1) MN: A335537 SN: 0078072, *TAP: SIZE: A LOC: 80 FEET FROM P LINE AT FORSHEY, *MB: CODE: CD LOC: 79FT FROM PL FORSHEY 7' OUTSIDE PL 4' INSIDE CURB ****/ | 2018-03-26 | EXCAVATED AND MADE REPAIRS ON A 5/8" IN LET ERVICE LEAK ALSO RAISED THE METER TO GRADE AND RENEW THE OUTLET LEAD ON THE INLET PLASTIC ON THE OUTLET
201800667801 | 2018-03-25 | LEAD/PLASTIC | 24 | VIVIAN CT | HUNTLEE DR | WMTLK | ML METER LEAK METER A195101 ACCT 227100-415995 EXAMINE INLET/OUTLET SERVICE FOR A LEAK. AREA FLOODED (C) /** 1) MN: A195101 SN: 0123308, *TAP: SIZE: A LOC: 525 FEET FROM P LINE AT HUNTLEE DR, *MB: CODE: BFL LOC: ON VIVIAN CT.,523' FROM P.L. HUNTLEE DR., 4' OUT- ****/ | 2018-04-02 | ARRIVED ON JOBSITE EXAMINED METER FOUND LEAK ON INLET EXCAVATED BY HAND AND REPAIRED
201800668401 | 2018-03-26 | LEAD/PLASTIC | 6218 | CAMBRIDGE CT | AURORA DR | WMTLK | LOCATION#230457-413171.METER#A423352. A LEAK WAS FOUND INSIDE OF THE METER BOX. WAS UNABLE TO DETERMINE WHERE THE LEAK WAS COMING FROM /** 1) MN: A312181 SN: 0136799, *TAP: SIZE: B LOC: 180 FEET FROM P LINE AT AURORA DR, *MB: CODE: BDK1 LOC: ON CAMBRIDGE 179FT FROM AURORA 7FT OUTSIDE ****/ | 2018-04-04 | EXCAVATWED METER BOX AND NO LEAK WAS FOUND
201800669801 | 2018-03-26 | LEAD | 1129 | N WHITE | BELL | WILK | ML- METER LEAK ACCT# 146991-522233 MTR# A154766 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A154766 SN: 0007994, *TAP: SIZE: A LOC: 236 FEET FROM P LINE AT ORCHID, *MB: CODE: BDN2 LOC: ON N WHITE 236FT FROM PL ORCHID ****/ | 2018-04-04 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH HANDWHEEL LEAKING REPAIRED + RENEWED OUTLET TO PROPERTY BACKFILLED
201800670601 | 2018-03-26 | LEAD | 5529 | LOYOLA AV | JOSEPH | WILK | ML- METER LEAK METER # A194029 ACCT # 109816-568763 INLET SERVICE LEAK BEHIND CURB COCK IN GRASS INFRONT METER, NO METER IN BOX /** 1) MN: A194029 SN: 0010975, *TAP: SIZE: B LOC: 37 FEET FROM P LINE AT JOSEPH, *MB: CODE: CFLM LOC: 43' P.L. JOSEPH ****/ | 2018-07-05 | EXCVATED OVER INLET SERVICE IN MUDPLOT .REPLACE 5/8 CURB COCK TIED BACK INTO LEAD .NEED TO BE REMOVED FROM METER BOX TO WATER MAIN.NO METER INSIDE BOX. JOB REFERRED
201800670701 | 2018-03-26 | LEAD | 2137 | TOURO |  | WILK | MI LEAK IN THE STREET EXAMINE INLET SERVICE ON ABANDON SERVICE IN THE STREET NEXT TO ADDRESS /** 1) MN: A281055 SN: 0060146, *TAP: SIZE: B LOC: 59 FEET FROM P LINE AT TOURO, *MB: CODE: CFH LOC: ON N MIRO 59FT FROM PL TOURO ****/ | 2018-04-17 | EXCAVATED INASPHALT STREET IN WET SPOT IN STREET + FOUND NOLEAK WET SPOT WAS ARIN WATER COMPACTED BACKFILLED+ DRESSED UP AREA
201800672801 | 2018-03-26 | LEAD | 1432-34 | N DORGENOIS | KERLEREC | WILK | MI- LEAK BETWEEN S/WALK & STREET INLET SERVICE LEAK IN TREE ROOTS /** AT 1432: 1) MN: A302815 SN: 0054813, *TAP: SIZE: A LOC: 43 FEET FROM P LINE AT KERLEREC, *MB: CODE: ADM LOC: ON D. DORGENOIS 35FT FROM PL KERLEREC 8FT OUTSIDE ** AT 1434: 2) MN: A145796 SN: 0054813, *TAP: SIZE: A LOC: 55 FEET FROM P LINE AT KERLEREC, *MB: CODE: ADM LOC: 54FT FROM LRPL KERLEREC FRONT AT 1434 ****/ | 2018-04-06 | REPLACED 5/8 INCH HANDWHEL + GUTS IN METER BOX
201800673101 | 2018-03-26 | LEAD | 2228 | N PRIEUR | MARIGNY | WILK | ML- METER LEAK METER # A315005 ACCT # 144272-483522 *******FLOODED AREA**** EXAMINE INLET SERVICE FOR A LEAK METR UNDER WATER /** 1) MN: A315005 SN: 0068414, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT MARIGNY, *MB: CODE: AD LOC: ON N PRIEUR ST 73' FROM PL MARIGNY ****/ | 2018-03-27 | REPLCAED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201800673701 | 2018-03-26 | LEAD/PLASTIC | 319 | OLIVIER | PELICAN | WMBK | TREE STUMP IN METER BOX CASING UNABLE TO CHANGE METER B-31131 PLEASE REPAIR AND CHANGE METER LOCATION #223827 REPLACE BROKEN METER BOX & REMOVE TREE ROOTS TO REPLACE METER /** 1) MN: B031131 SN: 0039150, *TAP: SIZE: B LOC: 150 FEET FROM P LINE AT PELICAN AVE, *MB: CODE: ADHL LOC: ON OLIVIER, 3' FROM U.P.L. PELICAN AVE. ****/ | 2018-06-27 | CHOPPED THRU TREE ROOTS AND RELOCATED METER BOX TO A LOCATION AROUND THE TREE WITH LESS TREE ROOTS
201800674201 | 2018-03-26 | LEAD/PLASTIC | 273 | ELMIRA AV | PELICAN | WILK | ML- METER LEAK ACCT # 224978-713988 METER # A351962 INLET SERVICE LEAK IN THE MUD PLOT FLOODING CURB /** 1) MN: A248571 SN: 0060297, *TAP: SIZE: A LOC: 43 FEET FROM P LINE AT PELICAN AVE, *MB: CODE: CDL LOC: ON ELIMRA AVE, 43' FROM PL PELICAN AVE ****/ | 2018-05-21 | EXCAVATED METER BOX AND FOUND BAD CURB COCK REPLACED CURB COCK AND BACKFILLED WITH RIVER SAND
201800674301 | 2018-03-26 | LEAD/PLASTIC | 418 | HOMER | TECHE | WILK | ML- METER LEAK METER#A359335 ACCT#224653-401133 INLET SERVICE LEAK IN THE MUD PLOT 04/17/18 LEAK IS NOW PREVENTING CUSTOMER TO EXITING AND ENTERING HOME PER SR#12838359 (AJR) /** 1) MN: A235620 SN: 0053106, *TAP: SIZE: A LOC: 160 FEET FROM P LINE AT TECHE, *MB: CODE: BDKL LOC: ON HOMER 159FT FROM L.R.P.L. TECHE RES ****/ | 2018-04-26 | EXCAVATED AND REPAIRED INLET SERVICE LEAK ALSO REPLACED LEAD OUTLET SERVICE WITH PLASTIC TUBING AND RASIED METER BOX TO GRADE. THERE IS STILL SOME LET ON INLET SIDE 2 X3 MUD CUT BACKFILLED NO DRESS UP NEEDED 3X5 MUD CUT BACKFILLED NO DRESS UP NEEDED
201800674901 | 2018-03-26 | LEAD | 908 | URSULINES AV | ROYAL | WILK | ML- METER LEAK ACCT# 115983-529433 MTR# A195037 INLET SERVICE LEAK /** 1) MN: A195037 SN: 0020743, *TAP: SIZE: A LOC: 59 FEET FROM P LINE AT DAUPHINE, *MB: CODE: AE LOC: AT 908 INSIDE 59' P.L. DAUPHINE ****/ | 2018-06-19 | EXAMINED JOB AT ABOVE LOCATION FOUND NO LEAKS UNABLE TO RENEW OUTLET TO CLOSE TO FOUNDATION WALL
201800677901 | 2018-03-27 | LEAD | 1128 | N WHITE |  | WILK | CURB COCK IS LEAKING. PLEASE REPAIR METER A369802 LOC ID 149574 INLET SERVICE LEAKK INSIDE METER BOX /** 1) MN: A311495 SN: 0082206, *TAP: SIZE: A LOC: 230 FEET FROM P LINE AT ORCHID, *MB: CODE: ADL7 LOC: ON N WHITE ST 230' FROM PL ORCHID ****/ | 2018-04-04 | ARRIVED AT ABOVE LOCATION EXCAVATED IN MUD PLOT FOUND 5/8 INCH CURB COCK LEAKING ON LEAD LINE + REPAIRED IT BACKFILLED
201800678401 | 2018-03-27 | LEAD | 811 | GOV NICHOLLS |  | WILK | **********PICK UP********** BAD BLEEDER VALVE NO CONSTANT REGISTRATION ON METER /** 1) MN: A314518 SN: 0014694, *TAP: SIZE: A LOC: 88 FEET FROM P LINE AT BOURBON, *MB: CODE: BE5 LOC: RES 88' P.L. BOURBON ****/ | 2018-05-31 | EXCAVATED 4 X 2 SIDEWALK CUT RENEWED OUTLET TO PROPERTY BACKFILLED AND CLEANED THE AREA
201800679401 | 2018-03-27 | LEAD/PLASTIC | 1730 | TITA |  | WILK | ML METER LEAK ACCOUNT #226151-406726 METER #A278588 INLET SERVICE LEAK IN THE MUD PLOT WITH PREVIOUS SIGNS OF REPAIRS /** 1) MN: A295699 SN: 0122566, *TAP: SIZE: B LOC: 246 FEET FROM P LINE AT BRINGIER, *MB: CODE: BDK3 LOC: OLN TITA 245' FROM PL BRINGIER 8' OUTSIDE PL 9' IN ****/ | 2018-03-27 | EXCAVATED METER OBSERVED LEAK ON INLET AT A TEE WITH ABANDONED METER BOX REPAIRED LEAK SAND NEEDED FOR DRESS UP
201800680501 | 2018-03-27 | LEAD | 229 | DAUPHINE | BIENVILLE | WMRE | LOCATION ID# 104797 MTR# C33449 PLEASE LOCATE AND RAISE METER TO GRADE LOCATE WATER METER & RAISE & MARK METER /** 1) MN: C016388 SN: 0176703, *TAP: SIZE: B LOC: 74 FEET FROM P LINE AT BIENVILLE, *MB: CODE: BF LOC: 73FT FROM USPL BIENVILLE ****/ | 2018-04-09 | ARRIVED AT ABOVE LOCATION LOCATED METER IN SIDEWLK ALREADY RAISED TO GRADE + MARKED IT
201800681201 | 2018-03-27 | LEAD | 1027 | CANAL | N RAMPART | WMRE | LOCATION ID# 207723 MTR# B40398 PLEASE LOCATE AND RAISE METER TO GRADE LOCATER WATER METER & RAISE & MARK METER /** 1) MN: B028877 SN: 0056859, *TAP: SIZE: B LOC: 107 FEET FROM P LINE AT NO. RAMPART, *MB: CODE: OOO LOC: ON CANAL, 107' FROM P.L. NO. RAMPART, 4' OUTSIDE, ****/ | 2018-04-09 | ARRIVED AT ABOVE LOCATION LOCATED METER IN SIDEWALK ALREADY TO GRADE + MARKED IT
201800682001 | 2018-03-27 | LEAD | 3015 | METROPOLITAN | LOUISA | WILK | ML METER LEAK ACCT# 160016-434428 METER# A413205 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A303757 SN: 0098019, *TAP: SIZE: B LOC: 61 FEET FROM P LINE AT ABUNDANCE, *MB: CODE: OOO LOC: ON METROPOLITAN, 85' FROM P.L. ABUNDANCE,2'OUTSIDE ****/ | 2018-03-29 | EXCAVATED IN 4X4 MUD PLOT BY HAND. FOUND LEAD ON INLET AND PLASTIC ON OUTLET WITH 5/8 CURB COCK LEAKING. REPLACED 5/8 CURB COCK RAISED METER TO GRADE BACKFILLED AND DRESSED WITH RIVER SAND. JOB COMPLETE.
201800684101 | 2018-03-28 | LEAD | 4711 | ROBIN HOOD DR | PRENTISS AV | WILK | ML- METER LEAK ACCT# 180677-436823 MTR# C028081 INET SERVICE LEAK IN MUDPLOT /** 1) MN: C026021 SN: 0159625, *TAP: SIZE: B LOC: 88 FEET FROM P LINE AT PRENTISS AVE, *MB: CODE: CDL1 LOC: ON ROBIN HOOD 88FT FROM PRENTISS 8FT OUTSIDE ****/ | 2018-03-29 | EXCAVATED IN 4X4 NUD PLOT BY HAND, FOUND LEAD ON INLET AND PLASTIC ON OUTLET WITH A 1'' CURB COCK LEAKING. REPLACED 1'' CURB COCK RAISED METER BOX TO GRADE BACKFILLED WITH RIVER SAND. JOB COMPLETE.
201800685001 | 2018-03-28 | LEAD | 5716 | VERMILLION BL | PRENTISS AV | WOLK | ML - METER LEAK MTR# A431303 ACCT # 303999-716918 BROKEN 5/8 HANDWHEEL AND METER BOX BOTTOM, RESET METER BOX CASING AND METER, NEW CONSTRUCTION /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-04-06 | EXCAVATED IN MUDPLOT, REPAIR INLET & OUTLET SERVICE LINES ALSO RAISE TO GRADE & RESET 5/8 METER A405910 DRESS UP WITH RIVERSAND JOB REFERRED TO ZONE 1 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX *************OLD METER INFO****************** METER:A431303 FAC:16356892 MAKE:HERSEY READ:0
201800685002 | 2018-04-06 | LEAD | 5716 | VERMILLION BL | PRENTISS AV | WSNR | JOB REFERRED TO ZONE 1 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-06-04 | EXCAVATED ON 8 X 6 ASPHALT CUT TO PREP FOR RENEWING OF INLET SERVICE FROM WATERMAIN TO P.L. BARRICADED JOBSITE JOB CONTINUED
201800685801 | 2018-03-28 | LEAD | 5713 | N CLAIBORNE AV | LAMANCHE | WILK | ML-METER LEAK ACCT#167142-423751 METER#A382737 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: B028275 SN: 0170409, *TAP: SIZE: A LOC: 107 FEET FROM P LINE AT LAMANCHE, *MB: CODE: BFL LOC: ON NO. CLAIBORNE AVE., 105' FROM P.L. LAMANCHE,2' ****/ | 2018-04-10 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING ON LEAD LINE + REPAIRED BACKFILLED
201800686801 | 2018-03-28 | LEAD | 1004 | N LOPEZ | ST PHILIP | WILK | ML - METER LEAK ACCT#110752-521399 METER#A284179 INLET SERVICE LEAK IN OLD CUT ON THE SIDEWALK /** 1) MN: A284179 SN: 0015687, *TAP: SIZE: B LOC: 29 FEET FROM P LINE AT ST PHILIP, *MB: CODE: AF LOC: 29' P.L. ST PHILIP ****/ | 2018-04-11 | ARRIVED AT ABOVE LOCATION EXCAVATED IN GUTTER BOTTOM FOUND 3/4 INCH LEAD LINE LEAKING + REPAIRED
201800687101 | 2018-03-28 | LEAD/PLASTIC | 1733 | KABEL DR | ANSON | WILK | ML-METER LEAK ACCT # 228694-717513 METER # B029190 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: B029190 SN: 0129559, *TAP: SIZE: B LOC: 261 FEET FROM P LINE AT ANSON, *MB: CODE: CE LOC: ON KABEL DR., 261' FROM P.L. ANSON, 7' OUTSIDE, 3' ****/ | 2018-04-06 | EXCAVATED ON THE INLET SERVICE AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOBSITE
201800687501 | 2018-03-28 | LEAD | 2329 | ADAMS | S CLAIBORNE AV | WOLK | WM LEAK IN THE SIDEWALK OUTLET SERVICE LEAK IN GRASS NEAR SIDEWALK FLOODING GRASSY AREA /** 1) MN: A329800 SN: 0060536, *TAP: SIZE: B LOC: 22 FEET FROM P LINE AT CLAIBORNE AVE S, *MB: CODE: CDM1 LOC: ON ADAMS,23' FROM R.P.L. SO. CLAIBORNE AVE. ****/ | 2018-04-10 | EXCAVATED IN MUD PLOT TO FIX OUTLET LEAK ON LEAD. CAN NOT REMOVE LEADOUT OF TREE ROOT NEED MACHINE. JEG
201800690301 | 2018-03-28 | LEAD | 633 | ELMIRA AV | OPELOUSAS AV | WMTLK | WM-LEAK IN SIDEWALK EXAMINE INLET/OUTLET SERVICE FOR LEAK SIDEWALK FLOODED LEFT ONE (1) CONE FOR SAFETY /** 1) MN: A236210 SN: 0054454, *TAP: SIZE: A LOC: 43 FEET FROM P LINE AT OPELOUSAS AVE, *MB: CODE: CEL1 LOC: ON ELMIRA 43FT FROM OPELOUSAS ****/ | 2018-04-11 | EXCAVATED IN CONCRETE SIDEWALK REPAIR 5/8 STOP & WASTE LEAD LINE. DRESS UP WITH RIVERSAND & COLDMILL JOB REFERRED TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER.
201800690401 | 2018-03-28 | LEAD | 314 | HARNEY | COLBERT | WILK | C-Y NO WATER METER #A426870 ACCT #149534-701285 *******J CLARK @ 20:07PM******* INLET SERVICE LEAK IN MUDPLOT *****CUSTOMER OUT OF WATER******* /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-03-28 | ARRIVED AT ABOVE LOCATION EXCAVATED IN MUD PLOT WAS NOT ABLE TO COMPLETE JOB SPOKE TO CUSTOMER TO RESTORE WATER IN THE MORNING. REFER TO ZONE 1 FOR FIRST AM ON 1AND HALF INCH CONTROLLIG LINE.
201800690402 | 2018-03-29 | LEAD | 314 | HARNEY | COLBERT | WILK | REFER TO ZONE 1 TO GIVE CUSTOMER WATER FIRST AM. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-03-29 | EXCAVATED IN MUDPLOT TO REPAIR LEAKING 1.25 LEAD CONTROLLER LINE CUSTOMER NOW HAS WATER. BACKFILLED JOB SITE FORCE ACCOUNT TO BANCROFT PROPERTY INVESTMENTS CONTRACTORS PUNCTURED HOLE THRU 1.25 CONTROLLER LINE. JEG
201800693701 | 2018-03-29 | LEAD/PLASTIC | 2711 | BRISTOL PL | HERSCHEL | WILK | MI: LEAK IN STREET ACCT # 228576-416633 METER# B018912 INLET SERVICE LEAK IN CONCRETE STREET *****PREVIOUS SIGNS OF REPAIRS JOB STILL LEAKING***** /** 1) MN: B024326 SN: 0122445, *TAP: SIZE: B LOC: 221 FEET FROM P LINE AT HERSCHEL, *MB: CODE: CDM3 LOC: ON BRISTOL PL., 221' FROM P.L. HERSCHEL, 9' OUT- ****/ | 2018-04-19 | EXCAVATED AND REPAIRED INLET SERVICE LEAK IN METER BOX ALSO REPLACED LEAD OUTLET SERVICE WITH PLASTIC WATER LINE AND RAISED METER BOX TO GRADE 2'X4'MUD CUT -BACKFILLED -NO DRESS UP NEEDED 3'X5'MUD CUT- BACKFILLED - NO DRESS NEEDED
201800694101 | 2018-03-29 | LEAD/PLASTIC | 3062 | BOYD | IVORY | WMTLK | ML- METER LEAK ACCT#227717-419859 METER#A304944 EXAMINE INLET & OUTLET SERVICE FOR A LEAK ON THE SIDEWALK /** 1) MN: A304944 SN: 0148106, *TAP: SIZE: A LOC: 287 FEET FROM P LINE AT IVORY, *MB: CODE: AEK LOC: ON UPPER COMMON RD., 287' FROM P.L. IVORY, 3' OUT- ****/ | 2018-04-06 | EXAMINED JOB DETERMINED THAT THE BOX COCK NEEDED TO BE REPLACED USED JACK HAMMER TO BREAK CONCRETE AND EXCAVATE TO METER BOX REPLACED BOX COCK AND CHANGED WASHER
201800694501 | 2018-03-29 | LEAD/PLASTIC | 1423 | PTOLEMY | WHITNEY AV | WILK | MI-LEAK AT THE SIDEWALK INLET SERVICE LEAK NEAR SIDEWALK FLOODING AREA 04/04/18 CUSTOMER STATES LEAK GETTING WORSE (NLD) /** 1) MN: A317745 SN: 0091067, *TAP: SIZE: A LOC: 120 FEET FROM P LINE AT WHITNEY AVE, *MB: CODE: BD LOC: ON PTOLEMY 120FT FROM WHITNEY 7FT OUTSIDE ****/ | 2018-04-06 | ARRIVED ON JOBSITE EXAMINED METER EXCAVATED BY HAND FOUND LEAK ON OUTLET AND REPAIRED
201800696601 | 2018-04-02 | LEAD | 528 | CAFFIN AV |  | WILK | LOCATION: 119077 MTR# A 419271 BAD BLEEDER VALVE LEAK. PLEASE REPAIR. BAD BLEEDER VALVE IN BOX /** 1) MN: A274200 SN: 0030343, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT CHARTRES, *MB: CODE: CF LOC: ON CAFFIN 49FT FROM URPL CHARTRES ****/ | 2018-06-04 | EXCAVATED 2 X 2 SIDEW3ALKCUT REPLACED 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA LEFT SAFETY CONES ON TOP CONCRETE REFER BACK TO ZONE 4 TO REMOVE LEAD FROM STREET
201800697201 | 2018-04-02 | LEAD | 1735 | N TONTI |  | WILK | ML--- METER LEAK ACCT # 127610-488146 METER # A395019 INLET SERVICE LEAK IN MUDPLOT NEAR METER /** 1) MN: A321676 SN: 0067659, *TAP: SIZE: A LOC: 57 FEET FROM P LINE AT AUBRY, *MB: CODE: ADKN LOC: ON N TONTI 57.6FT FROM PL OF AUBRY ****/ | 2018-04-18 | EXCAVATED 3 X 3 MUD PLOT FOUND LEAK ON INLET REPAIRED THE INLET REPAIRED THE INLET LEAK BACKFILLED AND CLEAN THE AREA
201800699801 | 2018-04-02 | LEAD | 1509 | N CLAIBORNE AV |  | WMTLK | ML-METER LEAK ACCT#112778-487511 METER#A409733 **CALL TAKEN BY TJOHN ON 3/31/18 @10:22A.M. ENTERGY POWER OUTAGE*** EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A262710 SN: 0015382, *TAP: SIZE: A LOC: 67 FEET FROM P LINE AT COLUMBUS, *MB: CODE: CEFK LOC: ON CLAIBORNE AVE 67FT FROM COLUMBUS ****/ | 2018-04-17 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201800704201 | 2018-04-02 | LEAD | 1257 | KERLEREC |  | WMTLK | MI- LEAK IN THE STREET ************TAKEN BY SHOSKINS AT 12:50PM ON 4/2/18******* EXAMINE INLET & OUTLET FOR LEAK. METER LOCATED N LARGE TREE ROOTS. METER UNDER WATER. (C) /** 1) MN: A181014 SN: 0043167, *TAP: SIZE: A LOC: 44 FEET FROM P LINE AT KERLEREC, *MB: CODE: AFHL LOC: 1ST METER SIDE ST ONMARAIS 44' P.L. KERLEREC ****/ | 2018-05-02 | EXCAVATED 3 X 2 BRICK SIDEWALK REPLACED 5/8 INCH METER COCK BACKFILLED AND CLEANED THE AREA
201800704501 | 2018-04-02 | LEAD | 1663 | N CLAIBORNE AV | ANNETTE | WMTLK | ML- METER LEAK ACCT# 120328-506195 MTR# A177248 *************** TAKEN BY CTHOMAS AT 3:28PM ON 4/2/18 ********ENTERGY POWER OUTAGE EXAMINE INLET/OUTLET SERVICE FOR LEAK INSIDE METER BOX ON SIDEWALK /** 1) MN: A177248 SN: 0039351, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT ALLEN, *MB: CODE: CFK LOC: ON N. CLAIBORNE AVE 110' FROM LSPL ALLEN ST ****/ | 2018-04-13 | ARRIVED AT ABOVE LOCATION EXAMINED WATER METER FOR LEAK + FOUND NO LEAK SIGN OF RECENT REPAIRS
201800707201 | 2018-04-03 | LEAD | N/A | ROSIERE | O"REILLY | WMLK | MI LEAK BETWEEN SIDEWALK AND STREET CHANGED FROM 1804 GENTILLY BL AND ROSIERE LEAK ON THE MAIN NEAR CURB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-04-13 | MADE 6 X 6 CUT IN BLACK TOP STREET AND MADE REPAIRS ON 4 INCH VALVE TO STOP LEAK BACKFILLED AREA
201800707901 | 2018-04-03 | LEAD/PLASTIC | 2938 | AMERICUS | MURL | WILK | HY-HYDRANT LEAK INET SERVICE LEAK IN MUDPLOT FLOODINR CURB, CARS ROLLING OVER METER ***NO HYDRANT LEAK /** 1) MN: A321976 SN: 0141523, *TAP: SIZE: B LOC: 10 FEET FROM P LINE AT MURL, *MB: CODE: OOOO LOC: ON AMERICUS, 9' FROM D.P.L. MURL, 9' OUTSIDE, 3' ****/ | 2018-04-13 | EXCAVATED METER BOX AND FOUND LEAK ON INLET SERVICE REPLACED LEAKING FITTING WITH NEW ONE LEAD ON INLET NEED TO BE REMOVED
201800710401 | 2018-04-03 | LEAD/PLASTIC | 2240 | CONSTANCE | CONSTANCE | WILK | ML- METER LEAK METER#A304752 ACCT#110749-542413 INLET SERVICE LEAK /** 1) MN: A304752 SN: 0011902, *TAP: SIZE: B LOC: 101 FEET FROM P LINE AT CONSTANCE, *MB: CODE: BE LOC: 1ST METER SIDE/PHILIP 100 FT FROM PL CONSTANCE ****/ | 2018-05-23 | EXAMINED AREA BROKE OUT CONCRETE EXCAVATED METER OBSERVED LEAK ON INLET SERVICE MADE REPAIRS AND RAISED TO GRADE BACKFILLED AND CLEANED AREA
201800711401 | 2018-04-03 | LEAD/PLASTIC | 4465 | ROSEMONT PL | RANSOM | WILK | ML: METERLEAK METER# A389455 ACCT# 182820-443325 PLEASE REPAIR ASAP INLET SERVICE LEAK OVERFLOWING FROM METER BOX /** 1) MN: A290027 SN: 0133155, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT RANSOM, *MB: CODE: CDM5 LOC: RES ON ROSEMONT 150FT PL RANSOM 8' OUTSIDE 2' ****/ | 2018-04-13 | EXCAVATED IN 4X4 MUDPLOT OVER GAS LINE MY HAND FOUND PLASTIC ON INLET AND LEAD ON OUTLET WITH A 5/8 CURB COCK LEAKING AND 5/8 HANDWHEEL BROKEN REPLACE 5/8 CURB COCK AND 5/8 HANDWHEEL WITH METER BOX COMPLETE TOOK LEAD OUT AND RAN 5FT OF WATER TUBING TO PROPERTY RAISE METER TO GRADE BACKFILL JOB COMPLETE
201800719101 | 2018-04-04 | LEAD/PLASTIC | 1401 | NUNEZ |  | WILK | ML METER LEAK ACCOUNT #301254-715944 METER #A425114 INLET SERVICE LEAK /** 1) MN: SN: 0048250, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT NUNEZ, *MB: CODE: BD LOC: ON SOCRATES, 74.5' FROM U.S.P.L. NUNEZ ****/ | 2018-05-21 | EXCAVATED METER BOX AND TUNNELED UNDER SIDE WALK TO AVOID BREAKING NEW SIDEWALK TO CHANGE CURB COCK BACKFILLED WITH RIVER SAND
201800719701 | 2018-04-04 | LEAD/PLASTIC | 2520 | MAGAZINE |  | WMRE | LOCATION ID-107451 MTR-A302949 MTR BURIED BY NEW LAWN/PLEASE LOCATE LOCATE WATER SERVICE AND MARK /** 1) MN: A302949 SN: 0003680, *TAP: SIZE: A LOC: 71 FEET FROM P LINE AT THIRD, *MB: CODE: BDL3 LOC: 71FT FROM LRPL THIRD ON MAGAZINE ****/ DOTTIE 9-14-18 EXP 10-4-18 | 2018-10-06 | LOCATED 5/8 METER ALSO REPLACED 5/8 CURB COCK TIED INTO LEAD.
201800719901 | 2018-04-04 | LEAD | 1428 | CLOUET | N VILLERE | WMTLK | ML- METER LEAK METER#A154278 ACCT#138675-429370 EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: SN: 0069358, *TAP: SIZE: A LOC: 269 FEET FROM P LINE AT VILLERE N, *MB: CODE: CDBM LOC: ON CLOUET 269' FROM PL OF VILLERE N ****/ | 2018-04-12 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING ON LEAD LINE +REPLACED IT IN GUTTER BOTTOM REPLACVED BROKEN METER BOX CASING BACKFILLED
201800722001 | 2018-04-05 | LEAD | 3316-18 | N RAMPART | DESIRE | WILK | MI- LEAK IN STREET EXAMINE INLET SERVICE FOR LEAK /** AT 3316: 1) MN: A229213 SN: 0056116, *TAP: SIZE: A LOC: 139 FEET FROM P LINE AT PIETY, *MB: CODE: CEM3 LOC: 139FT FROM LRPL PIETY ****/ | 2018-04-16 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201800722201 | 2018-04-05 | LEAD | 2002 | PIETY |  | WMBC | LOCATION: 136048 MTR# A 419345 BROKEN METER BOX CASING, PLEASE REPAIR. REPAIR BROKEN METER BOX CASING /** 1) MN: A316532 SN: 0084564, *TAP: SIZE: A LOC: 59 FEET FROM P LINE AT JOHNSON N, *MB: CODE: BE4 LOC: ON PIETY ST 59' FROM USPL N JOHNSON ****/ | 2018-04-17 | ARRIVED AT ABOVE LOCATION FOUND METER CASING MISSING + REPLACED IT WITH NEW ONE IN MUD PLOT AT PROPERTY
201800722501 | 2018-04-05 | LEAD | 1648 | GENTILLY BL | ONZAGA | WILK | MI- LEAK AT THE SIDEWALK ON ONZAGA EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A308792 SN: 0031513, *TAP: SIZE: A LOC: 59 FEET FROM P LINE AT GENTILLY RD, *MB: CODE: BFHN LOC: SIDE ST/ONZAGA 59 FT FROM PL GENTILLY RD 2 FT FROM ****/ | 2018-04-17 | EXCAVATED I MUD PLOT AND REPLACED CURB COCK AND RENEWED OUTLET AT GATE 3/4 INCH LEAD CONTINING INSIDE YARD BACKFILLED AREA
201800722601 | 2018-04-05 | LEAD | 539 | CAFFIN AV |  | WILK | LOCATION: 114582 MTR# A 419302 INLET SERVICE LEAKING BEHIND CURB COCK, PLEASE REPAIR INLET SERVICE LEAK IN BOX /** 1) MN: A345852 SN: 0055128, *TAP: SIZE: A LOC: 106 FEET FROM P LINE AT CAFFIN AVE, *MB: CODE: AF LOC: ON CHARTRES 105' FROM PL CAFFIN BY SHED INSIDE ****/ | 2018-06-18 | EXCAVATED 2 X 2 SIDEWALK MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA REFER BACK TO ZONE 4 TO HAVE LEAD REMOVED FROM STREET
201800724401 | 2018-04-05 | LEAD/PLASTIC | 5611 | CHARLOTTE DR |  | WILK | LOCATION ID-177947 MTR-C032726 MTR LEAK/BOX FILL BACK UP WHEN PUMP OUT INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: C014147 SN: 0123814, *TAP: SIZE: C LOC: 494 FEET FROM P LINE AT CRESCENT, *MB: CODE: BDM3 LOC: SW 494' P/L CRESCENT 8' OUTSIDE 8' INSIDE CURB ****/ | 2018-04-25 | EXCAVATED IN MUD PLOT TO FIX INLET BOX COCK HAD CHANGED THE BOTTOM WAS BAD FOUND PLASTIC ON INLET AND LEAD ON OULET
201800725701 | 2018-04-05 | LEAD | 1929 | ALMONASTER AV | JOHNSON | WOLK | WM- LEAK IN THE STREET AND THE SIDEWALK ***********J. GILLIAM @ 13:39PM************ OUTLET SERVICE LEAK CUSTOMER OUT OF WATER /** 1) MN: A339283 SN: 0075855, *TAP: SIZE: A LOC: 106 FEET FROM P LINE AT JOHNSON N, *MB: CODE: ADM2 LOC: ON ALMONASTER 104.4FT FROM PL OF N JOHNSON ****/ | 2018-04-05 | EXCAVATED 2 X 2 MUD PLOT MADE REPAIR ON OUTLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201800725901 | 2018-04-05 | LEAD | 2019 | N JOHNSON | PAUGER | WILK | ML - METER LEAK ACCOUNT NUMBER - 129146-494642 METER NUMBER - A429463 INLET SERVICE LEAK /** 1) MN: A221509 SN: 0057490, *TAP: SIZE: A LOC: 145 FEET FROM P LINE AT PAUGER, *MB: CODE: CDM LOC: METER ON N JOHNSON 143.7 FT FROM PL PAUGER ****/ | 2018-04-13 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING ON LAD LINE IN MUD PLOT ,REPAIRED
201800729401 | 2018-04-06 | LEAD | 722 | ALVAR | DAUPHINE | WMTLK | WM--- LEAK IN BETWEEN SIDEWALK AND CURB BAD BLEEDER VALVE, ALSO EXAMINE OUTLET SERVICE FOR LEAK CON REG, GATE IS LOCKED 04/24/18 LEAK GETTING WORSE (KSW) 05/03/18 LEAK HAS GOTTEN WORSE PER SR#12840035 (AJR) 05/22/18 LEAK HAS GOTTEN WORSE (NLD) 05/30/18 LEAK HAS GOTTEN WORSE PER SR#12842496 (AJR) 06/05/18 LEAK HAS GOTTEN WORSE (KSW) /** 1) MN: A237764 SN: 0052008, *TAP: SIZE: A LOC: 136 FEET FROM P LINE AT DAUPHINE, *MB: CODE: CDM2 LOC: ON ALVAR,135' FROM U.R.P.L. DAUPHINE ****/ | 2018-06-13 | EXCAVATED 3 X 3 MUD PLOT AROUND METER BOX ALSO 2 X 1 AT FENCE LINE RENEWED OUTLET UP TO PROPERTY BACKFILLED AND CLEANED THE AREA
201800734801 | 2018-04-06 | LEAD | 4612 | KENDALL DR |  | WOLK | UNABLE TO CHANGE METER. WHEEL IS DESTROYED AND CAN'T REMOVE IT. PLEASE REPAIR AND CHANGE METER A282944 LOC ID 169600 BROKEN HANDWHEEL ALSO CHANGE METER /** 1) MN: A282944 SN: 0112174, *TAP: SIZE: A LOC: 109 FEET FROM P LINE AT METROPOLITAN, *MB: CODE: BDM LOC: ON KENDALL DR 109FT FROM PL OF METROPOLITAN 6FT ****/ | 2018-05-03 | EXCAVATED BY HAND RAISE AN RENEWED 5/8" METER BOX COMPLETE UP TO GRADE. ALSO SET BEW 5/8 WATER METER. FOUND LED ON INLET AN OUTLET BACKFILL CLEANED UP JOB AREA. OLD METER INFO: A282944 FACT: 47144838 MAKE: SENSUS READ:9723
201800735801 | 2018-04-06 | LEAD | 5315 | WICKFIELD DR |  | WILK | INLET LEAK AT THE W ATER MAIN /** 1) MN: A301291 SN: 0101584, *TAP: SIZE: A LOC: 281 FEET FROM P LINE AT RAPIDES DR, *MB: CODE: ADLZ LOC: ON WICKFIELD DR., 281' FROM P.L. RAPIDES DR., 6' ****/ | 2018-04-06 | EXCAVATED IN CONCRETE SIDEWALK OVER 8 INCH WATER MAIN REPAIR 3/4 INLET LEAD LINE. DRESS UP WITH RIVERSAND & COLDMILL JOB REFER TO ZONE 1 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METE BOX
201800738401 | 2018-04-08 | LEAD | 3520 | FOUCHER |  | WILK | WILK WATER LEAK INLET SERVICE (ABANDON SERVICE) /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-04-07 | REPAIR LEAK ON ABANDON SERVICE.
201800740001 | 2018-04-09 | LEAD | 3935 | MAGAZINE | AUSTERLITZ | WILK | 2.0ML- METER LEAK ACCT# 116968-564603 MTR# A430185 INLET SERVICE LEAK AT CURB FLOODING CURB 08/07/18****CUST STATES LEAK GETTING WORST**** (KSW) 10/05/18 CUSTOMER STATES LEAK GETTING WORSE (NLD) /** 1) MN: A147627 SN: 0023518, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT AUSTERLITZ, *MB: CODE: CELM LOC: METER ON MAGAZINE 74 FT FROM PL AUSTERLITZ ****/ DOTTIE READY 9-18-18 EXP 10-8-18 | 2018-10-08 | ARRIVED AT ABOVE LOCATION, EXAMINED, EXCAVATED BY HAND AND MADE REPAIRS TO STOP LEAK ON 5/8 INLET SERVICE LINE. BACKFILLED, CLEANED UP, AND WASHED DOWN AREA TO COMPLETE JOB. "LEAD INLET
201800746601 | 2018-04-10 | LEAD | 1215 | GOV NICHOLLS |  | WILK | ML METER LEAK ACCOUNT #105441-526058 METER #A307177 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A307177 SN: 0015929, *TAP: SIZE: B LOC: 110 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: CDN2 LOC: 110FT FROM PL ST CLAUDE ****/ | 2018-04-20 | ARRIVED AT ABOVE LOCATION EXCAVATED IN MUD PLOT WITH TREE ROOTS + FOUND 5/8 INCH CURB LEAKING ON LEAD LINE + REPAIRED BACKFILED
201800747301 | 2018-04-10 | LEAD/PLASTIC | 4720 | LYNHUBER DR | DREUX AV | WILK | EXAMINE FOR INLET SERVICE LEAK /** 1) MN: B014010 SN: 0125618, *TAP: SIZE: __ LOC: 155 FEET FROM P LINE AT DREUX AVE, *MB: CODE: ADL LOC: MTR ON LYNHUBER 153FT FROM PL DREUX 8FT OUTSD PL ****/ | 2018-04-10 | EXCAVATED DOWN ON INLET & OUTLET SERVICES FOUND COCK LEAKING ALSO METER WAS BELOW GRADE FOUND LEAD ON INLET & OUTLET PLASTIC TUBING MADE REPAIRS BY REPLAXCING COCK RING & RAISED METER TO GRADE BACKFILLED DRESS UP NO METER IN BOX
201800751601 | 2018-04-11 | LEAD | 1207 | N TONTI | GOV NICHOLLS | WILK | MI - LEAK IN STREET INLET SERVICE LEAK ON ABANDON SERVICE IN FRONT VACANT LOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-04-18 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK ON ABANDON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND DAMAGES MADE BY (ENTERGY)
201800752701 | 2018-04-11 | LEAD | 500 1/2 | ST PETER |  | WILK | UNABLE TO CHANGE METER. INSPECTOR L UDEBOER STATED LOCATION HAS AN UNDERGROUND LEAK AND WATER PRESSURE IS TOO HIGH. PLEASE REPAIR AND CHANGE METER A324319 LOC ID 136953 UNDERGROUND LEAK BEHIND METER BOX /** 1) MN: C025582 SN: 0999999, *TAP: SIZE: C LOC: 47 FEET FROM P LINE AT DECATUR, *MB: CODE: CD LOC: ON ST PETER 47FT FROM DECATUR 8FT OUTSIDE ** 2) MN: A324319 SN: 0025491, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT DECATUR, *MB: CODE: CEL1 LOC: 46' FROM PL OF DECATUR ****/ | 2018-06-15 | REPLACED 5/8 INCH HANDWHEEL + GUTS + REPLACED 5/8 INCH WATER METER AT ABOVE LOCATION ***********OLD METER INFO********* METER:A324319 FAC:53375694 MAKE:SENSUS READ:64428
201800753501 | 2018-04-11 | LEAD | 1220 | FRANCE | MARAIS | WILK | ML - METER LEAK ACCOUNT NUMBER - 186775-431046 METER NUMBER - A304195 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A144307 SN: 0142796, *TAP: SIZE: C LOC: 172 FEET FROM P LINE AT MARAIS, *MB: CODE: BDL2 LOC: 172'FROM P L MARAIS 3RD METER 6' OUTSIDE PL 3' INS ****/ | 2018-04-26 | REPLACE 5/8 INCH WASHERS + METER COCK TO STOP LEAK 3 X 2 DRIVEWAY WAS EXCAVATED BACK FILED + CLEANED THE AREA
201800754401 | 2018-04-11 | LEAD/PLASTIC | 3150 | DICKENS DR | BERKLEY DR | WILK | ML METER LEAK METER# A222378 ACCT# 233654-420022 INLET SERVICE LEAK /** 1) MN: A222378 SN: 0151250, *TAP: SIZE: B LOC: 4 FEET FROM P LINE AT IVORY, *MB: CODE: ADL2 LOC: ON DICKENS DR 3.5' FROM DPL IVORY 1' INSIDE CURB ****/ | 2018-05-21 | EXCAVATED METER BOX AND FOUND LEAK ON BOX COCK AND HAND WHEEL INSTALLED METER BOX COMPLETE
201800756401 | 2018-04-12 | LEAD | 1012 | HARDING DR | DELGADO DR | WILK | WM LEAK AT THE CURB INLET SERVICE LEAK BETWEEN CURB & STREET FLOODING CURB & STREET /** 1) MN: A287343 SN: 0074085, *TAP: SIZE: A LOC: 250 FEET FROM P LINE AT MOSS, *MB: CODE: CDN2 LOC: 250' P.L. MOSS ****/ | 2018-04-23 | EXCAVATED IN CONCRETE SIDEWALK THROUGH HEAVY TREE ROOTS + REPLACED 3/4 INCH OUTLET SERVICE LINE FROM METER BOX TO PROPERTY BACKFILLED + DRESSED UP AREA
201800756601 | 2018-04-12 | LEAD | 1815 | PIETY | N ROMAN | WILK | ML- METER LEAK METER # A289301 ACCT # 145075-431652 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A146249 SN: 0084319, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT ROMAN N, *MB: CODE: CE5 LOC: 110' P.L. N ROMAN ****/ | 2018-04-26 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH OUTLET SERVICE RENEW OUTLET FROM METER BOX TO PROPERTY BACKFILLED JOB WITH RIVERSAND COLDMILL
201800756701 | 2018-04-12 | LEAD | 2220 | LOUISA | BYRNE PL | WILK | WM LEAK IN SIDEWALK INLET SERVICE LEAK IN MUDPLOT FLOODING AREA /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-04-23 | ARRIVED AT ABOVE LOCATION FOUND DEBRIS ON TOP OF METER BOX ON SIDEWALK EXCAVATED IN CUT ALREADY MADE FOUND 5/8 INCH HANDWHEEL LEAKING ON LEAD LINE + RAN PLASTIC TOPROPERTY BACKFILLED
201800758601 | 2018-04-12 | LEAD/PLASTIC | 1537 | FERN | BIRCH | WOLK | MI CHANGE LEAD WHIP HOLE EXPOSED METER # A313924 ACCOUNT # 105820-574202 OUTLET TIE-IN ALSO LEAD REMOVAL/LEAD LINE EXPOSED **1ST AM** /** 1) MN: A313924 SN: 0007815, *TAP: SIZE: __ LOC: 72 FEET FROM P LINE AT FERN, *MB: CODE: OOO LOC: 67' FROM LRP LINE FERN ****/ | 2018-04-13 | EXCAVATED IN TREE ROOTS AND REPAIRS ON A 5/8" OUTLET ALSO RAISED THE METER TO GRADE NEW OUTLET LEAD ON THE INLET JOB COMPLETE
201800759101 | 2018-04-12 | LEAD | 1663 | N VILLERE | ANNETTE | WILK | ML- METER LEAK ACCT# 120654-486675 MTR# A337723 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A337723 SN: 0037792, *TAP: SIZE: A LOC: 56 FEET FROM P LINE AT VILLERE N, *MB: CODE: BHL LOC: SIDE ST ON ANNETTE 57' P.L. N VILLERE ****/ | 2018-04-27 | REPLACED 5/8 INCH WQAQSHERS TO STOP LEAK
201800759301 | 2018-04-13 | LEAD/PLASTIC | 53 | ALLARD BL |  | WILK | ML- METER LEAK ACCT# 179767-514996 MTR# A224113 /** 1) MN: C022151 SN: 0012732, *TAP: SIZE: C LOC: 80 FEET FROM P LINE AT DUMAINE, *MB: CODE: ADL2 LOC: DRIVE CURB - 80' P/L DUMAINE 9' OUTSIDE 12' INSIDE ****/ INLET SERVICE LEAKING | 2018-04-30 | EXCAVATED IN MUD PLOT TO FIX BAD HAND WHEEL AND RAISE METER TO GRADE FOUND LEAD ON OUTLET AND PLASTIC ON INLET OUT
201800760201 | 2018-04-13 | LEAD | 1666 | N JOHNSON |  | WOLK | /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-04-12 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING ON LEAD LINE FLOODING AREA + REPAIRED BACKFILLED NO METER
201800762501 | 2018-04-13 | LEAD | 2012 | ANNETTE |  | WILK | ML- METER LEAK MTR# B042842 ACCT# 134030-495066 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: B022745 SN: 0064814, *TAP: SIZE: B LOC: 115 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CDK LOC: ON ANNETTE,115.4' FROM P.L. NO. JOHNSON,3' FROM ****/ | 2018-04-21 | METER LEAKING IN METER BOX OUTLET WASHER CHANGED METER BOX WASHERS
201800763503 | 2018-04-20 | LEAD | 1139 | NAPOLEON AV | COLISEUM | ECLS | CLOSE SERVICE ON LARGE G-001981 METER FOR REPAIRS INSIDE ACC#211189-556088 MN#G001981 /** 1) MN: G001981 SN: 0000000, *TAP: SIZE: G LOC: 24 FEET FROM P LINE AT NAPOLEON AVE., *MB: CODE: EHP1 LOC: ON COLISEUM, 19' FROM P.L. NAPOLEON AVE., 6' IN- ****/ /** 1) MN: G001981 SN: 0000000, *TAP: SIZE: G LOC: 24 FEET FROM P LINE AT NAPOLEON AVE., *MB: CODE: EHP1 LOC: ON COLISEUM, 19' FROM P.L. NAPOLEON AVE., 6' IN- ****/ | 2018-04-19 | REPLACED 1 1/2 CURB COCK TIED INTO LEAD
201800763701 | 2018-04-13 | LEAD | 930 | PHILIP | LAUREL | WILK | ML-- METER LEAK METER # A330849 ACCT# 127719-542030 BAD BLEEDER VALVE /** 1) MN: A330849 SN: 0058120, *TAP: SIZE: A LOC: 81 FEET FROM P LINE AT CONSTANCE, *MB: CODE: CD LOC: ON PHILIP 79FT FROM PL OF CONSTANCE ****/ | 2018-04-17 | EXCAVATED IN BRICK ON INLET LINE ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL
201800763702 | 2018-04-17 | LEAD | 930 | PHILIP | LAUREL | PASI | REFER TO PAVE A 4X4 BRICK SIDEWALK /** 1) MN: A330849 SN: 0058120, *TAP: SIZE: A LOC: 81 FEET FROM P LINE AT CONSTANCE, *MB: CODE: CD LOC: ON PHILIP 79FT FROM PL OF CONSTANCE ****/ | 2018-04-27 | REFER TO ZONE 7 PAVING
201800766801 | 2018-04-13 | LEAD | 2522 | ONZAGA |  | WILK | LOCATION ID-111313 MTR-A236549 LEAK AT AND AROUND MTR INLET SERVICE LEAK BEHIND METER BOX /** 1) MN: A236549 SN: 0065802, *TAP: SIZE: A LOC: 148 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: BDNK LOC: 148FT FROM USPL DORGENOIS ON ONZAGA ****/ | 2018-04-30 | EXCAVATED 3 X 3 SIDEWALK ALSO 4 X 2 SIDEWALK NEW STOP RENEWED OUTLET SERVICE LINE UP TO PROPERTY BACKFILLED AND CLEANED THE AREA
201800767701 | 2018-04-13 | LEAD/PLASTIC | 2712 | N RAMPART | PORT | WILK | PP POOR PRESSURE ACCOUNT #116239-426725 METER #A336589 CUST STATES THATPRESSURE IS DOWN TO A TRICKLE NOW INLET SERVICE LEAK IN ASPHALT STREET CAUSING POOR PRESSURE FLOODING AREA 04/14/18 PER INSPECTOR W JOHNSON UPGRADE TO ****1ST AM **** CUSTOMER HAS 10PSI AT OUTSIDE FAUCET (NLD) 04/15/18 CUSTOMER NOW OUT OF WATER PER SR#12838145 ***GIVE OUT M. ROBINSON @ 18:13PM*** /** 1) MN: A275709 SN: 0048875, *TAP: SIZE: A LOC: 118 FEET FROM P LINE AT PORT, *MB: CODE: AEK LOC: 118FT FROM LRPL PORT ON N RAMPART ****/ | 2018-04-15 | REPLACED 20 FT . OF 3/4 TUBING FROM 6"WATER MAIN TO CURB TIED INTO LEAD.
201800779401 | 2018-04-16 | LEAD | 3017 | N TONTI |  | WILK | INLET SERVICE LEAK NEAR SIDEWALK FLOODING AREA /** 1) MN: A231986 SN: 0121370, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT MONTEGUT, *MB: CODE: CDN2 LOC: 132FT FROM P.L. MONTEGUT 8FT OUTSIDE P.L. ****/ | 2018-04-23 | ARRIVED AT ABOVE LOCATION EXCAVATED IN HARD GRAVEL FOUND 5/8 INCH CURB COCK LEAKING ON LEAD LINE + REPAIRED
201800780501 | 2018-04-16 | LEAD | 2320 | GOV NICHOLLS |  | WILK | MI-- LEAK INSIDE METER BOX EXAMINE INLET SERVICE FOR LEAK CARS PARKING OVER FMTER /** 1) MN: A300699 SN: 0050997, *TAP: SIZE: A LOC: 131 FEET FROM P LINE AT TONTI N, *MB: CODE: B LOC: ON GOV. NICHOLLS,132' FROM U.R.P.L. NO. TONTI ****/ | 2018-04-17 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING ON LEAD LINE + REPAIRED IT BACKFILLED
201800782301 | 2018-04-16 | LEAD | 2026 | ALVAR |  | WOLK | LOCATION: 304565 MTR# A 419427 PER INSP. L. UDEBOR, OUTLET SERVICE LEAK NEED REPAIRS / CUSTOMER WILL BE MOVING IN SOON. OUTLET SERVICE LEAK BEHIND BOX, FOUND OFF LEFT OFF HOUSE UNDER RENOVATION /** 1) MN: A234753 SN: 0094056, *TAP: SIZE: A LOC: 171 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CDM1 LOC: ON ALVAR, 192.5' FROM P.L. NO. JOHNSON,8' OUTSIDE ****/ | 2018-04-17 | ARRIVED AT ABOVE LOCATION EXAMINED INELT + OUTLETFOUND NO LEAK
201800782901 | 2018-04-16 | LEAD | 1446 | N CLAIBORNE AV |  | WILK | LOCATIONID#117087 METER#A407203 BLEEDER LEAK BAD CURBCOCK/BLEEDER VALVE /** 1) MN: A225228 SN: 0024487, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT KERLEREC, *MB: CODE: CFLM LOC: 1ST METER 46' P.L. KERLEREC ****/ | 2018-04-20 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH HANDWHEEL INSIDEBOX CHANGED HANDWHEEL + GUTS
201800783101 | 2018-04-16 | LEAD | 1228 | KERLEREC |  | WILK | LOCATIONID#124096-486412 METER#A183603 METER BOX OVERFLOWING INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A183603 SN: 0044316, *TAP: SIZE: A LOC: 214 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: AENO LOC: 214' P.L. ST CLAUDE AVE ****/ | 2018-04-17 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK ;EAKING ON LEAD LINE + REPAIRED CLEANED AREA BACKFILLED
201800783601 | 2018-04-16 | LEAD/PLASTIC | 1105 | SHIRLEY DR | GEN MEYER AV | WILK | ML METER LEAK MTR# A208603- ACCT# 226000-405201 INLET SERVICE LEAK /** 1) MN: A208603 SN: 0095679, *TAP: SIZE: A LOC: 137 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: AD4 LOC: ON SHIRLEY DR., 136.5' FROM P.L. GEN. MEYER AVE., ****/ | 2018-06-20 | EXCAVATED ON THE INLET AND OUTLET SERVICE THROUGH TREE ROOTS AND REPAIR LEAK THEN WE BACKFILL AND CLEAN UP JOB SITE
201800786601 | 2018-04-17 | LEAD | 216 | N PRIEUR |  | WILK | MI LEAK ON SIDEWALK EXAMINE INLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: A315477 SN: 0173818, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT IBERVILLE, *MB: CODE: __ LOC: METER ON N PRIEUR 115.5 FT FROM PL IBERVILLE ****/ | 2018-04-22 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK ALSO REMOVED ILLEGAL JUMPER FROM METER BOX BACKFILLED + DRESSED UP AREA
201800787201 | 2018-04-17 | LEAD | 622 | FLOOD | CHARTRES | WILK | ML- METER LEAK ACCT#127425-425349 METER#A328246 INLET SERVICE LEAK FOUND OFF LEFT OFF /** 1) MN: A328246 SN: 0053467, *TAP: SIZE: A LOC: 177 FEET FROM P LINE AT CHARTRES, *MB: CODE: ADL LOC: ON FLOOD 175FT FROM USPL CHARTRES ****/ | 2018-06-18 | EXCAVATED 3 X 3 MUD PLOT AROUND METER BOX MADE REPAIR ON INLET SERVICE LINE BACKFILL AND CLEANED THE AREA
201800792301 | 2018-04-17 | LEAD | 1014 | CHARTRES | ST PHILIP | WILK | ML-METER LEAK ACCT#106116-528718 METER#B023633 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A292581 SN: 0135784, *TAP: SIZE: A LOC: 114 FEET FROM P LINE AT ST PHILIP, *MB: CODE: CF LOC: 115FT FROM PL ST PHILIP ****/ | 2018-06-29 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201800795201 | 2018-04-18 | LEAD | 1718 | VALENCE | BARONNE | WMTLK | LOCATIONID#100997-571404 METER#A381534 UNDERGROUND LEAK /** 1) MN: A301868 SN: 0002967, *TAP: SIZE: B LOC: 153 FEET FROM P LINE AT BARONNE, *MB: CODE: BDN2 LOC: ON VALENCE,155' FROM U.R.P.L. BARONNE ****/ DOTTIE READY 6-11-18 EXP 7-1-18 | 2018-06-18 | EXCAVATED IN MUDPLOT ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND. REFER TO ZONE 3 TO REMOVE LEAD
201800795401 | 2018-04-18 | LEAD | 1430 | N DERBIGNY |  | WILK | INSPECTOR L. UDEBOER STATED THAT THE BLEEDER VALVE IS LEAKING. PLEASE REPAIR METER A419501 LOC ID 122356 INLET SERVICE LEAK INSIDE METER BOX ***CUSTOMER ALSO HAS LEAK INSIDE PROPERTY LINE PASS STOP AND WASTE VALVE*** /** 1) MN: A241130 SN: 0040900, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT KERLEREC, *MB: CODE: BDK LOC: METER ON N DERBIGNY 95 FT FROM PL KERLEREC ****/ | 2018-04-27 | REMOVED STONE ROCK PURCHASE BY CUSTOMER AND RXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED NUD AND ROCKS THAT CUSTOMER PLACED BEHIND METER BOX
201800795501 | 2018-04-18 | LEAD | 523 | DUMAINE | DECATUR | WILK | ML- METER LEAK MTR.# D 003702 ACCT.# 107146-528880 INLET SERVICE LEAK @ THE UNION ON LARGE METER INSIDE MANHOLE /** 1) MN: D003702 SN: 0030711, *TAP: SIZE: CCC LOC: 194 FEET FROM P LINE AT DECATUR, *MB: CODE: __ LOC: 195' P.L. DECATUR ****/ | 2018-04-24 | REPLACED 1 1/2 INCH UNION TO STOP LEAK
201800799101 | 2018-04-18 | LEAD/PLASTIC | 1226 | TITA | LAMARQUE | WILK | ML METER LEAK METER# A419394 ACCT# 227008-407797 INLET SERVICE LEAK IN MUDPLOT FLOODING CURB /** 1) MN: A340709 SN: 0122020, *TAP: SIZE: A LOC: 119 FEET FROM P LINE AT LAMARQUE, *MB: CODE: BDL LOC: ON TITA 118FT FROM P.L. LAMARQUE 9FT OUTSIDE P.L. ****/ | 2018-05-17 | EXCAVATED METER BOX AND FOUND BAD CURB COCK REPLACED CURB COCK AND CHANGED WASHERS
201800799201 | 2018-04-18 | LEAD/PLASTIC | 730 | HUNTLEE DR | MACARTHUR BL | WILK | ML METER LEAK ACCOUNT #227456-701693 METER #A411604 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A215900 SN: 0115326, *TAP: SIZE: A LOC: 425 FEET FROM P LINE AT MAC ARTHUR BLVD, *MB: CODE: CFL LOC: ON HUNTLEE DR 423' FROM PL MAC ARTHUR BLVD 6' OUTS ****/ | 2018-05-09 | EXCAVATED ON THE INLET AND OUTLET SERVICE AND REPAIR LEAK AND RAISE THE METERBOX TO GRADE THEN WE BACKFILL AND CLEAN UP JOB SITE
201800801001 | 2018-04-18 | LEAD | 1803 | CALHOUN | CROMWELL PL | WILK | WILK - WATER LEAKING IN A REPAIR CUT ON THE SIDE WALK. SERVICE IS A 2" /** 1) MN: D004537 SN: 0056538, *TAP: SIZE: C LOC: 80 FEET FROM P LINE AT LOYOLA AVE, *MB: CODE: ADLN LOC: ON CALHOUN, 76' FROM P.L. LOYOLA AVE.,9' OUTSIDE ****/ DOTTIE READY 4-23-18 EXP 5-13-18 | 2018-05-06 | ARRIVED ON JOB SITE FOR LEAK ON SIDEWALK MADE A 6FT X 12 FT CUT IN STREET AND MADE REPAIRS ON A ABANDON SERVICE IN STREET .BACKFILLED AND DRESSED CUT.
201800802101 | 2018-04-18 | LEAD | 4009 | STATE STREET DR |  | WILK | WM- LEAK BETWEEN THE SIDEWALK AND CURB INLET SERVICE LEAKING @ CURB /** 1) MN: A304742 SN: 0088318, *TAP: SIZE: Y LOC: 420 FEET FROM P LINE AT FONTAINBLEAU DR, *MB: CODE: CD LOC: 377' P.L. FONTAINBLEAU DR ****/ DOTTIE READY8-2-18 EXP 8-22-18 | 2018-08-18 | EXCAVATED AND REPAIR ON 3/4 INCH INLET AT CURB MADE 4 X 4 MUD PLOT BACKFILL HOLE. JOB COMPLETE
201800802301 | 2018-04-18 | LEAD/PLASTIC | 2925 | PITTARI PL | PATTERSON RD | WILK | ML-METER LEAK ACCT#228811-420416 METER#B033790 INLET SERVICE LEAK AT METER /** 1) MN: B030318 SN: 0127762, *TAP: SIZE: B LOC: 204 FEET FROM P LINE AT PATTERSON RD, *MB: CODE: CD LOC: ON PITTARI PL 204' FROM PL PATTERSON RD 7' OUTSIDE ****/ | 2018-06-12 | EXCAVATED METER BOX AND FOUND LEAK ON CURB COCK AND RAISED BOX TO GRADE
201800806001 | 2018-04-19 | LEAD | 1433 | N CLAIBORNE AV |  | WMBK | INSPECTOR L. UDEBOER STATED HE IS UNABLE TO SET METER. INLET AND OUTLET TOO CLOSE TOGETHER. PLEASE REPAIR AND SET 3/4 METER. CUSTOMER LIVES AND LOCATION AND IS WAITING ON WATER. LOC ID 304615 *************J.GILLIAM @ 12:00PM************** INLET AND OUTLET TOO CLOSE UNABLE TO SET 3/4 METER CUSTOMER OUT OF WATER /** 1) MN: B032397 SN: 0015385, *TAP: SIZE: B LOC: 87 FEET FROM P LINE AT , *MB: CODE: AFK LOC: ****/ | 2018-04-19 | EXCAVATED IN BRICK/CONCRETE DRIVEWAY + REPLACED 3/4 INCH METER BOX BOTTOM + SET 3/4 INCH WATER METER BACKFILLED + DRESSED UP AREA
201800809801 | 2018-04-19 | LEAD | 1461 | N JOHNSON | KERLEREC | WILK | ML-METER LEAK ACCT# 125063-488184 METER# A333805 INLET SERVICE LEAK IN BOX /** 1) MN: A333805 SN: 0047096, *TAP: SIZE: A LOC: 140 FEET FROM P LINE AT KERLEREC, *MB: CODE: AD6 LOC: 1FT LS S & W CURB 140' P.L. KERLEREC ****/ | 2018-04-27 | REMOVED BRICK AND EXCAVATED IN MUD PLOT AND REPLACED OUTLET TO PROPERTY AND TIED INTO [PLASTIC REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201800809901 | 2018-04-19 | LEAD | 1817 | ST PHILIP |  | WMBK | LOCATION: 304620 MTR# A 415932 PER INSP L. UDEBOR....INLET/OUTLET NO LINING UP, ALSO OUTLET WASHER LEAKING CUSTOMER HOME WAITING ON WATER ************J. GILLIAM @ 14:18PM*********** BROKEN METER BOX CASING CUSTOMER OUT OF WATER /** 1) MN: SN: 0051030, *TAP: SIZE: A LOC: 128 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: AFKL LOC: INSIDE BY S & W 0128' P.L. N DERBIGNY ****/ | 2018-04-19 | ARRIVED AT ABOVE LOCATION + FOUND CUSTOMER OUT OF WATERREPLACED BROKEN 5/8 INCH HANDWHEEL + GUTS IN METER BOX RESTORING WATER BACK TO ABOVE LOCATION
201800813101 | 2018-04-20 | LEAD/PLASTIC | 4618 | HERSCHEL |  | WMTBG | LOCATION: 227087 MTR# A 310897 CASING OVER CURB COCK. PLEASE REPAIR AND CHANGE METER RAISE METER BOX TO GRADE, AJUST CURB COCO AND CHANGE METER /** 1) MN: A310897 SN: 0119626, *TAP: SIZE: A LOC: 225 FEET FROM P LINE AT HUNTLEE DR, *MB: CODE: CFL LOC: ON HERSCHEL, 225' FROM P.L. HUNTLEE DR., 4' OUT- ****/ | 2018-06-11 | EXAMINED AREA CLEANED OUT METER BOX OBSERVED ON OUTLET SERVICE EXCAVATED OUTLET SERVICE REPAIRED LEAK BACKFILLED CLEANED AREA
201800813801 | 2018-04-20 | LEAD | 1631 | ELYSIAN FIELDS AV | N DERBIGNY | WILK | ML - METER LEAK ACT# 213785-482171 METER# A297672 INLET SERVICE LEAK ON A METER USED BY CONTRACTORS ON N DERBIGNY SUPPLYING A TRAILOR PER ISNP K GRIFFIN ( B ) LEAVE IN THE SYSTEM /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-04-23 | FOUND METER LEAKING INSIDE CONSTRACTION SITE REPLACED 5/8 INCH WASHERS TO STOP LEAK
201800815101 | 2018-04-20 | LEAD | 1428-30 | CLOUET |  | WILK | ML--- METER LEAK METR# A154278 ACCT# 138675-429370 *** CUSTOMER STATES METER IS LEAKING AGAIN FOLLOWING RECENT REPAIRS**** EXAMINE INLET SERVICE FOR LEAK CARS PARKING ON METER /** AT 1428: 1) MN: SN: 0069358, *TAP: SIZE: A LOC: 269 FEET FROM P LINE AT VILLERE N, *MB: CODE: CDBM LOC: ON CLOUET 269' FROM PL OF VILLERE N ****/ | 2018-04-22 | EXCAVATED IN GUTTER BOTTOM + CONCRETE SIDEWALK + RELOCATED 5/8 INCH METER BOX COMPLETER FROM GUTTER BOTTOM TO SIDEWALK BACKFILLED + DRESSED UP AREA
201800817201 | 2018-04-20 | LEAD | 1800 | BURGUNDY | PAUGER | WILK | WM-LEAK BETWEEN THE STREET AND SIDEWALK INLET SERVICE LEAK ON SIDEWALK /** 1) MN: A291692 SN: 0007071, *TAP: SIZE: A LOC: 35 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CEHL LOC: ON KERLEREC 35FT FROM LRPL OF BURGUNDY ****/ | 2018-06-05 | EXACAVTED 6 X 2 SIDEWALK CUT RENEWED OUTLET TO PROPERTY BACKFILLED AND CLEANED THE AREA
201800828701 | 2018-04-22 | LEAD/PLASTIC | 1663 | PRATT DR | PARIS AV | WILK | ML-METER LEAK ACCT#161991-499177 MEETR#B033358 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: B024710 SN: 0106064, *TAP: SIZE: B LOC: 543 FEET FROM P LINE AT PARIS AVE, *MB: CODE: ADK LOC: 543FT FROM PL PARIS AVE 9' OUTSIDE PL ****/ | 2018-04-25 | EXCAVATED IN MUD PLOT TO FIX BAD BOX COCK AND RAISE TO GRADE FOUND PLASTIC ON OUTLET AND FOUND LEAD ON INLET
201800831301 | 2018-04-22 | LEAD | 5139 | MANDEVILLE |  | WILK | /** 1) MN: A254912 SN: 0098788, *TAP: SIZE: A LOC: 271 FEET FROM P LINE AT SELMA, *MB: CODE: CDM1 LOC: 271FT PL SELMA 8' OUTSIDE 4' INSIDE CURB ****/ | 2018-04-22 | EXCAVATED AND REPAIR INELT SERVICE IN STREET EXCAVATED BY HAND -NO DOTTIE 5'X10' STREET CUT - BACKHOE NEED PAVING
201800833102 | 2018-04-23 | LEAD/PLASTIC | 500 | EMERALD | OPAL | WMTBG | METER CASING BELOW GRADE /** 1) MN: A330153 SN: 0114664, *TAP: SIZE: A LOC: 342 FEET FROM P LINE AT OPAL, *MB: CODE: CDLM LOC: ON EMERALD, 345' FROM P.L. OPAL, 8' OUTSIDE P.L., ****/ /** 1) MN: A330153 SN: 0114664, *TAP: SIZE: A LOC: 342 FEET FROM P LINE AT OPAL, *MB: CODE: CDLM LOC: ON EMERALD, 345' FROM P.L. OPAL, 8' OUTSIDE P.L., ****/ | 2018-11-16 | EXCAVATED U=IN MUDPLOT TO REPAIR AND RAISED METER TO GRADE OUTLET HAS P.V.C INLET HAS LEAD
201800834203 | 2018-10-26 | LEAD/PLASTIC | 34 | WREN | MARCONI DR | CLUP | JOB CONTINUED TO CLEAN UP AND BACKFILL /** 1) MN: C007508 SN: 0104822, *TAP: SIZE: C LOC: 342 FEET FROM P LINE AT MARCONI DR, *MB: CODE: __ LOC: 342' P/L MARCONI DR 6' OUTSIDE 6' INSIDE CURB ****/ | 2018-10-26 | EXCV REPAIRED 6 IN CLAMP BACKFILL DRESS CUT WITH SAND AND COLDMILL WASH DOWN STREET IN FRONT OWNER PROPERTY. 6 X 6 CUT IN MUDPLOT, SIDEWALK.
201800838001 | 2018-04-23 | LEAD | 1733 | URQUHART | ST ANTHONY | WILK | MI- LEAK IN THE SIDEWALK * CUST STATES HE HAD TO TURN WATER OFF IF WAS FLOODING AREA.* LEAK INSIDE PROPERTY LINE. *****SPOKE WITH CUSTOMER***** /** 1) MN: A237034 SN: 0058897, *TAP: SIZE: A LOC: 74 FEET FROM P LINE AT ST ANTHONY, *MB: CODE: AD LOC: 73FT FROM PL ST ANTHONY 7.5' OUTSIDE PL 2.5' INSID ****/ | 2018-05-02 | EXCAVATED IN BRICK SIDEWALK + REPLACED 3/4 ICH LEAD OUTLET SERVICELINE FROM METER BOX TO PROPERTY COULD NOT REPLACE INLET DUE TO VEHICLE ON SITE BACKFILLED + DRESSED UP AREA
201800838101 | 2018-04-23 | LEAD | 1422 | SPAIN |  | WILK | ML METER LEAK ACCOUNT #126930-481836 METER #A387089 INLET SERVICE LEAK NEAR GUTTER BOTTOM /** 1) MN: A242774 SN: 0061115, *TAP: SIZE: A LOC: 143 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: __ LOC: ON SPAIN 142' FROM URPL N ROBERTSON ****/ | 2018-05-14 | EXCAVATED 4 X 2 SIDEWALK CUT MADE REPAIRS ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201800840201 | 2018-04-23 | LEAD/PLASTIC | 9 | SULLIVAN PL | HUNTLEE DR | WMTLK | WM LEAK IN THE STREET EXAMINE INLET AND OUTLET SERVICE FOR LEAK NEAR DRIVEWAY FLOODING SIDEWALK /** 1) MN: A318180 SN: 0116041, *TAP: SIZE: A LOC: 101 FEET FROM P LINE AT HUNTLEE DR, *MB: CODE: BFL LOC: ON SULLIVAN PL., 101' FROM P.L. HUNTLEE DR., 2' ****/ | 2018-05-17 | EXAMINED LEAKING AREA EXAMINED METER BOX OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK
201800840601 | 2018-04-23 | LEAD | 2510 | N MIRO |  | WOLK | LOCATION: 205309 PLEASE REPAIR BROKEN WHEEL AND SET A 5/8 METER. CUSTOMER HOME WAITING ON WATER **********CUSTOMER OUT OF WATER********** J GILLIAM 13:52 BROKEN HANDWHEEL *****HOUSE IS OCCUPIED***** /** 1) MN: SN: 0062581, *TAP: SIZE: B LOC: 9 FEET FROM P LINE AT ARTS, *MB: CODE: __ LOC: ON N MIRO 10FT FROM PL ARTS 9' OUTSIDE PL 3' INSID ****/ | 2018-04-23 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH HAMDWHEEL BACKFILLED + DRESSED UP AREA
201800841101 | 2018-04-23 | LEAD | 4814 | ROYAL | JOURDAN AV | WILK | LOCATION ID-160673 MTR-A276497 MTR LEAK AT CURB COCK EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A276497 SN: 0061893, *TAP: SIZE: A LOC: 108 FEET FROM P LINE AT JOURDAN AVE, *MB: CODE: CDL LOC: 108FT FROM PL JOURDAN ON ROYAL 8FT OUTSIDE PL ****/ | 2018-05-04 | EXCAVATED 4 X 3 MUD PLOT RENEWED OUTLET SERVICE LINE TO PROPERTY BACKFILLED AND CLEANED THE AREA REFER BACK TO ZONE 4 TO HAVE LEAD LINE REMOVED FROM
201800841301 | 2018-04-23 | LEAD/PLASTIC | 2238 | VALENTINE CT | COPERNICUS | WILK | ML- METER LEAK MTR# A277847 ACCT# 230750-409840 (LEAK HAS GOTTEN WORSE) INLET SERVICE LEAK IN THE MUD PLOT FLOODING CURB /** 1) MN: A277847 SN: 0143774, *TAP: SIZE: C LOC: 300 FEET FROM P LINE AT COPERNICUS, *MB: CODE: CD LOC: 300FT FROM P.L. COPERNICUS ****/ | 2018-05-17 | EXCAVATED METER BOX AND FOUND BAD CURB COCK AND BLEEDER VALVE REPLACED CURB COCK AND RAISED BOX TO GRADE
201800844602 | 2018-06-15 | LEAD | 2515 | CHARTRES |  | WMEX | EXAMINED JOB DID'T HAVE ENOUGH TIME TO REMOVE CONCRETE OUT OF METER BOX NEED TO SET ONE METER BOX COMPLETE DUE TO METER IN CASE IN CONCRETE REFER BACK TO ZONE 4 REMOVE CEMENT FROM METER BOX SIDEWALK /** 1) MN: A139842 SN: 0026562, *TAP: SIZE: B LOC: 113 FEET FROM P LINE AT SPAIN, *MB: CODE: CELM LOC: ON CHARTRES 113FT FROM PL SPAIN ****/ | 2018-06-21 | EXCAVATED 4 X 6 CONCRETE SIDEWALK REMOVE CEMENT FROM INSIDE OF METER BOX BACKFILL JOB WITH RIVERSAND COLDMILL UNABLE TO RENEW OUTLET ITS A (BED AND BREAKFAST ) HOTEL CUSTOMER IN BUILDING ALSO REPLACE UPPER METER BOX CASING
201800844801 | 2018-04-23 | LEAD | 1803 | FRANCE |  | WOLK | LOCATION# 178189 CUSTOMER# 433103 METER# B039001 INSPECTOR DID AN INSIDE/OUTSIDE INSPECTION FOUND NO FIXTURE PROBLEMS INSIDE/FOUND CONSTANT REGISTRATION ON METER....PLEASE REPAIR /** 1) MN: B028282 SN: 0123657, *TAP: SIZE: B LOC: 36 FEET FROM P LINE AT ROMAN N, *MB: CODE: CDK1 LOC: ON FRANCE 35'P L ROMAN 7FT OUTSD PL ****/ | 2018-04-30 | REPLACED 3/4 INCH HANDWHEEL + GUTS IN METER BOX
201800845801 | 2018-04-23 | LEAD/PLASTIC | 28 | VIVIAN CT | HUNTLEE DR | WILK | ML-METER LEAK ACCT#227102-416000 METER#A259101 EXAMINE INLET SERVICE FOR LEAK FLOODING CURB /** 1) MN: A259101 SN: 0115389, *TAP: SIZE: A LOC: 532 FEET FROM P LINE AT HUNTLEE DR, *MB: CODE: BFK LOC: ON VIVIAN CT., 533' FROM P.L. HUNTLEE DR, 4' OUT- ****/ | 2018-05-25 | EXAMINED AREA BROKE OUT CONCRETE IN DRIVEWAY EXCAVATED METER OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK BACKFILLED DRESS WITH SAND CLEANED AREA
201800846202 | 2018-04-24 | LEAD/PLASTIC | 5020 | WILTON DR | WINDSOR DR | WMTBG | ACCT#114897025 MET#A241874 PLEASE RAISE TO GRADE /** 1) MN: A241874 SN: 0102953, *TAP: SIZE: A LOC: 195 FEET FROM P LINE AT WINDSOR DR, *MB: CODE: BDK3 LOC: ON WILTON 184' FROM PL WINDSOR DR 7' OUTSIDE PL 5' ****/ **********************METER BOX BELOW GRADE*************************** /** 1) MN: A241874 SN: 0102953, *TAP: SIZE: A LOC: 195 FEET FROM P LINE AT WINDSOR DR, *MB: CODE: BDK3 LOC: ON WILTON 184' FROM PL WINDSOR DR 7' OUTSIDE PL 5' ****/ | 2018-10-26 | EXCAVATED 7 X 9 CUT AROUND METER BOX 4 X 9 SIDEWALK FOUND LEAD ON INLET AND OUTLET REPLACED LEAD OUTLET WITH PLASTIC. RELOCATED METER AWAY FROM DRAIN RAISE METER TO GRADE CLEAN BACKFILLED AND DRESS JOB.
201800848401 | 2018-04-24 | LEAD | 6640 | MARSHALL FOCH | FILMORE AV | WILK | ML METER LEAK METER # B042121 ACCOUNT # 172281-512069 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: B024648 SN: 0115755, *TAP: SIZE: B LOC: 297 FEET FROM P LINE AT FILLMORE AVE, *MB: CODE: BDKL LOC: ON MARSHALL FOCH, 296' FROM P.L. FILLMORE AVE., ****/ | 2018-04-24 | EXCAVATED IN MUDPLOT ON INLET LEAK MADE ALL REPAIRS TO STOP LEAK ON LEAD BACKFILL WITH RIVERSAND REFERRED TO ZONE 1 TO REMOVE LEAD ON INLET
201800848901 | 2018-04-24 | LEAD/PLASTIC | 529 | PACIFIC AV | ELIZA | WMTLK | WM-LEAK IN THE STREET EXAMINE INLET & OUTLET SERVICE FOR A LEAK FLOODING CURB /** 1) MN: A278368 SN: 0066715, *TAP: SIZE: A LOC: 235 FEET FROM P LINE AT ELIZA, *MB: CODE: CDM1 LOC: RES ON PACIFIC AVE 235' FROM PL ELIZA ****/ | 2018-05-14 | BROKE SIDEWALK WITH SLEDGE HAMMER AND EXCAVATED METER BOX BY HAND REPLACED BAD CURB COCK BACKFILLED WITH SAND AND COLD MILL
201800849001 | 2018-04-24 | LEAD | 2715 | N DORGENOIS | FRANKLIN AV | WILK | ML METER LEAK METER # A265198 ACCOUNT # 138104-506553 INLET SERVICE LEAK ON VACANT PIECE OF PROPERTY /** 1) MN: A265198 SN: 0079165, *TAP: SIZE: A LOC: 109 FEET FROM P LINE AT PAINTERS, *MB: CODE: ADN2 LOC: BY BRIDGE NEAR POST - 109' P.L. PAINTERS ****/ | 2018-05-08 | EXCAVATED 8 X 3 SIDEWALK CUT RENEWED OUTLET UP TO PROPERTY BACKFILLED AND CLENED THE AREA
201800849301 | 2018-04-24 | LEAD | 1827 | JOSEPH |  | WILK | LOCATION: 105560 MTR# A 415771 CURB COCK LEAKING. PLEASE REPAIR. INLET SERVICE LEAKING BEHIND CURB CUCK /** 1) MN: A279507 SN: 0007425, *TAP: SIZE: B LOC: 56 FEET FROM P LINE AT LOYOLA AVE, *MB: CODE: AF LOC: FRONT 56 FT FROM LR LOYOLA AVE. ****/ | 2018-04-25 | EXCAVATED IN CONCRETE SIDEWALK REPAIR 5/8 STOP & WASTE LEAD LINE DRESS UP WITH COLD MILL & RIVERSAND JOB REFERRED TO ZONE 3 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201800854001 | 2018-04-25 | LEAD | 739 | NASHVILLE AV | MAGAZINE | WILK | LOCATIONID#101789-565818 METER#A269790 LEAK INSIDE METERBOX /** 1) MN: A269790 SN: 0014576, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT NASHVILLE AVE, *MB: CODE: CEH3 LOC: ON MAGAZINE 82FT FROM L.S.P.L. OF NASHVILLE AVE ****/ DOTTIE READY 9-10-18 EXP 9-30-18 | 2018-09-28 | REPLACED 5/8 CURB COCK TIED INTO LEAD
201800854101 | 2018-04-25 | LEAD/PLASTIC | 3741 | PITTARI PL | TULLIS DR | WOLK | MI- CONS ON METER PER INSPECTOR MTR.# A-426024 ACCT NUMBER 228378-706988 /** 1) MN: A270261 SN: 0120787, *TAP: SIZE: B LOC: 131 FEET FROM P LINE AT TULLIS DR, *MB: CODE: CD LOC: ON PITTARI PL 131' FROM PL TULLIS DR 7' OUTSIDE PL ****/ | 2018-05-16 | EXCAVATED METER BOX AND FOUND BAD CURB COCK REPLACED COCK AND RAISED METER BOX TO GRADE
201800856001 | 2018-04-25 | LEAD/PLASTIC | 1003 | BELLEVILLE | NEWTON | WILK | WM-LEAK ON THE SIDEWALK INLET SERVICE LEAK IN THE MUD PLOT NEAR SIDEWALK /** 1) MN: A270886 SN: 0032572, *TAP: SIZE: B LOC: 24 FEET FROM P LINE AT NEWTON, *MB: CODE: AD LOC: ON BELLEVILLE 24FT FROM NEWTON 8FT OUTSIDE ****/ | 2018-05-16 | EXCAVATED AND REPAIRED INLET SERVICE LEAK IN METER BOX ALSO RAISED METER BOXES TO GRADE 3X3 MUD CUT-> BACK FILLED -> NO DRESS-> UP NEEDED 2X4 SIDEWALK CUT-> BACKFILLED-> NEED PAVING
201800856201 | 2018-04-25 | LEAD | 1832 | BENTON |  | WILK | ************************PICKUP********************* INLET ON ABANDON SERVICE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-05-07 | EXCAVATED 4 X 10 MUD PLOT FOUND LEK ON 3/4 INCH ABANDON INLET SERVICE MADE REPAIRS ON INELT BACKFILLED JOB WITH RIVERSAND
201800857701 | 2018-04-25 | LEAD/PLASTIC | 1605 | BODENGER BL | PARK PL | WOLK | WM-LEAK IN SIDEWALK CHECK OUTLET SERVICE FOR A LEAK @ PROPERTY LINE /** 1) MN: A306513 SN: 0106114, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT PARK BLVD, *MB: CODE: BF LOC: ON BODENGER 64FT FROM JPARK BL 5FT OUTSIDE ****/ | 2018-05-16 | EXCAVATED METER BOX AND FOUND LEAK ON LED LINE REMOVED LED FROM OUTLET AND RAN PLASTIC FROM METER BOX TO PROPERTY
201800858101 | 2018-04-25 | LEAD/PLASTIC | 2922 | WALL BL |  | WMBK | PER LEWIS UDUEBOR CASING IS OVER CURB COCK PLEASE REPAIR AND CH/M C-25950 LOCATION #231359 REPLACE BROKEN & SHIFTED METR BOX CASING OVER CURB COCK /** 1) MN: C025950 SN: 0141884, *TAP: SIZE: C LOC: 516 FEET FROM P LINE AT MURL, *MB: CODE: BM2 LOC: 514FT FROM P.L. MURL ****/ | 2018-06-12 | EXAMINED AREA EXCAVATED THROUGH ROOTS NEAR TREE EXPOSED INLET AND OUTLET SERVICE REPLACED BROKEN METER BOX AND RAISED TO GRADE BACKFILLED WITH SAND AND CLEANED AREA
201800858102 | 2018-06-13 | LEAD/PLASTIC | 2922 | WALL BL |  | WOLK | /** 1) MN: C025950 SN: 0141884, *TAP: SIZE: C LOC: 516 FEET FROM P LINE AT MURL, *MB: CODE: BM2 LOC: 514FT FROM P.L. MURL ****/ | 2018-06-12 | EXAMINED AREA EXCAVATED THROUGH ROOTS EXPOSED INLET AND OUTLETY RAISED METER TO GRADE BACKFILLED WITH SAND AND CLEANED AREA
201800862702 | 2018-05-10 | LEAD | 216 | N PRIEUR |  | WMRE | EXCAVATED IN GUTTER ACROSS ABOVE LOCATION + UNABLE TO LOCATE NEED BACK HOE REFER BACK TO ZONE 4 TO LOCATE /** 1) MN: A315477 SN: 0173818, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT IBERVILLE, *MB: CODE: __ LOC: METER ON N PRIEUR 115.5 FT FROM PL IBERVILLE ****/ | 2018-05-16 | EXAMINED JOB AT ABOVE LOCATION FOUND CUSTOMER HAS WATER NOW
201800863301 | 2018-04-26 | LEAD/PLASTIC | 5223 | CAMP |  | WILK | MI-- CUT SERVICES *** CUSTOMER W/O WATER***** SERVICES CUT BY ENTERGY 3700 TULANE AVE NEW ORLEANS, LA. 70119 504-593-3491 ********DAMAGE CLAIM******** (L.THOMPSON @ 12:17PM) CUT INLET SERVICE BY ENTERGY GAS,HOLE IS OPEN CUSTOMER OUT OF WATER /** 1) MN: A242533 SN: 0016834, *TAP: SIZE: B LOC: 123 FEET FROM P LINE AT BELLECASTLE, *MB: CODE: CFM LOC: 123FT FROM LSPL BELLECASTLE ****/ | 2018-04-26 | EXAMINE WATER SERVICE CUT BY ETERGY GAS REPLACED 4 FT OF 3/4 TUBING TIED INTO LEAD DUE TO ENTERGY WORKING IN AREA.CREW FOUND METER C034405 AT ABOVE LOCATION
201800865101 | 2018-04-26 | LEAD | 1919 | N RAMPART | PAUGER | WILK | MI- LEAK IN THE SIDE WALK INLET SERVICE LEAK IN SIDEWALK FLOODING CURB & STREET /** 1) MN: A268642 SN: 0041773, *TAP: SIZE: A LOC: 141 FEET FROM P LINE AT BOURBON, *MB: CODE: AEN2 LOC: ON RAMPART 142FT FROM BOURBON ****/ | 2018-05-09 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201800870701 | 2018-04-27 | LEAD/PLASTIC | 601 | RIVER OAKS DR | HERSCHEL | WMTLK | MI-LEAK AT THE SIDEWALK EXAMINE INLET/OUTLET SERVICE FOR LEAK AT SIDEWALK /** 1) MN: A296472 SN: 0118138, *TAP: SIZE: B LOC: 36 FEET FROM P LINE AT HERSCHEL, *MB: CODE: CDL LOC: ON RIVER OAKS DR 36' FROM PL HERSCHEL 7' OUTSIDE P ****/ | 2018-05-17 | EXCAVATED METER BOX AND FOUND BAD COCK AND BOX BELOW GRADE REPLACED CURB COCK AND RAISED METER BOX TO GRADE BACKFILLED AND DRESSED UP WITH RIVER SAND
201800871302 | 2018-05-09 | LEAD | 2539 | COLUMBUS |  | WMTLK | EXAMINE JOB AT ABOVE LOCATION UNABLE TO DO JOB DUE TO CONSTRACTION GOIN ON /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-06-06 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8INCH CURB COCK + 5/8INCH HANDWHEEL + RAISED 5/8INCH METER BOX BOTTOM TO GRADE ALSO SET 5/8 INCH METER BACKFILLED + DRESSED UP AREA
201800872501 | 2018-04-28 | LEAD/PLASTIC | 309 | HENDEE | PATTERSON RD | WILK | ML-METER LEAK METER#A432144 ACC#236376-403547 INLET SERVICE LEAK /** 1) MN: A117525 SN: 0166469, *TAP: SIZE: B LOC: 23 FEET FROM P LINE AT ALIX, *MB: CODE: __ LOC: ON HENDEE, 4' FROM D.P.L. ALIX, 12' INSIDE CURB ****/ | 2018-06-11 | BROKE OUT SIDEWALK TO REPLACE BAD CURB COCK REPLACED COCK AND BACKFILLED WITH SAND AND COLD MILL
201800872701 | 2018-04-28 | LEAD | 1019 | ST MAURICE AV | ST CLAUDE AV | WILK | WM-LEAK ON THE SIDEWALK INLET SERVICE LEAK IN BOX /** 1) MN: A335827 SN: 0065335, *TAP: SIZE: A LOC: 160 FEET FROM P LINE AT RAMPART N, *MB: CODE: CL1 LOC: ON ST MAURICE 161FT FROM PL N RAMPART ****/ | 2018-05-10 | EXCAVATED 4 X 5 GUTTER BOTTOM ALSO 4 X 2 MUD PLOT RENEWED OUTLET SERVICE LINE TO PROPERTY BACKFILLED AND CLEANED THE AREA
201800873101 | 2018-04-28 | LEAD | 2561 | N TONTI | ARTS | WILK | ML- METER LEAK ACCT# 150152-484638 MTR# A407057 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A305131 SN: 0082939, *TAP: SIZE: B LOC: 144 FEET FROM P LINE AT ARTS, *MB: CODE: BFLK LOC: ON TONTI 147FT FROM ARTS ****/ | 2018-05-08 | EXCAVATED 6 X 2 MUD PLOT RENEW OUTLET TO PROPERTY BACKFILLED AND CLEANED THE AREA
201800874701 | 2018-04-29 | LEAD | 1330 | DELERY | N VILLERE | WMLK | WM-LEAK IN THE STREET LEAK ON THE WATER MAIN IN THE STREET (C) /** 1) MN: A238970 SN: 0104149, *TAP: SIZE: A LOC: 9 FEET FROM P LINE AT VILLERE N, *MB: CODE: BDL1 LOC: ON DELERY, 9' EXTENDED LOWER LINE NO. VILLERE,7.5' ****/ | 2018-05-09 | EXCAVATED 5 X 10 ASPHALT STREET CUT FOUND LEAK ON ABANDON 3/4 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND COLDMILL
201800875601 | 2018-04-29 | LEAD | 2218 | CLOUET | N MIRO | WILK | MI-C Y NO WATER METER#A424679 AQCCT#120460-590435 NO WATER ON THE INLET (JOB GIVEN TO J. GILLIAM (PET) /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-04-29 | MADE 4 X 8 CUT IN DRIVEWAY AND MADE REPAIRS ON 3/4 INCH TEE RENEWED OUTLET TO PROPERTY TIED INTO LEAD AT GATE BACKFILLED AREA
201800875701 | 2018-04-29 | LEAD/PLASTIC | 801 | VERRET | SLIDELL AV | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: C021180 SN: 0089977, *TAP: SIZE: C LOC: 42 FEET FROM P LINE AT VERRET, *MB: CODE: ADH LOC: ON SLIDELL 42'FROM P L VERRET 9' OUTSIDE PL OIL ST ****/ | 2018-05-14 | EXCAVATED AND REPAIRED INLET SERVICE LEAK IN METER BOX
201800875901 | 2018-04-29 | LEAD | 1310 | BROOKLYN | LAMARQUE | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A314128 SN: 0083910, *TAP: SIZE: A LOC: 83 FEET FROM P LINE AT LAMARQUE, *MB: CODE: CD LOC: MTR ON BROOKLYN 83FT FRM PL LAMARQUE ****/ | 2018-05-19 | EXAMINED LEAKING AREA LOCATED MARKING LEFT BY ECHOLOGIC EXCAVATED IN STREET EXPOSED SERVICE INLET LEAK REPAIRED LEAK BACKFILLED AND CLEANED JOB SITE
201800876101 | 2018-04-29 | LEAD/PLASTIC | 701 | PATTERSON DR |  | WOLK | WATER LEAK -OUTLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A213900 SN: 0062355, *TAP: SIZE: C LOC: 95 FEET FROM P LINE AT PATTERSON DR, *MB: CODE: BDHX LOC: ON VALLETTE 95' FROM PL PATTERSON DR ****/ | 2018-05-22 | EXCAVATED AND REPAIRED INLET SERVICE LEAK IN TREE ROOTS ALSO RAISED METER BOX TO GRADE 3X10 MUD CUT->BACKFILLED->NO DRESS-UP NEEDED
201800877001 | 2018-04-29 | LEAD/PLASTIC | 3215 | NEWTON | HORACE | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-05-16 | EXAMINED AREA CHOPPED BUSH AND HIGH DRESS CUT OF WAY LOCATED LEAK EXCAVATED METER BOX EXPOSED INLET AND OUTLET OBSERVED COPPER ON BOTH SIDES LEAK ON INLET SIDE AND BROKEN HAND WHEEL REPAIRED LEAK AND REPLACE BROKEN OUTLET
201800877101 | 2018-04-29 | LEAD | 1549 | N DERBIGNY | LAHARPE | WILK | ML- METER LEAK ACCT# 124010-487636 MTR# A431080 EXAMINE INLET SERVICE FOR A LEAK (CARS PARKING ON METER) /** 1) MN: SN: 0044486, *TAP: SIZE: A LOC: 90 FEET FROM P LINE AT LAHARPE, *MB: CODE: D LOC: ON DERBIGNY 89FT FROM LSPL LAHARPE ****/ | 2018-05-08 | EXCAVATED 4 X 6 LIMESTONES GUTTER BOTTOM RELOCTE METER BOX INTO SIDEWALK RENEWED 5/8 INCH OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILLED JOB WITH RIVERSAND COLDMILL TIE INTO LEAD LINE GOIN UNDER FOUNDATION
201800878501 | 2018-04-30 | LEAD | 3301 | GRAND RTE ST JOHN | VIGNAUD | WILK | ML- METER LEAK ACCT# 116470-522072 MTR# A286908 BAD BLEEDER VALVE /** 1) MN: A286908 SN: 0021769, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT PONCE DE LEON, *MB: CODE: BEH7 LOC: SIDE ST ON HAGAN AVE 116' P.L. PONCE DE LEON ****/ | 2018-05-09 | EXCAVATED 3 X 2 SIDEWALK CUT MADE REPAIR ON INLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201800879801 | 2018-04-30 | LEAD | 604 | HAGAN AV | TOULOUSE | WILK | ML- METER LEAK ACCT# 218791-719739 METER # A359769 EXAMINE INLET SERVICE FOR LEAK IN MUDPLOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-05-09 | EXCAVATED 3 X 3 FLOWER BED REPLACE 3/4 INCH HANDWHEEL WITH 5/8 INCH HANDWHEEL TO STOP LAK BACKFILLED AND CLEANED THE AREA
201800880001 | 2018-04-30 | LEAD | 1809 | N BROAD | O"REILLY | WILK | ML METER LEAK METER# A423677 ACCT# 140057-491891 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A306682 SN: 0070890, *TAP: SIZE: A LOC: 86 FEET FROM P LINE AT O REILLY, *MB: CODE: B LOC: FRONT OF 1809 N BROAD NEAR DR BY 1813 N BROAD ****/ | 2018-05-21 | MADE 4 X 4 CUT INSIDE WALK AND MADE REPAIRS ON 3/4 INCH INLET SERVICE O 3/4 INCH INLET SERVICE FOR ABANDON HOUSE BACKFILLED AREA
201800881501 | 2018-04-30 | LEAD | 1027 | CLOUET | ST CLAUDE AV | WILK | ML - METER LEAK ACCT # 160965-427526 METER # A322712 INLET SERVICE LEAK /** 1) MN: SN: 0048216, *TAP: SIZE: B LOC: 180 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: __ LOC: ON CLOUET 182' FROM PL ST CLAUDE AVE 7.5' OUTSIDE ****/ | 2018-05-15 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET NEED CONCRETE PILE TO BE PICKED UP AND BACKFILLED LEFT 1 BARREL ON JOB FOR SAFETY
201800881901 | 2018-04-30 | LEAD | 1320 | HENRY CLAY AV | PRYTANIA | WMTLK | LOCATIONID#105103-702167 METER#A152538 METERBOX OVERFLOWING /** 1) MN: A152538 SN: 0039892, *TAP: SIZE: A LOC: 166 FEET FROM P LINE AT PRYTANIA, *MB: CODE: AEGZ LOC: 166FT FROM LSPL PRYTANIA IN DRIVE ****/ | 2018-05-02 | EXCAVATED IN CONCRETE DRIVEWAY REPAIR 5/8 STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND & COLDMILL JOB REFER TO ZONE 3 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201800882001 | 2018-04-30 | LEAD | 1335 | HENRY CLAY AV |  | WMTLK | LOCATIONID#101107-562547 METER#B033513 METERBOX OVERFLOWING /** 1) MN: B020815 SN: 0002541, *TAP: SIZE: B LOC: 27 FEET FROM P LINE AT HENRY CLAY AVE, *MB: CODE: ADH LOC: BY CATCH BASIN SIDE ST NEAR CORNER. 2FT FROM RPL ****/ | 2018-05-02 | EXCAVATED IN MUD PLOT REPAIR 3/4 STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND JOB REFER TO ZONE 3 TO TAKE LEAD LINE OUT FROMWATER MAIN TO METER BOX
201800882301 | 2018-04-30 | LEAD | 817 | EXPOSITION BL | MAGAZINE | WMTLK | LOCATIONID#135504-563254 METER#A278393 LEAK INSIDE METERBOX /** 1) MN: A290730 SN: 0066229, *TAP: SIZE: A LOC: 132 FEET FROM P LINE AT MAGAZINE, *MB: CODE: BDN LOC: ON EXPOSITION BLVD., 133' FROM P.L. MAGAZINE ****/ | 2018-05-03 | EXCAVATED IN MUDPLOT ON INLET LEAK MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND ON LEAD REFER TO ZONE 3 TO REMOVE LEAD METER:A290730 FAC:49140324 MAKE:SENSUS READ:13530
201800882302 | 2018-05-03 | LEAD | 815 | EXPOSITION BL | MAGAZINE | WSNR | REFER TO ZONE TO REMOVE LEAD LINE ON THE INLET /** 1) MN: A278393 SN: 0066229, *TAP: SIZE: A LOC: 132 FEET FROM P LINE AT MAGAZINE, *MB: CODE: BDN LOC: ON EXPOSITION BLVD., 131.7' FROM P.L. MAGAZINE ****/ | 2018-08-17 | REFERRED TO CONTRACTOR
201800883801 | 2018-04-30 | LEAD/PLASTIC | 3737 | PIEDMONT DR | MONTEPELIER | WILK | MI- LEAK AT THE SIDEWALK INLET SERVICE LEAK INSIDE METER BOX, ALSO REPLACE BROKEN METER BOX CASING /** 1) MN: A263823 SN: 0086246, *TAP: SIZE: A LOC: 23 FEET FROM P LINE AT PIEDMONT DR, *MB: CODE: CDN1 LOC: 23FT FROM PL MONTEPELIER 9FT OUTSD 4FT INSD CUR ****/ | 2018-05-11 | EXCAVATED IN A 4X4 MUD PLOT BTY HAND. FOUND PLASTIC ON OUTLET AND LEAD ON INLET WITH 5/8 CRUB COCK LEAKING. REPLACE 5/8 CURB COCK WITH A METER BOX COMPLETE. BACKFILL AN RAISE METER TO GRADE. JOB COMPLETE.
201800888501 | 2018-05-01 | LEAD | 1235 | ANNETTE | MARAIS | WOLK | MI-CHANGE LEAD WHIP ****AREA EXPOSED*** OUTLET TIE-IN HOUSE UNDER RENOVATION (C) /** 1) MN: A339557 SN: 0045457, *TAP: SIZE: A LOC: 50 FEET FROM P LINE AT MARAIS, *MB: CODE: BD LOC: METER ON ANNETTE 51.5 FT FROM PL MARAIS ****/ | 2018-05-01 | EXCAVATED IN MUD PLOT REPAIR 5/8 STOP & WASTE LEAD LINE & RENEW 3/4 OUTLET SERVICE PLASTIC LINE FROM METER BOX TO PROPERTY LINE ALSO RAISE TO GRADE & RESET 5/8 METER A431521 JOB REFER TO ZONE 4 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX OLD METER INFO A415887 FACT: 15481333 MAKE: HERSEY READ:0
201800889501 | 2018-05-01 | LEAD | 2401 | ROBERT |  | WMTLK | MTR LEAK/MTR BOX OVER FLOWING/AREA FLOODED EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: B021640 SN: 0067849, *TAP: SIZE: B LOC: 80 FEET FROM P LINE AT UPPERLINE, *MB: CODE: BDHO LOC: ON S ROBERTSON 80FT FROM PL ROBERT ****/ | 2018-05-03 | EXCAVATED IN MUDPLOT REPAIR 3/4 STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND JOB REFER TO ZONE 3 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201800889701 | 2018-05-01 | LEAD/PLASTIC | 618 | ENGLISH TURN DR | ENGLISH TURN CT | WMTLK | ML METER LEAK ACCT# 237438-700366 METER# A299700 EXAMINE INLET/OUTLET SERVICE FOR LEAK INSIDE METER BOX IN DRIVEWAY /** 1) MN: A299700 SN: 0172950, *TAP: SIZE: A LOC: 50 FEET FROM P LINE AT ENGLISH TURN, *MB: CODE: CD LOC: ON ENGLISH TURN 50 FT FROM DIV P/L LAKEWAY 8FT ****/ | 2018-06-11 | EXAMINED AREA PUMPED AND CLEANED OUT METER OBSERVED LEAK ON OUTLET SERVICE REPAIRED CLEANED AREA
201800891001 | 2018-05-01 | LEAD | 405 | ST MAURICE AV | BIENVENUE | WILK | ML METER LEAK ACCT# 129261-426316 METER# A393627 EXAMINE INLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: SN: 0057734, *TAP: SIZE: A LOC: 53 FEET FROM P LINE AT BIENVENUE, *MB: CODE: OOO LOC: ON ST. MAURICE AVE.,53' FROM L.S.P.L. BIENVENUE ****/ | 2018-06-13 | EXCAVATED 3 X 3 MUD PLOT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA ****REFER BACK TO ZONE TO HAVE LEAD REMOVED FROM STREET*
201800892701 | 2018-05-01 | LEAD/PLASTIC | 2405 | ATHIS |  | WILK | ML-- METER LEAK METER # 162812-472598 ACCT# 168812-472598 EXAMINE INLET SERVICE LEAK CAUSING OVERFLOW /** 1) MN: B030347 SN: 0101987, *TAP: SIZE: B LOC: 56 FEET FROM P LINE AT ATHIS, *MB: CODE: ADL LOC: ON ST. ROCH AVE., 56' FROM P.L. ATHIS, 7' OUTSIDE ****/ | 2018-05-04 | EXCAVATED IN MUD PLOT AROUND 3/4" METER BOX , MADE REPAIRS ON INLET SERVICE INSIDE METER BOX CLEANED AND DRESSED UP AREA , FOUND LEAD ON INLET SERVICE
201800892901 | 2018-05-02 | LEAD | 2622 | ALMONASTER AV | LAW | WOLK | LOCATION# 156735 CUSTOMER# 479473 METER# A310298 INSPECTOR DID AN INSIDE/OUTSIDE INSPECTION FOUND A CONSTANT STOP & GO @ COCK.....PLEASE REPAIR /** 1) MN: A257644 SN: 0093920, *TAP: SIZE: A LOC: 162 FEET FROM P LINE AT LAW, *MB: CODE: BDM1 LOC: ON ALMONASTER AVE 161.5' FROM PL LAW 9' OUTSIDE PL ****/ | 2018-05-16 | EXAMINED JOB AT ABOVE LOCATION FOUND NO LEAK ON OUTLET SERVICE
201800894301 | 2018-05-02 | LEAD/PLASTIC | 2258 | GEN COLLINS AV |  | WOLK | ML - METER LEAK ACCOUNT NUMBER - 230951-408792 METER NUMBER - A135243 CHECK FOR LEAK @ PROPERTY LINE METER BOX OVERFLOWING /** 1) MN: A135243 SN: 0139452, *TAP: SIZE: B LOC: 168 FEET FROM P LINE AT GALLATIN, *MB: CODE: ADM2 LOC: ON GEN. COLLINS AVE., 168' FROM P.L. GALLATIN, 7' ****/ | 2018-05-16 | EXCAVATED AND RENEW OUTLET SERVICE ALSO LEAK ON PROPERTY AND BACKFILL DRESS UP JOB SITE
201800895001 | 2018-05-02 | LEAD | 900 | MONTEGUT | BURGUNDY | WMTLK | ML-METER LEAK ACCT# 121922-426807 METER # A400425 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER, LOW LINE AREA /** 1) MN: A291420 SN: 0040357, *TAP: SIZE: A LOC: 71 FEET FROM P LINE AT MONTEGUT, *MB: CODE: AHK LOC: ON BURGUNDY,75' FROM U.S.P.L. URQUHART ****/ | 2018-05-15 | EXCVATED 4 X 4 BRICK SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201800897801 | 2018-05-02 | LEAD | 3622 | URQUHART |  | WILK | LOCATION: 211985 PER INSP L. UDEBOR, INLET SERVICE NEED REPAIRS AND NO CURB COCK. PLEASE REPAIRS AND SET 5/8 METER CUSTOMER WAITING ON WATER INLET SERVICE LEAK ALSO SET 5/8 METER HOUSE IS VACANT, CUSTOMER WAITING TO MOVE IN /** 1) MN: A325054 SN: 0054907, *TAP: SIZE: B LOC: 50 FEET FROM P LINE AT URQUHART, *MB: CODE: ADH LOC: ON INDEPENDENCE 50' FROM P.L. URQUHART 6' OUTSIDE ****/ | 2018-05-16 | EXCAVATED 4 X 6 MUD PLOT RENEW 3/4 INCH INLET SERVICE TO METER BOX SET A 5/8 INCH WATER METER LEFT OFF IN BOX BACKFILLED JOB WITH RIVERSAND
201800898501 | 2018-05-02 | LEAD | 1829 | LAPEYROUSE |  | WILK | LOCATION: 303909 MTR# A 430559 INLET SERVICE LEAK BEHIND CURB COCK, PLEASE REPAIR. INLET SERVICE LEAK BEHIND METER BOX FLOODING CURB/STREET /** 1) MN: A304620 SN: 0053824, *TAP: SIZE: A LOC: 92 FEET FROM P LINE AT PRIEUR N, *MB: CODE: BDE LOC: ON LAPEYROUSE,92' FROM L.R.P.L. NO. PRIEUR ****/ | 2018-05-11 | EXCAVATED 4 X 3 MUD PLOT SET ONE METER BOX COMPLETE AND TIE CUSTOMER LINE OUTLET BACKFILLED AND CLEANED THE AREA *******REFER TO HAVE LEAD REMOVE FROM THE STREET*****
201800899301 | 2018-05-03 | LEAD | 1317 | GALLIER | URQUHART | WOLK | MI- LEAK IN DRIVEWAY CAUSED SINKHOLE /** 1) MN: A130275 SN: 0076480, *TAP: SIZE: B LOC: 149 FEET FROM P LINE AT URQUHART, *MB: CODE: ADW2 LOC: 149'FROM URQUHART 2'FROM CURB ON GALLIER ****/ EXAMINE UP TO PROPERTY LINE FOR LEAK | 2018-05-15 | EXCVAVTED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL NEED PILE TO BE PICKED UP AT ABOVE LOCATION
201800903101 | 2018-05-03 | LEAD | 415 | S DUPRE | BANKS | WILK | ML- METER LEAK MTR# A 384167 ACC#114136-706943 INLET SERVICE LEAK NEAR SIDEWALK /** 1) MN: A319675 SN: 0017506, *TAP: SIZE: A LOC: 173 FEET FROM P LINE AT BANKS, *MB: CODE: BFL LOC: 172' P.L. BANKS ****/ | 2018-05-21 | EXCAVATED IN MUD PLOT AND REPLACED 3/4 INCH OUTLET TO PROPERTY WITH 3/4 INCH PLASTIC TUBING TO PROPERTYTIED INTO COPPER BACKFILLED AREA
201800903801 | 2018-05-03 | LEAD | 2615 | DAUPHINE | PORT | WOLK | ACCT# 103574-480608 METER# A276241 CONSTANT REGISTRATION. PLEASE REPAIR /** 1) MN: A276241 SN: 0040308, *TAP: SIZE: A LOC: 127 FEET FROM P LINE AT PORT, *MB: CODE: BEN LOC: ON DAUPHINE 127.6FT FROM LSPL OF ALMONASTER AVE ****/ | 2018-05-14 | EXAMINED JOB + FOUND NO LEAK INSIDE METER BOX
201800907101 | 2018-05-03 | LEAD | 1811 | MARIGNY | PRIEUR | WILK | ML - METER LEAK MTR # A298628 ACCT # 115471-482726 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A298628 SN: 0063117, *TAP: SIZE: A LOC: 93 FEET FROM P LINE AT ROMAN N, *MB: CODE: ADM4 LOC: ON MARIGNY 93FT FROM PL OF N ROMAN 2FT FROM PL ****/ | 2018-05-14 | REPLACED 5/8 INCH WASHERS TO STOP LEAK
201800907201 | 2018-05-03 | LEAD | 4917 | IBERVILLE | HELENA | WILK | ML-METER LEAK MTR# A 29211 ACC#146619-717364 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A320762 SN: 0078685, *TAP: SIZE: B LOC: 148 FEET FROM P LINE AT ANTHONY N, *MB: CODE: CD LOC: ON IBERVILLE 147FT FROM PL OF N ANTHONY ****/ | 2018-05-28 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 5/8 CURB COCK LEAKING REPLACE CURB COCK TIED INTO LEAD UNABLE TO REMOVE LEAD DUE TO CAR PARKED OVER WATER MAIN *************OLD METER INFO************ METER:A293211 FAC:50194984 NAKE:SENSUS READ:20314
201800907901 | 2018-05-03 | LEAD | 1726 | GENTILLY BL |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 172803-492039 METER NUMBER - C018740 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: C016346 SN: 0116292, *TAP: SIZE: C LOC: 236 FEET FROM P LINE AT D'ABADIE, *MB: CODE: AD LOC: BET AUBRY & DABADIE BY POLE 236' P/L DABADIE 10' ****/ | 2018-05-23 | MADE 4 X 4 SIDEWALK CUT AND RELOCATED METER OUT OFGARDEN AND ROOTS INTO SIDEWALK BACKFILLED AREA
201800908001 | 2018-05-03 | LEAD | 2415 | ST BERNARD AV | N DORGENOIS | WILK | MI LEAK ON THE SIDEWALK INLET SERVICE LEAK IN TREEROOTS FLOODING CURB/STREET /** 1) MN: A238268 SN: 0090703, *TAP: SIZE: __ LOC: 137 FEET FROM P LINE AT N ROCHEBLAVE, *MB: CODE: A LOC: ON ST BERNARD AVE 136.5' FROM PL N ROCHEBLAVE 13' ****/ | 2018-05-27 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201800908901 | 2018-05-03 | LEAD | 4001 | CAMP | CONSTANTINOPLE | WILK | WM LEAK BETWEEN STREET & SIDEWALK **********LEAVE IN SYSTEM********* CHANGED FROM 1020 COSTANTINOPLE/CHESTNUT INLET SERVICE LEAK ON SIDEWALK & CURB 05/15/18 LEAK GETTING WORSE (KSW) /** 1) MN: 000000 SN: 0012095, *TAP: SIZE: B LOC: 77 FEET FROM P LINE AT CAMP, *MB: CODE: BEOH LOC: FIRST METER SIDE ST ON CONSTANTINOPLE 77' P/L CAMP ** 2) MN: A280083 SN: 0012095, *TAP: SIZE: B LOC: 76 FEET FROM P LINE AT CAMP, *MB: CODE: BEOH LOC: ON CONSTANTINOPLE 2ND METER 77FT FROM PL CAMP ****/ DOTTIE READY 5-17-18 EXP 6-6-18 | 2018-05-30 | ARRIVED ON JOB EXCAVATED IN BRICK SIDEWALK FOUND LEAK ON INLET LEAD SERVICE BEHIND METER BOX COCK MADE REOAIRS AND BACKFILLED LEAD NEED TO BE REMOVED FROM METER BOX TO WATER MAIN. JOB COMPLETE
201800910601 | 2018-05-04 | LEAD | 2516 | GOV NICHOLLS | N DORGENOIS | WILK | ML - INLET SERVICE LEAK NEAR METER BOX /** 1) MN: A144142 SN: 0040228, *TAP: SIZE: A LOC: 131 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: CF LOC: METER ON GOV NICHOLLS 131 FT FROM PL N ROCHEBLAVE ****/ | 2018-05-24 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201800913101 | 2018-05-04 | LEAD | 1004 | N LOPEZ |  | WILK | ML - METER LEAK ACCT#110752-521399 METER#A284179 EXAMINE INLET SERVICE FOR LEAK INSIDE BOX /** 1) MN: A284179 SN: 0015687, *TAP: SIZE: B LOC: 29 FEET FROM P LINE AT ST PHILIP, *MB: CODE: AF LOC: 29' P.L. ST PHILIP ****/ | 2018-05-15 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO MAKE THE REPAIRS...MADE A 3X3 MUD CUT BACKFILLED AND DRESS UP
201800914701 | 2018-05-04 | LEAD | 1247 | TENNESSEE |  | WILK | ML METER LEAK METER# A430257 ACCT# 304307-711825 INLET SERVICE LEAK IN GRASS NEAR METER /** 1) MN: A322339 SN: 0106966, *TAP: SIZE: A LOC: 141 FEET FROM P LINE AT URQUHART, *MB: CODE: ADL LOC: MTR 141FT FROM PL URQUHART ON TENNESSEE 9FT OUTSD ****/ | 2018-05-21 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON ABANDON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201800917701 | 2018-05-05 | LEAD | 526 | SOCRATES | VALLETTE | WILK | **********PICK UP*********** INLET SERVICE LEAK IN THE SIDEWALK BY VACANT LOT /** 1) MN: SN: 0062208, *TAP: SIZE: A LOC: 212 FEET FROM P LINE AT NUNEZ, *MB: CODE: CD LOC: ON SOCRATES 210' FROM PL NUNEZ ****/ | 2018-05-19 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCHCURB COCK FOR ABANDON LOT BACKFILLED AREA
201800921302 | 2018-06-05 | LEAD | 346 | BARONNE | PERDIDO | WILK | NEED BACK HOE TO MAKE REPAIR IN STREET REFER BACK TO ZONE 4 FOR REPAIRS /** 1) MN: H001539 SN: 0041620, *TAP: SIZE: H LOC: 38 FEET FROM P LINE AT BARONNE, *MB: CODE: CD LOC: ON PERDIDO 47' FROM P.L. BARONNE 21' OUTSIDE P.L. ****/ | 2018-06-06 | EXCAVATED IN ASPHALT STRET + EXPOSED ABANDONED 2 INCH INLET SERVICE LINE FOUND NO LEAK ON INLET AT ABOVE LOCATION COMPACTED BACKFILLED + DRESSED UP AREA
201800928401 | 2018-05-07 | LEAD | 2205-07 | DUMAINE | N GALVEZ | WILK | WM-LEAK IN SIDEWALK EXAMINE INLET SERVICE FOR A LEAK 05/15/18 LEAK NOW CAUSING POOR PRESSURE PER SR#12841180 (AJR) /** AT 2205: 1) MN: A115952 SN: 0041938, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT GALVEZ N, *MB: CODE: ADL1 LOC: ON DUMAINE 63.5FT FROM PL OF N GALVEZ ****/ | 2018-05-23 | REPLACE BAD 5/8 INCH WATER METER AT ABOVE LOCATION *****************OLD METER INFO************** METER:A378916 FAC:73273347 MAKE:SENSUS READ:7032
201800929901 | 2018-05-07 | LEAD | 4303 | HOLLYGROVE | HEATON | WMTLK | MI- LEAK ON SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK, **SIGNS OF METER BOX BEING ROLLED OVER*** /** 1) MN: A129019 SN: 0079998, *TAP: SIZE: B LOC: 15 FEET FROM P LINE AT HEATON, *MB: CODE: CFLM LOC: 15FT FROM PL HEATON ON HOLLYGROVE ****/ | 2018-05-14 | EXCAVATED IN MUD PLOT ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK.BACKFILL WITH RIVERSAND REFER TO ZONE 1 TO REMOVE LEAD.
201800929902 | 2018-05-14 | LEAD/PLASTIC | 4301 | HOLLYGROVE | HEATON | WSNR | REFER TO ZONE 1 TO REMOVE LEAD FROM METERBOX TO MAIN. /** 1) MN: A287324 SN: 0079998, *TAP: SIZE: B LOC: 19 FEET FROM P LINE AT HEATON, *MB: CODE: CFLM LOC: 18FT PL HEATON 7FT OUTSD PL 3FT INSD CURB ****/ | 2018-08-20 | EXCAVATED OVER WATER MAIN TO RENEW LEAD LINE WAS NOT ABLE TO FINISH DUE TO TIME, MADE AREA SAFE AND CLEANED UP, REFER TO ZONE 7 FOR REPAIR
201800931401 | 2018-05-07 | LEAD | 2130-38 | DUMAINE | N JOHNSON | WMTLK | MI LEAK ON THE SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** AT 2138: 1) MN: A155319 SN: 0055786, *TAP: SIZE: B LOC: 46 FEET FROM P LINE AT DUMAINE, *MB: CODE: BDL1 LOC: 30FT FROM LPL CURB SIDE OPP GATE ON N GALVEZ ****/ | 2018-05-21 | EXAMINED JOB AND FOUND METER NOT SET IN CURB COCK REPLACED 5/8 INCH WASHERS ON INLET AND OUTLET INSIDE METER BOX
201800931701 | 2018-05-07 | LEAD | 3429 | LAUREL | DELACHAISE | WILK | ML- METER LEAK MN:A318745 LOCATION:102020-558448 INLET SERVICE LEAK BEHIND CURB COCK /** 1) MN: A318745 SN: 0004777, *TAP: SIZE: B LOC: 129 FEET FROM P LINE AT DELACHAISE, *MB: CODE: BELN LOC: ON LAUREL 127FT FROM L.S.P.L. DELACHAISE ****/ DOTTIE READY 9-13-18 EXP 10-3-18 | 2018-09-28 | EXCAVATED IN SIDEWALK OVER INLET SERVICE. REMOVE AND REPLACE 3/4 CURB COCK. MADE 3XS5 CUT IN SIDEWALK TIED BACK ONTO LEAD. NEED TO REMOVE LEAD FROM WATER MAIN TO METER BOX.
201800932001 | 2018-05-07 | LEAD | 828 | ROBERT | MAGAZINE | WILK | ML - METER LEAK ACCT#101020-560430 METER#A122550 INLET SERVICE LEAK BEHIND CURB COCK /** 1) MN: A122550 SN: 0021497, *TAP: SIZE: B LOC: 74 FEET FROM P LINE AT MAGAZINE, *MB: CODE: BD13 LOC: 74FT FROM URPL MAGAZINE ****/ DOTTIE READY 8-6-18 EXP 8-26-18 | 2018-08-14 | ARRIVED AT THE ABOVE LOCATION IN THE MUDPLOT IN ROOTS AROUND THE METERBOX. MADE REPAIRS ON LEAD INLET THEN BACKFILLED. REFER TO CREW TO RENEW THE INLET FROM THE CURB TO THE MAIN.
201800933701 | 2018-05-07 | LEAD | 2204 | LAPEYROUSE | N MIRO | WILK | WM LEAK IN SIDEWALK **PLEASE CONTACT UPON ARRIVAL** INLET SERVICE LEAK IN MUDPLOT FLOODING CURB & STREET /** 1) MN: A137480 SN: 0058167, *TAP: SIZE: A LOC: 46 FEET FROM P LINE AT MIRO N, *MB: CODE: CDMN LOC: ON LAPEYROUSE 45' FROM PL OF MIRO N ****/ | 2018-05-22 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201800934601 | 2018-05-07 | LEAD | 1924 | FRANKLIN AV | N PRIEUR | WILK | ML METER LEAK ACCT# 124437-712845 METER# A426694 CUST WANTS BE CALLED WHEN REPAIRS IS MADE INLET SERVICE LEAK CAUSING METER BOX TO OVERFLOW, FOUND OFF LEFT OFF /** 1) MN: A267758 SN: 0045173, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT JOHNSON N, *MB: CODE: D LOC: METER ON FRANKLIN AVE 131.5 FT FROM PL N JOHNSON ****/ | 2018-05-24 | MADE 2 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK FOR ABANDON HOUSE BACKFILLED AREA
201800934801 | 2018-05-07 | LEAD | 1403 | DELERY | N VILLERE | WILK | WM-LEAK ON SIDEWALK INLET SERVICE LEAK IN STREET /** 1) MN: A302281 SN: 0089769, *TAP: SIZE: A LOC: 12 FEET FROM P LINE AT VILLERE N, *MB: CODE: BDN5 LOC: ON DELERY, 12' FROM P.L. NO. VILLERE ****/ | 2018-05-26 | EXCAVATED 5 X 25 ASPHALT STREET CUT RENEW 3/4 INCH INLET SERVICE FROM WATER MAIN TO METER BOX RENEW 3/4 INCH OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILLED JOB WITH RIVERSAND COLDMILL
201800935701 | 2018-05-07 | LEAD/PLASTIC | 1504 | GARDENA DR | PARIS AV | WILK | CUT SERVICE BY ENTERGY *******DAMAGE CLAIM******** C MALLET @ 18:12PM CUT INLET BY ENTERGY ******CUSTOMER OUT OF WATER***** MECH CONSTRUCTION JUDE BAUDOIN (337)322-8948 /** 1) MN: A299990 SN: 0117199, *TAP: SIZE: A LOC: 120 FEET FROM P LINE AT PERLITA, *MB: CODE: ADK7 LOC: LPL 120FT FROM PL PERLITA 7' OUTSIDE PL 3' INSIDE ****/ | 2018-05-07 | EXCAVATED IN MUDPLOT ON INLET LEAK FOR CUSTOMER OUT OF WATER ON LEAD MADE ALL REPAIR TO STOP LEAK ALSO TO RESTORE WATER REFERRED TO ZONE 1 TO REMOVE LEAD
201800939302 | 2018-05-10 | LEAD/PLASTIC | 411 | COUNTRY CLUB DR | BELLAIRE DR | WMRE | ACCT#139426042 METER#C030919 METER BURIED,LOCATE & RAISE /** 1) MN: C021416 SN: 0140135, *TAP: SIZE: C LOC: 210 FEET FROM P LINE AT BELLAIRE DR, *MB: CODE: ADK2 LOC: 210FT FROM UPL BELLAIRE DR 8' OUTSIDE PL 2' INSIDE ****/ /** 1) MN: C021416 SN: 0140135, *TAP: SIZE: C LOC: 210 FEET FROM P LINE AT BELLAIRE DR, *MB: CODE: ADK2 LOC: 210FT FROM UPL BELLAIRE DR 8' OUTSIDE PL 2' INSIDE ****/ | 2018-05-24 | EXCAVATED A 3 X 3 MUDPLOT CUT TO REPAIR INLET SERVICE AND RAISE METER BOX TO GRADE BACKFILLED . NO METER INSIDE METER BOX & FOUND LEAD ON INLET /OUTLET SERVICE
201800939601 | 2018-05-08 | LEAD | 2216 | D"ABADIE | N MIRO | WILK | ML- METER LEAK ACCT#172367-488953 METER#A392120 EXAMINE INLET SERVICE FOR A LEAK, CUSTOMERS PARKING ON METER /** 1) MN: A313658 SN: 0058564, *TAP: SIZE: A LOC: 127 FEET FROM P LINE AT MIRO N, *MB: CODE: ADKN LOC: 127FT FROM PL N MIRO 9' OUTSIDE ****/ | 2018-05-22 | REPLACE INLET AND OUTLET WASHERS AT ABOVE LOCATION
201800943201 | 2018-05-08 | LEAD | 4142 | TOULOUSE | DAVID | WMTLK | ML- METER LEAK ACCT# 146348-515411 MTR# A430793 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: A315310 SN: 0078044, *TAP: SIZE: A LOC: 62 FEET FROM P LINE AT TOULOUSE, *MB: CODE: ADHL LOC: ON TOULOUSE ST 63' FROM PL TOULOUSE ST ****/ | 2018-05-15 | EXCAVATED IN MUDPLOT REPAIR 5/8 STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND TAKE LEAD LINE OUT AT 4144 TOULOUSE TOO JOB REF TO ZONE 1 TO TAKE LEAD LINE OUT FROM WATERMAIN TO METERBOX
201800945601 | 2018-05-08 | LEAD | 2940 | PALMYRA |  | WILK | WM - LEAK ON THE SIDEWALK INLET SERVICE LEAK IN MUDPLOT FLOODING CURB /** 1) MN: A271983 SN: 0028331, *TAP: SIZE: B LOC: 79 FEET FROM P LINE AT PALMYRA, *MB: CODE: BDH6 LOC: ON SO. GAYOSO,79' FROM U.P.L. PALMYRA ****/ | 2018-05-21 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201800948404 | 2018-12-03 | LEAD | 1378 | ANNETTE | N VILLERE | LKST | WATER LEAK CONTINUES AFTER PREVIOUS REPAIR. CONTRACTOR NEEDS THIS REPAIRED BEFORE THEY CAN COMPLETE RESTORATION. ***DO NOT CREATE RESTORATION WORK ORDER AFTER REPAIR.RESTORATION IS ALREADY ASSIGNED TO THE CONTRACTOR.**** /** 1) MN: A233395 SN: 0045211, *TAP: SIZE: A LOC: 65 FEET FROM P LINE AT VILLERE N, *MB: CODE: AD5 LOC: ON ANNETTE,64.5' FROM U.R.P.L. NO. VILLERE ****/ | 2018-12-08 | EXCAVATED IN ASHALT STREET + MADE REPAIR ON 3/4 IN INLET SERVICE LINE COMPACTED BACKFILLED + DRESSED UP AREA
201800949301 | 2018-05-08 | LEAD/PLASTIC | 219 | PELICAN | BOUNY | WILK | PP POOR PRESSURE ACCT# 225906-400362 METER# A398267 INLET UNDERGROUND LEAK CAUSING POOR PRESSURE **1ST AM** 05/11/18 PER L HEBERT SPOKE WITH CUST ***VERY LITTLE TO NO PRESSURE*** ( 2ND *****B 1ST AM***** REQUEST ) /** 1) MN: A308514 SN: 0171560, *TAP: SIZE: A LOC: 144 FEET FROM P LINE AT BOUNY, *MB: CODE: DF1 LOC: RES ON PELICAN AVE 144.5' FROM PL BOUNY 2' OUTSIDE ****/ | 2018-05-22 | BROKE OUT BRICK AND CONCRETE ON SIDEWALK EXAMINED NO LEAK BROKE AND EXCAVATED IN STREET TRACED LEAD LINE ONLY TO EXPOE LEAK UNABLE TO COMPLETE REPAIR DUE TO TIME BARRCADED OFF SITE *************OLD METER INFO********** METER:A398267 FAC:14104028 MAKE:HERSEY READ:231
201800950701 | 2018-05-08 | LEAD/PLASTIC | 4301 | TOURO | MANDOLIN | WILK | MI-LEAK BETWEEN SIDEWALK AND STREET *****CUSTOMER REQUEST CALL UPON ARRIVAL***** ******504-282-0982 MS VERONICA HENRY****** INLET SERVICE LEAK IN MUDPLOT FLOODING CURB & STREET /** 1) MN: C008491 SN: 0117257, *TAP: SIZE: C LOC: 30 FEET FROM P LINE AT MANDOLIN, *MB: CODE: A LOC: ON TOURO, 33' FROM P.L. MANDOLIN, 7' OUTSIDE P.L. ****/ | 2018-05-27 | REPLACED 5/8 CURB COCK TIED INTO LEAD
201800950801 | 2018-05-09 | LEAD/PLASTIC | 3520 | SOMERSET DR | BERKLEY DR | WILK | ML-METER LEAK METER#C025212 ACCT#230184-415111 /** 1) MN: C025212 SN: 0139553, *TAP: SIZE: B LOC: 165 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: CDMN LOC: ON SOMERSET 165FT FROM BERKLEY 7FT OUTSIDE ****/ INLET SERVICE LEAKING INSIDE METER BOX | 2018-06-07 | EXAMINED AREA EXCAVATED METER BOX EXPOSED INLET AND OUTLET OBSERVED LEAK ON OUTLET OBSERVED COPPER ON OUTLET WAS DAMAGE REPAIRED LEAK AND DAMAGEED LINE ON OUTLET RAISED METER TO GRADE BACKFILLED CLEANED AREA LEFT 2CONES ON SITE NEED SAND AND COAL MILL
201800951001 | 2018-05-09 | LEAD | 1208 | 8TH |  | WOLK | LOCATION# 223518 CUSTOMER# 538364 METER# C034848 INSPECTOR DID AN OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION BY WHEEL OF METER......PLEASE REPAIR /** 1) MN: SN: 0008941, *TAP: SIZE: A LOC: 37 FEET FROM P LINE AT CAMP, *MB: CODE: ADK5 LOC: FRONT 30'FRM CAMP ** 2) MN: C013132 SN: 0008941, *TAP: SIZE: C LOC: 39 FEET FROM P LINE AT CAMP, *MB: CODE: CD LOC: ON 8TH 19' FROM P.L. CAMP 8FT OUTSIDE 4'INSIDE ****/ DOTTIE READY 5-15-15 EXP6-4-18 | 2018-05-22 | ARRIVED ON JOB SITE FOR CONSTANT REGISTRATION AND FOUND 3/4 METER COCK LEAKING EXCAVTED IN 5 X 5 MUDPLOT AND EXCHANGE METER COCK WITH NEW METER COCK BACKFILLED AND DRESSED CUT UP.
201800952502 | 2018-05-10 | LEAD/PLASTIC | 15 | SNIPE | MARCONI DR | WMRE | ACCT#108272042 METER#B030519 METER BURIED,LOCATE & RAISE /** 1) MN: B021051 SN: 0103325, *TAP: SIZE: B LOC: 258 FEET FROM P LINE AT MARCONI DR, *MB: CODE: AGL4 LOC: 258FT PL MARCONI DR 5' OUTSIDE ****/ /** 1) MN: B021051 SN: 0103325, *TAP: SIZE: B LOC: 258 FEET FROM P LINE AT MARCONI DR, *MB: CODE: AGL4 LOC: 258FT PL MARCONI DR 5' OUTSIDE ****/ | 2018-05-20 | EXCAVATED AND LOCATED RAISED TO GRADE INSTALL NEW SERVICE FOUND LEAD ON INLET REMOVE LEAD FROM OUTLET JOB CONTINUED TO REPLACE LEAD ON INLET
201800953401 | 2018-05-09 | LEAD/PLASTIC | 6357 | WEST END BL | FREMONT | WMTLK | ML METER LEAK ACCOUNT #136870-508751 METER #A408895 EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN BOX /** 1) MN: A313383 SN: 0091491, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT FREMONT, *MB: CODE: BL2 LOC: ON WEST END BL 73' FROM PL FREMONT ST 3' OUTSIDE P ****/ | 2018-05-27 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 OUTLET SERVICE BACKFILLED AREA
201800955001 | 2018-05-09 | LEAD | 1634 | PIETY | N DERBIGNY | WILK | ML-METER LEAK MTR# A 415864 ACC#161894-432387 INLET SERVICE LEAK NO METER IN BOX, GETTING OFF IN THE DCB 05/16/18 REPAIR OUTLET AND RASIE TO GRADE PER SR#12841266 (AJR) /** 1) MN: A210541 SN: 0100776, *TAP: SIZE: A LOC: 49 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: CE LOC: 49FT FROM PL N DERBIGNY ****/ | 2018-05-25 | EXCAVATED 3 X 2 SIDEWALK MADE REPAIRS ON OUTLET SERVICE LINE AND RAISED METER BOX TO GRADE BACKFILLED AND CLEANED THE AREA
201800955401 | 2018-05-09 | LEAD | 3005 | BIENVILLE | N GAYOSO | WILK | WATER LEAK -INLET SERVICE. LEAK IS NOT VISIBLE (NON-SURFACING). LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. **WATER LEAK IS INTERFERING WITH DPW CATCH BASIN INSTALLATION*** /** 1) MN: A272381 SN: 0055355, *TAP: SIZE: A LOC: 53 FEET FROM P LINE AT GAYOSO N, *MB: CODE: ADL LOC: ON BIENVILLE,47' FROM L.S.P.L. NO. GAYOSO ****/ | 2018-05-27 | EXCAVATED 4 X 8 CONCRETE BASE STREET CUT FOUND LEAK ON 3/4 INCH ABANDON INLET SERVICE MADE REPAIRS ON INELT BACKFILLED JOB WITH RIVERSAND COLDMILL
201800955501 | 2018-05-09 | LEAD | 3604 | PALMYRA | S GENOIS | WMTLK | ML-METER LEAK MTR# A 327085 ACC#133165-709963 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A322778 SN: 0064030, *TAP: SIZE: A LOC: 43 FEET FROM P LINE AT GENOIS S, *MB: CODE: __ LOC: ON PALMYRA 42.5FT FROM GENOIS S ****/ | 2018-06-03 | EXCAVATED IN MUDPLOT. REPAIR 5/8 STOP & WASTE LEAD LINE & REPLACE 5/8 BOTTOM. DRESS UP WITH RIVERSAND REFER TO ZONE 3 TO TAKE LEAD LINE FROM WATER MAIN TO METER BOX
201800956101 | 2018-05-09 | LEAD | 220 | S GAYOSO | CLEVELAND AV | WMTLK | ML-METER LEAK ACCT#113528-531264 METER#A133672 EXAMINE INLET & OUTLET SERVICE FOR A LEAK OVERFLOWING & FLOODING SIDEWALK /** 1) MN: A133672 SN: 0048838, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT CLEVELAND AVE, *MB: CODE: AFL7 LOC: IN GARDEN AT PLON S GAYOSO 149.6' FROM URPL CLEVEL ****/ | 2018-05-27 | EXCAVATED 4 X 6 MUD PLOT IN TREE ROOTS BY HAND FOUND LEAK ON 5/8 INCH OUTLET SERVICE RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILLED JOB WITH RIVERSAND CLEANED UP WORK AREA
201800956201 | 2018-05-09 | LEAD | 1705 | PAULINE | N ROMAN | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK ***CARS PARKING ON METER*** /** 1) MN: A291120 SN: 0147456, *TAP: SIZE: C LOC: 54 FEET FROM P LINE AT ROMAN N, *MB: CODE: ADK LOC: 52' PL N ROMAN 7' OUTSIDE ****/ | 2018-05-25 | EXCAVATED 3 X 3 MUD PLOT ALSO MUD PLOT AT PROPERTY RENEWED OUTLET TO PROPERTY BACKFILLED AND CLEANED THE AREA
201800958001 | 2018-05-09 | LEAD | 2323 | LIZARDI | TONTI | WILK | WM- LEAK ON THE SIDEWALK INLET SERVICE LEAK @ CURB NEXT TO ABOVE ADDRESS /** 1) MN: A157416 SN: 0126794, *TAP: SIZE: A LOC: 176 FEET FROM P LINE AT TONTI, *MB: CODE: ADL1 LOC: ON LIZARDI 178FT FROM PL TONTI 6FT INSIDE CURB ****/ | 2018-06-04 | EXCAVATED IN MUD PLOT AND REPLACED 1 INCH CURB COCK FOR ABANDON LOT BACKFILLED AREA
201800961301 | 2018-05-10 | LEAD | 331 | ROYAL | CONTI | WILK | LOCATIONID#105413-527266 METER#A355894 BLEEDER LEAK /** 1) MN: A132931 SN: 0002034, *TAP: SIZE: A LOC: 122 FEET FROM P LINE AT CONTI, *MB: CODE: AEW LOC: ****/ | 2018-06-18 | EXCAVATED IN FLAGSTONE SIDEWALK + REPLACED 5/8 INCH CURB COCK NEAR N.O.P.S.I VAULT BACKFILLED + DRESSED UP AREA
201800962501 | 2018-05-10 | LEAD | 932 | LIZARDI | BURGUNDY | WMTLK | ML- METER LEAK ACCT#142413-424919 METER# A417292 EXAMINE INLET & OUTLET SERVICE FOR A LEAK CARS ROLLING OVER METER BOX /** 1) MN: A262502 SN: 0073474, *TAP: SIZE: B LOC: 239 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CDL LOC: ON LIZARDI 238FT FROM PL BURGUNDY ****/ | 2018-05-26 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201800963202 | 2018-06-05 | LEAD | 123 | CARONDELET |  | WILK | EXAMINED AREA AT ABOVE LOCATION NEED BACK HOE TO MAKEREPAIR IN STREET REFER BACK TO ZONE 4 FOR REAPIRS OWNER SAYS BEST TIME FOR REPAIR IS AFTER 2 PM ANYDAY /** 1) MN: 000000 SN: 0002313, *TAP: SIZE: D LOC: 140 FEET FROM P LINE AT CANAL, *MB: CODE: AD LOC: ON CARONDELET 190FT FROM CANAL 8FT OUTSIDE ** 2) MN: SN: 0000000, *TAP: SIZE: E LOC: 186 FEET FROM P LINE AT CANAL, *MB: CODE: __ LOC: 168' P.L. CANAL ****/ | 2018-06-12 | EXCAVATED IN ASPHALT STREET + REPLACED 1 1/2 INCH CURB COCK + REPLACED 1 1/2 WATER METER COMPACTED BACKFILL + DRESSED UP AREA **********OLD METER INFO*********** METER:D006627 FAC:46277915 MAKE:SENSUS READ:75658
201800963501 | 2018-05-10 | LEAD | 2327 | PAULINE |  | WILK | MI- LEAK AT THE SIDEWALK INLET SERVICE LEAK INSIDE METER BOX NEAR TREE /** 1) MN: A343592 SN: 0095139, *TAP: SIZE: A LOC: 198 FEET FROM P LINE AT NO. TONTI, *MB: CODE: AD LOC: ON PAULINE, 196.5' FROM P.L. NO. TONTI, 8' OUTSIDE ****/ | 2018-05-25 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201800964701 | 2018-05-10 | LEAD | 1662 | ABUNDANCE | REPUBLIC | WILK | **********PICK UP********** EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A258839 SN: 0078873, *TAP: SIZE: B LOC: 129 FEET FROM P LINE AT BRUXELLES, *MB: CODE: BDK2 LOC: 129' P.L. BRUXELLES ****/ | 2018-05-24 | EXCAVATED 9 X 2 SIDEWALK + DRIVEWAY CUT RENEWED OUTLET TO PROPERTY BACKFILLED AND CLEANED THE AREA
201800964801 | 2018-05-10 | LEAD/PLASTIC | 169 | PINEWOOD CT | WALL BL | WILK | ML - METER LEAK ACCT#235941-702705 METER#A254659 INLET SERVICE LEAK IN THE MUD PLOT FLOODING THE CURB /** 1) MN: A241792 SN: 0164628, *TAP: SIZE: A LOC: 11 FEET FROM P LINE AT CYPRESS ACRES DR, *MB: CODE: OOO LOC: ON PINEWOOD 11FT FROM PL CYPRESS ACRES 9FT OUTS ****/ | 2018-06-01 | EXAMINED AREA EXCAVATED METER EXPOSED LEAK OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK BACKFILLED NEED SAND FOR DRESS UP CLEANED AREA LEFT CONE AND BOARD ON MUD PLOT
201800965001 | 2018-05-10 | LEAD/PLASTIC | 411 | WEBSTER | ANNUNCIATION | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A292367 SN: 0029444, *TAP: SIZE: A LOC: 99 FEET FROM P LINE AT ANNUNCIATION, *MB: CODE: CFLM LOC: ON WEBSTER 98.4' FROM SPL ANNUNCIATION ST ****/ DOTTIE READY 5-16-18 EXP 6-5-18 | 2018-05-29 | ARRIVED ON JOB SITE FOR METER LEAK MADE A 5 X 5 CUT ON SIDEWALK AND EXCAVTED DOWN TO METEER COCK AND EXCHANGE COCK WITH NEW METER COCK AND MADE REPAIR TIED ONTO LEAD NEED TO BE REMOVE FROM WATER MAIN WITH PLASTIC .BACKFILLED AND DRESSED CUT.
201800965401 | 2018-05-10 | LEAD | 2023 | ALMONASTER AV | N JOHNSON | WOLK | MI - LEAK ON SIDE WALK IN FRONT OF PROPERTY NEXT DOOR CHANGED FROM 2013 ALMONASTER AV EXAMINE OUTLET SERVICE UP TO PROPERTY LINE FOR A LEAK /** 1) MN: A345195 SN: 0095597, *TAP: SIZE: __ LOC: 150 FEET FROM P LINE AT NO. JOHNSON, *MB: CODE: ADK2 LOC: ON ALMONASTER AVE., 152'F ROM P.L. NO. JOHNSON, 9' ** 2) MN: A343386 SN: 0073188, *TAP: SIZE: A LOC: 161 FEET FROM P LINE AT GALVEZ N, *MB: CODE: CDN LOC: 147' P/L N JOHNSON 10' OUTSIDE 2' INSIDE CURB ****/ | 2018-05-25 | EXCAVATED 2 X 2 MUD PLOT AT PROPERTY FOUND LEAK ON PROPERTY REFER BACK TO PROPERTY OWNER THAT EXIST ON PROPERTY
201800966401 | 2018-05-10 | LEAD | 4011 | CAMP |  | WMTLK | LOCATION ID-125068 MTR-A298105 LEAK IN MTR BOX/AREA SATURATED EXAMINE INLET/OUTLET SERVICE FOR LEAK AREA FLOODED /** 1) MN: A298105 SN: 0046973, *TAP: SIZE: A LOC: 84 FEET FROM P LINE AT CONSTANTINOPLE, *MB: CODE: CDLN LOC: ON CAMP,84.6' FROM U.P.L. CONSTANTINOPLE ****/ | 2018-05-29 | EXCAVATED IN MUDPLOT ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND REFERRE TO ZONE 3 TO REMOVE LEAD
201800967501 | 2018-05-10 | LEAD/PLASTIC | 2736 | SOMERSET DR | ANSON | WILK | ********************PICKUP*************** INLET SERVICE LEAK IN GRASSY AREA BY METER AREA SATURATED LEFT ONE (1) CONE /** 1) MN: B026691 SN: 0123959, *TAP: SIZE: B LOC: 589 FEET FROM P LINE AT ANSON, *MB: CODE: CDM2 LOC: 589'FROM P L ANSON ****/ | 2018-06-07 | EXAMINED AREA EXCAVATED INLET SERVICE OBSERVED LEAK ON INLET MADE REPAIRS BACKFILLED CLEANED AREA NEED SAND FOR DRESS UP
201800970001 | 2018-05-11 | LEAD | 1011 | FRANKLIN AV |  | WOLK | /** 1) MN: A298444 SN: 0057687, *TAP: SIZE: A LOC: 68 FEET FROM P LINE AT RAMPART, *MB: CODE: BEK LOC: 68FT FROM LSPL RAMPART ON FRANKLIN ****/ | 2018-05-10 | EXAMINED JOB AT ABOVE LOCATION AND FOUND CHOKED METER SET 5/8 INCH METER AT ABOVE LOCATION
201800970201 | 2018-05-11 | LEAD | 6064 | PATTON |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 118324-564880 METER NUMBER - A310665 BAD BLEEDER VALVE, FLOODING SIDEWALK AND GRASS /** 1) MN: A248058 SN: 0027814, *TAP: SIZE: __ LOC: 109 FEET FROM P LINE AT WEBSTER, *MB: CODE: BFLM LOC: 109' P.L. WEBSTER ****/ DOTTIE READY 9-10-18 EXP 9-30-18 | 2018-09-19 | ARRIVED AT ABOVE LOCATION, FOUND LEAK ON 5/8 INLET SERVICE LINE AND MADE REPAIRS TO STOP LEAK. BACKFILLED , CLEANED UP AND WASHED DOWNJOBSITE TO COMPLETE. LEAD INLET
201800971001 | 2018-05-11 | LEAD | 1436 | ARTS | ROBERTSON | WILK | ML-METER LEAK*** ACCT#302353-431684 METER #A293309 EXAMINE INLET SERVICE FOR A LEAK, CARS PARKING ON METER BOX /** 1) MN: A341279 SN: 0052991, *TAP: SIZE: A LOC: 274 FEET FROM P LINE AT VILLERE N, *MB: CODE: AD1 LOC: ON ARTS ST 273.5' FROM PL N VILLERE ****/ | 2018-05-15 | EXCAVATED IN MUDPLOT ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND .REFER TO ZONE 4 TO REMOVE LEAD.
201800971501 | 2018-05-11 | LEAD | 621 | ANDRY | CHARTRES | WILK | ML - METER LEAK MTR# A417280 ACCT # 161867-424997 EXAMINE INLET SERVICE FOR A LEAK IN METER BOX /** 1) MN: A285027 SN: 0100615, *TAP: SIZE: A LOC: 99 FEET FROM P LINE AT ROYAL, *MB: CODE: ADK1 LOC: 109FT PL ROYAL 3' OUTSIDE 7' INSIDE CURB ****/ | 2018-05-29 | EXCAVATED 4 X 2 MUD PLOT TRENCH RENEWED OUTLET O PROPERTY BACKFILLED AND CLEANED THE AREA **********REFER BACK TO ZONE 4 TO REMOVE FROM STREET**********
201800971601 | 2018-05-11 | LEAD/PLASTIC | 2245 | BECK | PRANCER | WILK | MI-LEAK IN STREET ***** CUST STATES THAT THERE ARE LEAKS ALL ALONG THE BLOCK. INLET SERVICE LEAK IN CONCRETE STREET /** 1) MN: A308680 SN: 0136401, *TAP: SIZE: B LOC: 106 FEET FROM P LINE AT PRANCER, *MB: CODE: CD LOC: ON BECK 106' FROM PL PRANCER 7' OUTSIDE PL 3' INSI ****/ | 2018-06-21 | BROKE THE STREET AND EXCAVATED ON THE WATERMAIN AND REPAIR THE INLET SERVICE LEAK THEN WE BACKFILL JOB SITE BUT HAVE TO COME BACK AND CLEAN UP JOB SITE
201800972101 | 2018-05-11 | LEAD/PLASTIC | 4665 | PERILLI DR | HAMMOND | WILK | WM- LEAK IN THE STREET INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A140063 SN: 0152454, *TAP: SIZE: B LOC: 536 FEET FROM P LINE AT GRANT, *MB: CODE: BDM5 LOC: ON PERRELLI 515' FROM GRANT 10FT OUTSIDE ****/ | 2018-05-27 | EXAMINED AREA EXCAVATED IN MUD PLOT OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK RAISED TO GRADE REPLACED BROKEN METER BOX WITH NEW COMPLETE SET UP BACKFILLED AND CLEANED AREA
201800973101 | 2018-05-11 | LEAD | 1538 | PAINTERS |  | WILK | WM LEAK BETWEEN STREET AND CURB INLET SERVICE LEAK @ CORNER FROM ABOVE ADDRESS FLOODING CUB & STREET /** 1) MN: A329412 SN: 0059141, *TAP: SIZE: A LOC: 17 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: OOO LOC: MTR ON PAINTERS 17FT FRM PL N CLAIBORNE 4FT INSD ****/ | 2018-05-24 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 1 1/2 CONCTROLLING LINE BACKFILLED AREA
201800973201 | 2018-05-11 | LEAD/PLASTIC | 4726 | DEMONTLUZIN |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 135288 - 478363 METER NUMBER - A126074 INLET SERVICE LEAK /** 1) MN: A126074 SN: 0082631, *TAP: SIZE: A LOC: 108 FEET FROM P LINE AT CARNOT, *MB: CODE: ADK5 LOC: ON DEMONTLUZIN, 109' FROM U.S.P.L. CARNOT ****/ | 2018-05-13 | EXCAVATED IN MUDPLOT BY HAND TO REPAIR LEAK ON 3/4 LEAD ON INLET AND RAISED METER TO GRADE.PLASTIC FOUND ON OUTLET LEFT LEAD ON INLET. 4X4 MUD PLOT CUT
201800973801 | 2018-05-11 | LEAD | 3146 | N CLAIBORNE AV | CLOUET | WILK | WM-LEAK BETWEEN SIDEWALK & STREET INLET SERVICE LEAK IN MUDPLOT FLOODING CURB AND STREET /** 1) MN: A266250 SN: 0097081, *TAP: SIZE: B LOC: 330 FEET FROM P LINE AT CLOUET, *MB: CODE: BD LOC: 367' FROM PL CLOUET 9' OUTSIDE PL 1' INSIDE CURB ****/ | 2018-05-31 | REMOVE JUMPER FROM INSIDE OF METER BOX. JOB COMPLETE
201800974101 | 2018-05-11 | LEAD | 722 | CONSTANTINOPLE | LAUREL | WILK | ML - METER LEAK METER # A280870 ACCT # 113694-557129 INLET SERVICE LEAK AT METER /** 1) MN: A261945 SN: 0043887, *TAP: SIZE: A LOC: 149 FEET FROM P LINE AT LAUREL, *MB: CODE: AGW LOC: BY FENCE 148' P.L. LAUREL ****/ | 2018-05-15 | EXCAVATED IN MUDPLOT REPAIR 5/8 STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND REF TO ZONE 3 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METERBOX
201800978801 | 2018-05-12 | LEAD | 5523 | N GALVEZ | CAFFIN AV | WILK | MI- METER BOX LEAKING ***************CSM IS DOWN*************************88 INLET SERVICE LEAK IN THE MUD PLOT FLOODING THE CURB /** 1) MN: C019691 SN: 0132211, *TAP: SIZE: C LOC: 113 FEET FROM P LINE AT CAFFIN AVE, *MB: CODE: EHL1 LOC: RES ON GALVEZ 113' FROM PL CAFFIN AVE 7' OUTSIDE P ****/ | 2018-05-23 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR ON INLET SRVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA JOB CONTINUED
201800985101 | 2018-05-14 | LEAD/PLASTIC | 3300 | LAMARQUE | HORACE | WOLK | MI CHANGE LEAD WHIP METER# N/A ***********S.SLACK @ 9:25AM************ CHANGE LEAD WHIP, CUSTOMER OUT OF WATER HOLE EXPOSED /** 1) MN: SN: 0133338, *TAP: SIZE: A LOC: 35 FEET FROM P LINE AT LAMARQUE, *MB: CODE: AH LOC: ON HORACE, 35' FROM P.L. LAMARQUE, 5' OUTSIDE ****/ | 2018-05-14 | EXCAVATED ON THE OUTLET SERVICE AND RENEW THE OUTLWET AND RAISE METERBOX TO GRADE THEN WE BACKFILL AND CLEAN JOB SITE
201800989401 | 2018-05-14 | LEAD | 1530 | N ROBERTSON |  | WILK | ML- METER LEAK ACCT#302769-486543 METER#A426455 EXAMINE INLET SERVICE FOR LEAK CARS PARKING ON TOP METER /** 1) MN: A320756 SN: 0052257, *TAP: SIZE: A LOC: 106 FEET FROM P LINE AT LAHARPE, *MB: CODE: CDLN LOC: ON N ROBERTSON 107FT FROM URPL LAHARPE ****/ | 2018-06-05 | REPLACED BOTH INLET OUTLET WASHERS AT ABOVE LOCATION
201800991101 | 2018-05-14 | LEAD | 1634 | BARTHOLOMEW | N DERBIGNY | WILK | MI LEAK IN THE STREET INLET SERVICE LEAK IN FRONT OF VACANT LOT IN STREET FLOODING AREA 05/21/18 UPGRADED TO "B" LEAVE IN SYSTEM PER INSP K GRIFFIN (NLD) /** 1) MN: A309099 SN: 0108798, *TAP: SIZE: A LOC: 230 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: BEK1 LOC: 230' P.L. N CLAIBORNE AVE ****/ | 2018-05-25 | MADE 8 X 8 CUT IN BLACK TOP STREET AND MADE REPAIRS ON 3/4 INCH INLET SERVICE FOR ABANDON LOT BACKFILLED AREA
201800991501 | 2018-05-14 | LEAD/PLASTIC | 2608-10 | CONSTANCE | 4TH | WILK | MI - LEAK ON SIDEWALK **DPW IS AT ADDRESS TO MAKE SIDEWALK REPAIRS AND DISCOVERED LEAK** INLET SERVICE LEAK @ SIDEWALK INTERFERRING WITH DEPARTMENT OF PUBLIC WORKS REPAIRS /** AT 2608: 1) MN: A315289 SN: 0028070, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT THIRD, *MB: CODE: BEN3 LOC: BET THIRD/FOURTH 81FT. FRM PL THIRD ** AT 2610: 2) MN: A314072 SN: 0028070, *TAP: SIZE: B LOC: 108 FEET FROM P LINE AT THIRD, *MB: CODE: AEN3 LOC: BET THIRD/FOURTH 83FT. FRM PL THIRD ****/ | 2018-06-08 | ARRIVED ON JOB SITE EXAMINE AREA VFOR LEAK EXCAVATED IN MUD PLOT BY HAND MADE WORK SITE
201800991901 | 2018-05-14 | LEAD/PLASTIC | 3173 | POTOMAC | OREGON | WILK | MI- LEAK ON SIDEWALK *** CUST STATED LEAK RUINING MATERIALS BUILDING HOME**** INLET SERVICE LEAK @ SIDEWALK LEAK LOCATED @ ABOVE ADDRESS SIDEWALK FLOODED /** 1) MN: A216962 SN: 0270036, *TAP: SIZE: C LOC: 4 FEET FROM P LINE AT POTOMAC, *MB: CODE: AD23 LOC: ON ORGEON 4FT FR5OM PLOTOMAC 4FT OUTSIDE ****/ | 2018-06-01 | EXAMINED AREA OBSERVED LEAKING COMING FROM TWO LOCATION EXCAVATED THROUG SAND STOPED LEAK ON ABANDON SERVICE PUMP DOWN WATER AND EXCAVATED AT 1 SERVICE AND REPAIRED LEAK ON INLET SERVICE BACKFILLED AND CLEANED SITE SAND NEED AT METER FOR BACKFILLING
201800992101 | 2018-05-14 | LEAD/PLASTIC | 1752-54 | SHIRLEY DR | VESPASIAN BL | WILK | ML-METER LEAK METER#A403167 ACCT#226184-405294 **********1ST AM********* INLET SERVICE LEAK INSIDE METER BOX FLOODING DRIVEWAY NO ANSWER BY DOOR /** AT 1752: 1) MN: A305928 SN: 0134007, *TAP: SIZE: C LOC: 357 FEET FROM P LINE AT COPERNICUS, *MB: CODE: AD25 LOC: ON SHIRLEY D 383.5' FROM PL COPERNICUS 6' OUTSIDE ****/ | 2018-05-15 | CUT OUT METER BOX WITH AIR GUN STARTED EXCAVATING BY HAND AND FOUND LED ON Y=THE OUTLET CUT BACK FUTHER WITH AIR GUN TO REMOVE LED AT PROPERTY RAN INTO TREE ROOTS GOT EXCAVATOR TO DIG A LITTLE RAN RAN PLASTIC LINE FROM PROPERTY TO METER BOX AND RAISED METER BOX TO GRADE BACKFILLED WITH SAND AND COLD MILL
201800992201 | 2018-05-14 | LEAD | 2671 | N DORGENOIS | ARTS | WILK | ML-METER LEAK INLET SERVICE LEAK CAUSING METER BOX TO OVERFLOW INTEFERRING WITH CONTRACTORS' WORK /** 1) MN: A257394 SN: 0106212, *TAP: SIZE: A LOC: 161 FEET FROM P LINE AT ARTS, *MB: CODE: ADMK LOC: 161FT PL ARTS - 9' OUTSIDE ****/ | 2018-05-30 | EXCAVATED 3 X 2 DRIVEWAY CUT ALSO 4 X 2 MUD PLOT RELOCATED METER BOX FROM TO MUD PLOT AND METER BOX IS UP TO GRADE BACKFILLED AND CLEANED THE AREA. REFER BACK TO ZONE 4 TO HAVE LEAD REMOVED FROM STREET
201800993901 | 2018-05-15 | LEAD/PLASTIC | 6527 | PAULINE DR | FRANKFORT | WILK | WM LEAK IN SIDEWALK **PLEASE KNOCK ON DOOR WHEN YOU ARRIVE** INLET SERVICE LEAK IN MUDPLOT /** 1) MN: B032043 SN: 0119146, *TAP: SIZE: B LOC: 198 FEET FROM P LINE AT FRANKFORT, *MB: CODE: CDN LOC: ON PAULINE 198FT FROM FRANKFORT ****/ | 2018-05-18 | EXCAVATED IN MUDPLOT BY HAND TO REPAIR LEAK ON 3/4 HANDWHEEL. PLASTIC FOUND ON INLET AND LEAD FOUND ON OUTLET. (DNR LEAD) 4 X 3 MUDPLOT CUT
201800994901 | 2018-05-15 | LEAD | 4462 | LAFAYE |  | WOLK | LOCATION: 135443 MTR# A 430515 INLET/OUTLET TOO FAR APART, PLEASE REPAIR ASAP. CUSTOMER W/ BABY HOME WAITING ON WATER ************J.WHITE @ 12:37PM*********** BROKEN METER BOX BOTTOM, CAUSING INLET AND OUTLET TO NOT LINE UP CUSTOMER OUT OF WATER /** 1) MN: A345076 SN: 0081994, *TAP: SIZE: A LOC: 497 FEET FROM P LINE AT GENTILLY BLVD, *MB: CODE: AD LOC: ON LAFAYE ST 500' FROM PL GENTILLY BLVD ****/ | 2018-05-15 | EXCAVATED IN MUDPLOT BY HAND TO REPLACE BROKE METER BTTOM AND ASLO RAISED METER TO GRAD LEAD LINE ON INLET AND OUT SERVICE 3X4 CUT IN MUD PLOT.
201800995801 | 2018-05-15 | LEAD/PLASTIC | 4144 | TOULOUSE | DAVID | WILK | METER#A356047 *********PICKUP JOB********* INLET SERVICE LEAK /** 1) MN: A228737 SN: 0078044, *TAP: SIZE: B LOC: 64 FEET FROM P LINE AT TOULOUSE, *MB: CODE: ADHL LOC: 1ST METER SIDE ST ON DAVID 64' P.L. TOULOUSE ****/ | 2018-05-15 | EXCAVATED IN MUDPLOT REPAIR 5/8 STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND...JOB COMPLETE
201800997301 | 2018-05-15 | LEAD | 1302 | MARENGO |  | WILK | INLET LEAK /** 1) MN: B022945 SN: 0003536, *TAP: SIZE: B LOC: 90 FEET FROM P LINE AT MARENGO, *MB: CODE: ADH2 LOC: 2ND METER ON PERRIER 87FT FROM PL MARENGO ** 2) MN: A308593 SN: 0003536, *TAP: SIZE: B LOC: 87 FEET FROM P LINE AT MARENGO, *MB: CODE: ADH2 LOC: ON MARENGO 87' FROM PL MARENGO 8' OUTSIDE PL 2' IN ****/ | 2018-05-15 | EXCAVATED IN MUDPLOT REPAIR 3/4 STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND JOB REF TO ZONE 3 TO TAKE LEAD LINE OUT FROM WATER MAIN TO BOTH METERBOXS
201800998501 | 2018-05-16 | LEAD | 821 | ST PETER | DAUPHINE | WILK | ACCT# 105535-527851 MTR# A325588 INSPECTOR FOUND METER LEAKING INSIDE CURBCOCK /** 1) MN: A325588 SN: 0012253, *TAP: SIZE: B LOC: 130 FEET FROM P LINE AT DAUPHINE, *MB: CODE: AENO LOC: ON ST. PETER,130' FROM P.L. DAUPHINE ****/ | 2018-06-12 | EXCAVATED 5 X 3 BRICK SIDEWALK REPLACED 5/8 INCH METER COCK AND RENEWED OUTLET TO PROPERTY BACKFILL AND CLEANED THE AREA
201800999901 | 2018-05-16 | LEAD | 926 | N BROAD |  | WMTBG | LOCATION: 177472 MTR# A 417279 PER INSP L. UDEBOR, METER BOX BELOW GRADE RAISE METER TO PROPER GRADE /** 1) MN: A224808 SN: 0022842, *TAP: SIZE: A LOC: 166 FEET FROM P LINE AT ST PHILIP, *MB: CODE: C7 LOC: ON N BROAD 162' FROM PL ST PHILIP 3' OUTSIDE PL 12 ****/ | 2018-05-30 | REPLACE UPPER METER BOX CASING AT ABOVE LOCATION
201801000201 | 2018-05-16 | LEAD | 1815 | GOV NICHOLLS |  | WOLK | LOCATION: 124276 MTR# A 299799 PER INSP L. UDEBOR, PLEASE REPAIR BROKEN WHEEL AND CHANGE METER BROKEN HANDWHEEL ALSO CHANGE METER /** 1) MN: A299799 SN: 0045174, *TAP: SIZE: A LOC: 121 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: AFKL LOC: 181FT FROM LRPL N ROMAN ****/ | 2018-06-01 | REPLACED 5/8 INCH HANDWHEEL IN METER BOX + REPLACED 5/8 INCH WATER METER OLD METER INFO: A299799 FACT: 51229758 MAKE: SENSUS RAD:21027
201801001401 | 2018-05-16 | LEAD | 2235 | N MIRO |  | WILK | WM - LEAK ON THE SIDEWALK EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A135654 SN: 0102741, *TAP: SIZE: A LOC: 35 FEET FROM P LINE AT MIRO N, *MB: CODE: CDHL LOC: ON MARIGNY, 35' FROM P.L. NO. MIRO, 7.5' OUTSIDE ****/ | 2018-05-30 | EXCAVATED 4 X 2 SIDEWALK ALSO 2 X 2 MUD PLOT RELOCATED METER BOX TO SIDEWALK + RENEWED OUTLET TO PROPERTY BACKFILLED AND CLEANED THE AREA
201801002501 | 2018-05-16 | LEAD | 5964 | PATTON | STATE STREET DR | WILK | ML- METER LEAK MTR# A275304 ACCT# 152990-565512 INLET SERVICE LEAK BEHIND CURB COCK SLIGHTLY FLOODING THE GUTTER BOTTOM /** 1) MN: A275304 SN: 0050644, *TAP: SIZE: B LOC: 43 FEET FROM P LINE AT STATE, *MB: CODE: CDM LOC: 44FT FROM PL STATE ****/ DOTTIE READY 9-10-18 EXP 9-30-18 | 2018-09-19 | ARRIVED AT ABOVE LOCATION, EXAMINED, AND FOUND LEAK ON 5/8 INLET SERVICE LINE. MADE REPAIR TO STOP LEAK, BACKFILLED, CLEANED UO AND WASHED DOWN AREA TO COMPLETE JOB. LEAD INLET
201801002901 | 2018-05-16 | LEAD | 1018 | ANDRY |  | WMRE | INSPECTOR L UDUEBOR STATES HE IS UNABLE TO LOCATE SERVICE. HE STATED "ROCKS ALL OVER, USED METAL DETECTOR". PLEASE LOCATE AND CHANGE METER A413907 LOC ID 129005 LOCATE, RAISE TO GRADE AND CHANGE METER /** 1) MN: A236898 SN: 0061804, *TAP: SIZE: A LOC: 156 FEET FROM P LINE AT RAMPART N, *MB: CODE: C LOC: ON ANDRY 159FT FROM USPL N RAMPART 2FT INSIDE CURB ****/ | 2018-05-23 | FOUND METER BOX 9 FT FROM THE CURVE CUSTOMER HAS LIMESTONE LAID ON TOP OF METER REMOVE LIMESTONE FROM AROUND METER METER IS UP TO GRADE IN SIDEWALK ALREADY
201801005401 | 2018-05-16 | LEAD/PLASTIC | 1661 | NIE PK | GEN MEYER AV | WILK | ML - METER LEAK ACCT#231659-416708 METER#C031444 ((CUSTOMER STATED WATER IS FLOWING OUT)) INLET SERVICE LEAK @ CURB /** 1) MN: C023263 SN: 0143847, *TAP: SIZE: C LOC: 492 FEET FROM P LINE AT PATTERSON RD, *MB: CODE: ADM2 LOC: ON NIE PK., 61' FROM D.P.L. PATTERSON RD., 1' IN- ****/ | 2018-06-13 | EXAMINED AREA OBSERVED LEAK ON INLET SERVICE EXCAVATED METER BOX EXPOSED INLET AND OUTLET EXCAVATED AROUND GAS LINE REPAIRED LEAK REMOVED OLD METER BOX BROKEN REPLACED WITH NEW BACKFILLED CLEANED AREA
201801007801 | 2018-05-17 | LEAD/PLASTIC | 1017 | BELLEVILLE |  | WMTLK | NO METER IN BOX LEAKING FROM THE CURB COCK LOCATON #224611 EXAMINE INLET AND OUTLET SERVICE FOR LEAK ON SIDEWALK /** 1) MN: A314028 SN: 0061084, *TAP: SIZE: A LOC: 155 FEET FROM P LINE AT NEWTON, *MB: CODE: CD LOC: ON BELLEVILLE 153FT FROM NEWTON ****/ | 2018-06-06 | EXAMINED AREA BROKE OUT CONCRETE SIDEWALK EXPOSED LEAK ON LEAD INLET SERVICE MADE REPAIRS BACKFILLED NEED SAND AND COAL MILL LEFT CONE AT SITE CLEANED AREA LEFT ROCK NEED PICK UP
201801008201 | 2018-05-17 | LEAD | 5431 | FRANKLIN AV |  | WMTLK | LOCATION ID-170102 MTR-B033759 BAD METER LEAK/METER BOX OVER FLOWING/AREA SATURATE EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: B027768 SN: 0112692, *TAP: SIZE: B LOC: 218 FEET FROM P LINE AT MITHRA, *MB: CODE: BDM5 LOC: ON FRANKLIN AVE 218' FROM PL MITHRA 8' OUTSIDE PL ****/ | 2018-05-29 | EXCAVATED IN MUDPLOT. REPAIR 3/4 STOP & WASTE LEAD LINE . DRESS UP WITH RIVERSAND.JOB REFER TO ZONE 5 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201801009001 | 2018-05-17 | LEAD | 2114 | ALLEN |  | WILK | L UDUEBOR STATES "CASING OVER CURB COCK, UNABLE TO BREAK CASING", UNABLE TO CHANGE METER. PLEASE REPAIR AND CHANGE METER C034875 LOC ID 190946 METER BOX SHIFTED OVER CURB COCK, ALSO RAISE METER TO GRADE /** 1) MN: C012516 SN: 0149310, *TAP: SIZE: C LOC: 173 FEET FROM P LINE AT GALVEZ N, *MB: CODE: BDK LOC: 171FT PL N GALVEZ 7FT OUTSIDE P/L ****/ | 2018-05-23 | EXCAVATED 4 X 4 LIMESTONES DRIVEWAY RAISED METER BOX UP TO GRADE
201801009401 | 2018-05-17 | LEAD | 1222 | MAZANT | MARAIS | WMTLK | MI- LEAK IN THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-05-22 | REPLACED DAMAGE METER AND WASHERS ***************OLD METER INFO********** METER:A369404 FAC:72632281 MAKE:SENSUS READ:8378
201801012701 | 2018-05-18 | LEAD/PLASTIC | 309 | RIVER OAKS DR | COPERNICUS | WILK | ML- METER LEAK ACCT# 227839-416088 MTR# A120527 06/09/18 EXAMINE INLET & OUTLET SERVICE FOR A LEAK @ THE SIDEWALK FLOODING CURB GETTING OFF IN THE DCB, 1 CONE LEFT FOR PROTECTION (KSW) /** 1) MN: A120527 SN: 0117782, *TAP: SIZE: B LOC: 251 FEET FROM P LINE AT COPERNICUS, *MB: CODE: CDL LOC: ON RIVER OAKS DR., 251' FROM P.L. COPERNICUS, 7' ****/ INLET SERVICE LEAKING IN MUD PLOT | 2018-06-14 | EXAMINED AREA EXCAVATED METER BOX OBSERVED LEAK ON INLET SERVICE RENEWED BRITILE LINE TO PROPERTY ON OUTLET REPLACED BROKEN METER BOX RAISED METER TO GRADE BACKFILLED DRESSED WITH SAND CLEANED SITE
201801013601 | 2018-05-18 | LEAD | 1425 | ST ROCH AV | N ROBERTSON | WILK | ML- METER LEAK ACCT# 128274-481875 MTR# A311492 INLET SERVICE LEAK IN BOX /** 1) MN: A238886 SN: 0055257, *TAP: SIZE: A LOC: 166 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: CEL LOC: ON ST ROCH AVE 167.5' FROM LRPL N ROBERTSON ****/ | 2018-06-08 | EXCAVATED 4 X 2 SIDEWALK CUT RENEWED OUTLET TO PROPERTY AND REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILL AND CLEANED THE AREA (MADE ADDITIONAL 2X2 SIDEWALK TO FOUND LEAK FURTHER BACK) REFER BACK TO ZONE 4 TO REMOVE LEAD FROM STREET
201801014601 | 2018-05-18 | LEAD/PLASTIC | 2460 | HYMAN PL |  | WMBK | MI- BROKEN METER BOX CASE DUE TO POSSIBLE TREE ROOTS METER # A270069 BROKEN METER BOX CASING BY TREE ROOTS LEFT 1 CONE FOR SAFTY, ALSO SPOKE WITH CUSTOMER /** 1) MN: A270069 SN: 0134420, *TAP: SIZE: B LOC: 443 FEET FROM P LINE AT GALLATIN, *MB: CODE: CDL LOC: 443FT FROM P.L. GALLATIN ****/ | 2018-06-13 | ARRIVED ON JOB SITE EXAMINE GROKEN METER BOX CASING IN TREE ROOTS EXCAVATED IN MUD PLOT AND TREE ROOTS BY HAND REROUTED METER BOX OUT OF TREE ROOTS SET UP NEW METER BOX COMPLETE RAN PLASTIC FROM METER BOX TO PROPERTY BACKFILLED DRESS UP WORK SITE
201801015701 | 2018-05-18 | LEAD | 3710 | DRYADES |  | WILK | LOCATION ID-120616 MTR-A362817 POOR PREASSURE AND LEAK IN THE STREET **********L THOMPSON 13:45********** INLET SERVICE LEAK IN AN ASPHALT STREET NEAR GUTTER FLOODING AREA CAUSING CUSTOMER TO HAVE POOR PRESSURE /** 1) MN: A275379 SN: 0036270, *TAP: SIZE: A LOC: 92 FEET FROM P LINE AT AMELIA, *MB: CODE: __ LOC: ON DRYADES,92' FROM U.P.L. AMELIA ON DRYADES ****/ | 2018-05-19 | EXAMINED LEAK ING AREA EXCAVATED IN STREET + DRIVEWAY REPAIRES LEAK BACKFILLEDCLEANED AREA LEAK WAS ON YHE INLET SERVICE
201801020801 | 2018-05-19 | LEAD | 3016 | PALMYRA | S SALCEDO | WILK | MI- LEAK IN STREET INLET LEAK IN ASPHALT STREET (C) /** 1) MN: A260745 SN: 0008742, *TAP: SIZE: B LOC: 143 FEET FROM P LINE AT SALCEDO S, *MB: CODE: BFL LOC: 144FT PL S SALCEDO 3' OUTSIDE ****/ | 2018-05-31 | MADE 8 X 8 CUT IN CONCRETEBASE STREET AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201801024501 | 2018-05-20 | LEAD/PLASTIC | 920 | ODEON AV | LUNA | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-06-07 | EXAMINED AREA CHOPPED THROUGH BUSHES OVER GROWN LOCATED METER CLEANED OUT METER BOX EXCAVATED METER OBSERVED LEAK ON INLET SERVICE NO METER IN BOX REPAIRED LEAK BACKFILLED CLEANED AREA
201801027301 | 2018-05-20 | LEAD | 5864 | LOUISVILLE | BROOKS | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A296494 SN: 0091212, *TAP: SIZE: B LOC: 492 FEET FROM P LINE AT KENILWORTH, *MB: CODE: BDM6 LOC: 492FT FROM PL KENILWORTH 7' OUTSIDE PL 3' INSIDE C ****/ | 2018-05-28 | EXCAVATED IN CONCRETE SIDEWALK. REPAIR 5/8 STOP & WASTE LEAD LINE . ALSO TOOK LEAD LINE OUT ON THE OUTLET SIDE. RENEW 3/4 OUTLET SERVICE PLASTIC LINE FROM METER BOX TO PROPERTY LINE. DRESS UP WITH RIVERSAND & COLD MILL. JOB REFER TO ZONE 1 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201801028801 | 2018-05-21 | LEAD | 5422 | ST CLAUDE AV |  | WDSM | DECREASE EXISTING SERVICE FROM A 1 INCH METER TO A 5/8 INCH WATER METER AT 5422 ST CLAUDE AVE IN SAME LOCATION FOR THE FLAT SUM OF $100.00 SWBNO APP#122880 WFA 2663 /** 1) MN: D005571 SN: 0128385, *TAP: SIZE: D LOC: 220 FEET FROM P LINE AT ANDRY, *MB: CODE: AEL LOC: ON ST CLAUDE 234FT FROM PL ANDRY ****/ | 2018-06-04 | REDUCE EXISTING 1 1/2 METER TO 5/8 INCH METER
201801032501 | 2018-05-21 | LEAD | 541 | DESLONDE | ROYAL | WOLK | MI LEAD WHIP CHANGE METER# A279472 OUTLET SERVICE LEAK HOUSE UNDER RENOVATION /** 1) MN: A294203 SN: 0047398, *TAP: SIZE: B LOC: 316 FEET FROM P LINE AT ROYAL, *MB: CODE: CEM7 LOC: ON DESLONDE 315FT FROM LRPL ROYAL ****/ | 2018-06-04 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA REFER BACK TO ZONE 4 TO REMOVE LEAD FROM STREET
201801032601 | 2018-05-21 | LEAD | 2513 | CLEVELAND AV |  | WILK | LOCATIONID#109484-530769 METER#A396321 METERBOX OVERFLOWING INLET SERVICE LEAK IN MUDPLOT FLOODING CURB /** 1) MN: A266772 SN: 0010698, *TAP: SIZE: A LOC: 94 FEET FROM P LINE AT S ROCHEBLAVE, *MB: CODE: BFK LOC: ON CLEVELAND AVE 94FT FROM PL S ROCHEBLAVE ****/ | 2018-06-05 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH HANDWHEEL TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801032701 | 2018-05-21 | LEAD | 2530 | CLEVELAND AV |  | WMBC | LOCATIONID#112092-530796 METER#A385331 MISSING METER CASING PLEASE REPLACE MISSING UPPER METER BOX CASING /** 1) MN: A268326 SN: 0048887, *TAP: SIZE: A LOC: 137 FEET FROM P LINE AT DORGENOIS S, *MB: CODE: AE LOC: 137FT FROM URPL DORGENOIS ON CLEVELAND AVE ** 2) MN: SN: 0048887, *TAP: SIZE: B LOC: 5 FEET FROM P LINE AT DORGENOIS S, *MB: CODE: OOO LOC: ON CLEVELAND 5FT FROM DIV PL S DORGENOIS THERE IS 1 MORE NOT LISTED. ****/ | 2018-05-30 | REPLACED UPPER METER BOX CASING AT ABOVE LOCATION
201801033001 | 2018-05-21 | LEAD/PLASTIC | 1518 | SUMNER | LAWRENCE ST | WOLK | WM-LEAK IN THE STREET (CUST STATED LEAK IS FLOODING THE AREA) **********1ST AM********* OUTLET SERVICE LEAK FLOODING SIDEWALK /** 1) MN: A298930 SN: 0160866, *TAP: SIZE: B LOC: 122 FEET FROM P LINE AT LAWRENCE, *MB: CODE: OOO LOC: ON SUMNER 122FT FROM PL LAWRENCE 9FT OUTSIDE PL ****/ | 2018-05-24 | ARRIVED ON JOBSITE EXCAVATED AND EXAMINED INLET OUTLET AND T FOUND LEAK ON STOP AND WASTE MADE REPAIRS RAISED TO GRADE BACKFILLED AND CND CLEANED JOBSITE
201801033701 | 2018-05-21 | LEAD/PLASTIC | 2233 | JEFFERSON AV | FRERET | WOLK | WM LEAK IN SIDEWALK OUTLET SERVICE LEAK AT PROPERTY LINE CUSTOMER OUT OF WATER /** 1) MN: A328403 SN: 0058907, *TAP: SIZE: A LOC: 98 FEET FROM P LINE AT FRERET, *MB: CODE: ADM LOC: ON JEFFERSONA VE.,57.7' FROM R.P.L. FRERET ****/ | 2018-05-21 | ANALYZE JOB, FOUND LEAK, MADE ALL REPAIRS, RESTORED CUSTOMER WATER, REFER TO ZONE FOR REROUTE & REMOVE LEAD TO THE MAIN ON INLET
201801034101 | 2018-05-21 | LEAD/PLASTIC | 3600 | MANSFIELD AV | BERKLEY DR | WMTLK | ML-METER LEAK**** ACCT#232183-418715 METER-A367717 EXAMINE INLET/OUTLET SERVICE FOR LEAK ON SIDEWALK 06/08/18 CUST STATED LEAK HAS GOTTEN WORSE (KSW) /** 1) MN: A152814 SN: 0149856, *TAP: SIZE: B LOC: 352 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: BDK6 LOC: ON MANSFIELD AVE., 54.4' FROM D.P.L. BERKLEY DR., ****/ | 2018-06-19 | EXAMINED AREA PUMPED OUT WATER EXCAVATED METER OBSERVED LEAK ON OUTLET SERVICE AND INLET SERVICE MADE REPAIRS BACKFILLED CLEANED AREA ALSO RAISED TO GRADE
201801036601 | 2018-05-22 | LEAD | 1750 | N MIRO | HAVANA | WILK | LOCATION: 114398 MTR# A 416129 PER INSP L UDEBOR, INLET SERVICE LEAK BEHIND CURB COCK. INLET SERVICE LEA INSIDE METER BOX /** 1) MN: A332124 SN: 0061425, *TAP: SIZE: A LOC: 74 FEET FROM P LINE AT HAVANA, *MB: CODE: CF LOC: ON MIRO 74FT FROM HAVANA ****/ | 2018-06-06 | EXCAVATED 3 X 2 SIDEWALK CUT RENEWED OUTLET UP TO PROPERTY ALSO REPLACED 5/8 INCH METER COCK BACKFILLED AND CLEANED THE AREA REFER BACK TO ZONE 4 FOR REMOVAL OF LEAD FROM STREET
201801036701 | 2018-05-22 | LEAD | 1737 | N MIRO | HAVANA | WILK | LOCATION: 123933 MTR# A 416055 PER INSP L. UDEBOR, LEAK COMING FROM INLET RELIEF VALVE. INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A311229 SN: 0066116, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT MIRO N, *MB: CODE: BD LOC: ON HAVANA,98.4' FROM U.S.P.L. NO. MIRO ****/ | 2018-06-06 | EXCAVATED 2 X 10 DRIVEWAY CUT RENEWED OUTLET TO PROPERTY BACKFILLED AND CLEANED THE AREA REFER BACK TO ZONE 4 TO HAVE LEAD REMOVE FROM STREET
201801037801 | 2018-05-22 | LEAD | 935 | ST ANN | BURGUNDY | WILK | ML METER LEAK NETER# A404008 INLET SERVICE BAD BLEEDER VALVE /** 1) MN: A187966 SN: 0029822, *TAP: SIZE: A LOC: 35 FEET FROM P LINE AT BURGUNDY, *MB: CODE: AEK1 LOC: 18FT LPL CURB ****/ | 2018-05-31 | EXCAVATED 4X 2 SIDEWALK CUT MADE REPAIR ON INLET SERVICE LINE AND RENEWED OUTLET TO PROPERTY BACKFILLED AND CLEANED THE AREA WAS UNABLE TO SAVE CONCRETE TILE REFER BACK TO ZONE 4 TO REMOVE LEAD FROM STREET
201801040401 | 2018-05-23 | LEAD | 1736 | TOURO | N ROMAN | WOLK | LOCATION# 112317 CUSTOMER# 493655 METER# A288683 INSPECTOR DID AN OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION ON METER, LEAK INSIDE METER BOX......PLEASE REPAIR /** 1) MN: 000000 SN: 0059192, *TAP: SIZE: A LOC: 0 FEET FROM P LINE AT TOURO, *MB: CODE: AEL1 LOC: ****/ | 2018-06-07 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201801043901 | 2018-05-23 | LEAD | 4709 | N RAMPART | SISTER | WILK | ML - METER LEAK ACCOUNT NUMBER - 145733-424518 METER NUMBER - C013466 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: C013466 SN: 0077541, *TAP: SIZE: C LOC: 77 FEET FROM P LINE AT SISTER, *MB: CODE: CD LOC: ON N RAMPART 77FT FROM PL SISTER ****/ | 2018-06-19 | EXAMINED FOUND 1 INCH WASHER LEAK CHANGED WASHERS ON INELT + OUTLET UNABLE TO CHANGE OUTLET DUE TO CAR PARKED ON JOB
201801045501 | 2018-05-23 | LEAD/PLASTIC | 2616 | MERCEDES BL |  | WILK | LOCATION ID-230038 MTR-A427879 LOW PRESSURE INLET SERVICE LEAK UNDERMINING ASPHALT STREET AT DRAIN CATCH BASIN CAUSING POOR PRESSURE **1ST AM** /** 1) MN: A145531 SN: 0134043, *TAP: SIZE: B LOC: 120 FEET FROM P LINE AT ANSON, *MB: CODE: CDLM LOC: ON MERCEDES 120' FROM PL ANSON 14' OUTSIDE PL ****/ | 2018-05-24 | CUT SERVICE FROM CURB TO MIDDLE OF THE STREET WITH MACHINE REPAIRED ON SERVICE AND REMOVED LEAD LINE RAN NEW PLASTIC FROM STREET TO METER BOX BACKFILLED WITH RIVER SAND COLD MILL
201801046101 | 2018-05-24 | LEAD | 1920 | O"REILLY | N PRIEUR | WILK | ACCT# 221012-494439 MTR# A401058 INSPECTOR FOUND LEAK AT WHEEL SIDE OF METER. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-06-07 | EXCAVATED 4 X 6 LIMESTONE GUTTER BOTTOM 4 X 4 CONCRETE SIDEWALK RELOCATED METER BOX INTO SIDEWALK RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILLED JOB WITH RIVERSAND COLDMILL REPLACE BROKEN 5/8 INCH METER WITH NEW METER ********OLD METER INFO******** METER:A401058 FAC:14106819 MAKE:HERSEY READ:151
201801047601 | 2018-05-24 | LEAD | 2321 | PIETY |  | WILK | ML - METER LEAK MTR # A430229 ACCT # 304360-718539 EXAMINE INLET SERVICE FOR A LEAK IN FRONT VACANT LOT. FOUND METER OFF LEFT OFF /** 1) MN: A321942 SN: 0084373, *TAP: SIZE: A LOC: 164 FEET FROM P LINE AT TONTI N, *MB: CODE: BDM1 LOC: FRONT - 164' P.L. N TONTI ****/ | 2018-07-03 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201801051201 | 2018-05-24 | LEAD/PLASTIC | 4728 | EASTVIEW DR | HAMMOND | WILK | MI-HOLE/ DEPRESSION IN STREET CUST STATES HOLE IS VERY LARGE . EXAMINE DEPRESSION IN STREET 05/26/18 UPGRADED TO ****B**** PER S SLACK (GAVE OUT) NLD /** 1) MN: A265519 SN: 0135023, *TAP: SIZE: A LOC: 227 FEET FROM P LINE AT LEEDS, *MB: CODE: CDM1 LOC: ON EASTVIEW DR 227' FROM PL LEEDS 7' OUTSIDE PL ****/ | 2018-05-26 | EXCAVATED IN THE 4X8 CUT IN STREET OVER 6" WATER MAIN BROKEN PUT 6X12 REPAIR CLAMP ON IT BACKFILL
201801051501 | 2018-05-24 | LEAD/PLASTIC | 119 | DANNY DR | CROYDEN AV | WILK | ML METER LEAK METER# A406774 ACCT# 226682-706797 INLET SERVICE LEAK /** 1) MN: A130937 SN: 0121609, *TAP: SIZE: A LOC: 259 FEET FROM P LINE AT PATTERSON DR, *MB: CODE: ADM2 LOC: ON DANNY DR., 259' FROM P.L. PATTERSON DR., 11' ****/ | 2018-06-14 | EXAMINED AREA OBSERVED LEAK ON INLET SERVICE EXCAVATED METER BOX EXPOSED REPAIRED LEAK BACKFILLED CLEANED AREA
201801052701 | 2018-05-25 | LEAD | 907 | N VILLERE | DUMAINE | WOLK | LOCATION# 194638 CUSTOMER# 703853 METER# A428231 INSPECTOR DID AN OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION ON METER, PERFORMED S&WB SHUT-OFF TEST METER CONTINUES TO RUN........PLEASE REPAIR /** 1) MN: 000000 SN: 0013029, *TAP: SIZE: B LOC: 87 FEET FROM P LINE AT DUMAINE, *MB: CODE: BEOK LOC: ON N VILLERE 86FT FROM PL DUMAINE 10' OUTSIDE PL 2 ****/ | 2018-06-06 | REPLACED HANDWHEEL INSIDE METER BOX WITH 5/8 INCH WASHERS
201801053301 | 2018-05-25 | LEAD/PLASTIC | 1820 | S JEFFERSON DAVIS PK |  | WILK | LOCATION: 157107 MTR# B 042739 PER INSP BIBBINS, WATER LEAKING FROM CURB COCK. INLET SERVICE LEAK /** 1) MN: B026544 SN: 0094384, *TAP: SIZE: B LOC: 197 FEET FROM P LINE AT SO. RENDON, *MB: CODE: BFN LOC: ON S JEFF DAVIS PKWY, 84' FROM P.L. GEN. TAYLOR, ****/ | 2018-06-04 | EXCAVATED IN MUDPLOT ON INLET IN TREEROOTS REPLACE METERBOX COCK ON LEAD LINE BACKFILL REFERRE TO ZONE 3 TO REMOVE LEAD
201801054101 | 2018-05-25 | LEAD | 1004 | N LOPEZ |  | WILK | ML - METER LEAK ACCT#110752-521399 METER#A284179 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A284179 SN: 0015687, *TAP: SIZE: B LOC: 29 FEET FROM P LINE AT ST PHILIP, *MB: CODE: AF LOC: 29' P.L. ST PHILIP ****/ | 2018-06-07 | EXCAVATED HANDWHEEL AND MADE REPAIR ON INLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA REFER BACK TO ZONE 4 FOR REMOVAL OF LEAD FROM THE STREET
201801054801 | 2018-05-25 | LEAD | 2607 | ST ANTHONY | LAW | WILK | MI- CUT SERVICE (BENTON GEORGIA- 504-9857747859) CUST STATES THAT EVERYONE HAS WATER SERVICES. **************DAMAGE CLAIM************* CHANGED FROM 2605 ST ANTHONY CUT INLET SERVICE UNDERGROUND ACROSS FROM ABOVE ADDRESS @ VACANT LOT BY ENTERGY GAS/ BENTON GEORGIA /** 1) MN: SN: 0070586, *TAP: SIZE: A LOC: 67 FEET FROM P LINE AT LAW, *MB: CODE: CL LOC: ON ST ANTHONY 79' FROM PL OF LAW ****/ | 2018-06-26 | EXCAVATED IN CONCRETE SIDEWALK BY HAND + REPLACED 3/4 INCH ABANDON CORPORATION COCK THAT WAS BROKEN BY ENTERGY GAS LINE FORCE ACCOUNT ENTERGY FOR REPAIRS BACKFILLED + DRESSED UP AREA
201801054901 | 2018-05-25 | LEAD | 1884 | LAURADALE DR | COPERNICUS | WILK | MI- LEAK ON SIDEWALK ** FLOODING AREA*** INET SERVICE LEAK IN MUDPLOT /** 1) MN: A277824 SN: 0126690, *TAP: SIZE: B LOC: 43 FEET FROM P LINE AT COPERNICUS, *MB: CODE: CFM LOC: ON LAURADALE DR 43' FROM PL COPERNICUS 3' OUTSIDE ****/ | 2018-06-10 | EXCAVATED IN MUDPLOT ON INLET LEAK ON LEAD MADE ALL REPAIR TO STOP LEAK BACKFILL REFER TO ZONE 6 TO REMOVE LEAD
201801055201 | 2018-05-25 | LEAD | 2509 | REPUBLIC |  | WILK | MI- LEAK AT THE SIDEWALK EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A288985 SN: 0081018, *TAP: SIZE: B LOC: 42 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: BD5 LOC: ON REPUBLIC 42FT FROM DORGENOIS N ****/ | 2018-06-07 | EXCAVATED 2 X 2 MUD PLOT AROUND METER BOX ALSO 3 X 2 MUD PLOT AT PROPERTY RENEWED OUTLET AT PROPERTY TO METER BOX BACKFILLED AND CLEANED THE AREA REFER BACK TO ZONE 4 TO HAVE LEAD REMOVED FROM STREET
201801056001 | 2018-05-25 | LEAD/PLASTIC | 4711 | ARTHUR DR |  | WILK | LOCATON: 261127 MTR# B 040955 PER INSP J. RUTH, NO WATER COMING FROM INLET. PLEASE REPAIR. CUSTOMER HOME WAITING ON WATER!!!!! **********1ST AM********** NO WATER ON INLET /** 1) MN: B026069 SN: 0118642, *TAP: SIZE: B LOC: 640 FEET FROM P LINE AT HAMMOND, *MB: CODE: CDN1 LOC: BET GRANT-HAMMOND 640'FRM VALVE AT HAMMOND ****/ | 2018-05-26 | EXCAVATED IN THE MUD PLOT OVER 3/4 METER BOX FOUND LEAD ON THE OUTLET REPLACE FROM METER BOX TO PROPERTY LINE WITH 8FT OF 3/4 WATER TUBING REPLACE 3/4 METER BOX COMPLETE BACKFILL
201801056301 | 2018-05-25 | LEAD | 2001 | LAHARPE |  | WILK | WM LEAK ON THE SIDEWALK INLET SERVICE LEAK ON SIDEWALK FLOODING CURB AND STREET /** 1) MN: A306156 SN: 0051668, *TAP: SIZE: A LOC: 40 FEET FROM P LINE AT LAHARPE, *MB: CODE: BDH LOC: ON 39' FROM PL OF LAHARPE ****/ | 2018-06-07 | EXCAVATED 2 X 2 MUD PLOT AROUND METER BOX ALSO 3 X 2 MUD PLOT AT PROPERTY RENEWED OUTLET TO PROPERTY BACKFILLED AND CLEANED THE AREA
201801058801 | 2018-05-27 | LEAD/PLASTIC | 1658 | ELIZARDI BL | MAGELLAN | WOLK | LOCATION# 234126 CUSTOMER# 406503 METER# A428728 INSPECTOR DID AN OUTSIDE INSPECTION FOUND METER FILLED BACK UP AFTER PUMPED OUT CAN'T DETERMINE WHERE LEAK IS COMING FROM.....PLEASE REPAIR /** 1) MN: A120264 SN: 0152732, *TAP: SIZE: B LOC: 200 FEET FROM P LINE AT MAGELLAN, *MB: CODE: ADLM LOC: ON ELIZARDI 202FT FROM P.L. MAGELLAN ****/ | 2018-06-19 | EXAMINED AREA CLEANED METER BOX OUT EXCAVATED ON OUTLET SERVICE OBSERVED LEAK ON OUTLET REPAIR LEAK BACKFILLED CLEANED AREA
201801059201 | 2018-05-27 | LEAD | 3997 | DUMAINE | OLGA | WILK | ML METER LEAK ACCT# 110341-514620 METER# A301186 /** 1) MN: A301186 SN: 0030391, *TAP: SIZE: A LOC: 193 FEET FROM P LINE AT ROOSEVELT PL, *MB: CODE: BD LOC: ON DUMAINE 193' FROM SPL ROOSEVELT PLACE ****/ EXAMINE INLET SERVICE FOR LEAK | 2018-06-25 | EXCAVATED 2 X 2 MUD PLOT AROUND METER BOX ALSO 3 X 2 MUD PLOT AT PROPERTY RNEWED OUTLET TO PROPERTY BACKFILLED AND CLEANED THE AREA
201801063701 | 2018-05-29 | LEAD | 3010 | PAUGER |  | WMBK | LOCATION: 268419 MTR# A 416229 PER INSP UDEBOR, OUTLET WASHER LEAK, METER NOT LINING UP BROKEN METER BOX CASING, METER NOT LINING UP HOUSE UNDER RENOVATION 06/05/148 PER S/R 12842959 METER LEAK (KSW) /** 1) MN: A114907 SN: 0060870, *TAP: SIZE: A LOC: 87 FEET FROM P LINE AT TONTI N, *MB: CODE: CDLM LOC: ON PAUGER 86.6' FROM LPL N TONTI ****/ | 2018-06-22 | EXCAVATED 2 X 4 MUD PLOT IN GUTTER BOTTOM FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIR S ON OUTLET UP TO SIDEWALK WAS UNABLE TO RENEW OUTLET CAUSE OF TRUCK ON JOB SITE BACKFILL JOB WITH RIVERSAND CUSTOMER HAS GOOD PRESSURWE NOW
201801064001 | 2018-05-29 | LEAD | 2042 | N ROCHEBLAVE |  | WILK | ML - METER LEAK - METER NUMBER # B040774= ACCOUNT NUMBER - 179004-496165 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: B026271 SN: 0078361, *TAP: SIZE: B LOC: 100 FEET FROM P LINE AT ANNETTE, *MB: CODE: D LOC: 100FT FROM PL S&W ANNETTE MTR ON N ROCHEBLAVE 7FT ****/ | 2018-06-29 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 3/4 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201801064201 | 2018-05-29 | LEAD | 2047 | N ROCHEBLAVE | ANNETTE | WILK | ********************PICKUP****************** EXAMINE INLET SERVICE FOR LEAK /** 1) MN: B028144 SN: 0079280, *TAP: SIZE: B LOC: 153 FEET FROM P LINE AT ANNETTE, *MB: CODE: B LOC: 153' P.L. ANNETTE ****/ | 2018-06-29 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201801064301 | 2018-05-29 | LEAD | 3500 | BANKS |  | WILK | ML-- METER LEAK METER # B040772 ACCT # 118757-533276 INLET SERVICE IN MUDPLOT /** 1) MN: B026867 SN: 0048448, *TAP: SIZE: B LOC: 60 FEET FROM P LINE AT BANKS, *MB: CODE: ADH6 LOC: 1ST METER SIDE ST BY GUY WIRE METER ON S CLARK ****/ | 2018-06-13 | EXCAVATED IN MUDPLOT REPAIR 3/4 VSTOP AND WASTE LEAD LINE AND BOTTOM.DRESS UP WITH RIVER SAND. JOB REFER TO ZONE 4 TO REMOVE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201801067501 | 2018-05-29 | LEAD | 940 | LIZARDI | N RAMPART | WILK | ML-METER LEAK ACCT#140977-424916 METER#A417363 EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A245887 SN: 0071887, *TAP: SIZE: A LOC: 33 FEET FROM P LINE AT LIZARDI, *MB: CODE: CDHL LOC: ON N RAMPART ST 33' FROM PL LIZARDI ****/ | 2018-06-26 | EXCAVATED 3 X 2 MUD PLOT AT PROPERTY RENEWED OUTLET SERVICE LINE TO PROPERTY BACKFILLED AND CLEANED THE AREA
201801067901 | 2018-05-29 | LEAD | 5329 | DOUGLAS | EGANIA | WILK | ML-METER LEAK MTR# A 415617 ACC#173814-425066 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A248175 SN: 0117387, *TAP: SIZE: B LOC: 240 FEET FROM P LINE AT EGANIA, *MB: CODE: CDN1 LOC: 244FT FROM PL EGANIA MTR ON DOUGLAS 8FT OUTSD PL ****/ | 2018-06-26 | EXCAVATED 3 X 2 MUD PLOT AT PROPERTY ALSO 2 X 2 MUD PLOT AROUND METER BOX RENEWED OUTLET TO PROPERTYBACKFILLED AND CLEANED THE AREA
201801068501 | 2018-05-29 | LEAD | 2117 | CLOUET | N GALVEZ | WOLK | ML- METER LEAK ACCT# 158910-718379 MTR# A358176 EXAMINE OUTLET SERVICE AT PROPERTY LINE FOR LEAK 05/30/18 CUSTOMER OUT OF WATER PER SR#12842509, GIVE OUT *******J.GILLIAM @14:01AM********* /** 1) MN: A295882 SN: 0096795, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT GALVEZ N, *MB: CODE: CD LOC: ON CLOUET 112' FROM PL N GALVEZ 6.5' OUTSIDE PL 1. ****/ | 2018-05-31 | ARRIVE AT ABOVE LOCATION FOUND 2 X 4 INCH HOLE EXPOSED LEAK IS ON 5/8 INCH OUTLET SERVICE MADE REPAIRS ON OUTLET BACKFILLED JOB WITH RIVERSAND CUSTOMER HAS WATER NOW
201801069001 | 2018-05-29 | LEAD | 2431 | BROADWAY | NELSON | WMTLK | ML - METER LEAK ACCT#145341-584897 METER#A211155 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: A211155 SN: 0077044, *TAP: SIZE: A LOC: 33 FEET FROM P LINE AT NELSON, *MB: CODE: BDN1 LOC: ON BROADWAY 33FT FROM PL OF NELSON ****/ | 2018-06-19 | EXCAVATED IN MUDPLOT REPAIR 5/8 STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND JOB REF TO ZONE 3 TO TAKE LEAD LINE FROM WATER MAIN TO METER BOX
201801072901 | 2018-05-30 | LEAD/PLASTIC | 4491 | FRANKLIN AV |  | WOLK | MI CHANGE LEAD WHIP METER #A175160 ACCOUNT #133396-478337 CHANGE LEAD WHIP, ALSO CUSTOMER RENEW OUTLET FROM PROPERTY TO PROPERTY LINE STILL HAS CONSTANT REGISTRATION /** 1) MN: A175160 SN: 0086001, *TAP: SIZE: A LOC: 626 FEET FROM P LINE AT GENTILLY BLVD, *MB: CODE: BDK3 LOC: ON FRANKLIN AVE.,626' FROM P.L. GENTILLY BLVD. ****/ | 2018-06-06 | EXCAVATED IN MUDPLOT TOOK LEAD LINE OUT REPAIR 5/8 STOP & WASTE LEAD LINE ALSO RENEW 3/4 OUTLET SERVICE PLASTIC LINE DRESS UP WITH RIVERSAND JOB REF TO ZONE 5 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201801073501 | 2018-05-30 | LEAD | 3501 | ROGER WILLIAMS |  | WILK | ML-METER LEAK ACCT# 158590-493471 MTR.# A 405172 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A141283 SN: 0096166, *TAP: SIZE: B LOC: 50 FEET FROM P LINE AT TENSAS, *MB: CODE: ADKO LOC: ON ROGER WILLIAMS, 50' FROM P.L. TENSAS,8' OUTSIDE ****/ | 2018-06-13 | EXCAVATED IN MUDPLOT ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND.
201801076701 | 2018-05-30 | LEAD | 1365 | ANNETTE |  | WILK | LOCATION: 304987 PER INSP UDEBOR, INLET & OUTLET NOT LINING UP. PLEASE REPAIR AND SET 5/8 METER. CUSTOMER WILL BE POURING CONCRETE SOON, NEED WATER ASAP. INLET AND OUTLET NOT LINING UP, ALSO SET 5/8 METER HOUSE UNDER RENOVATION /** 1) MN: A277508 SN: 0038958, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT URQUHART, *MB: CODE: BF25 LOC: ON ANNETTE 44' FROM PL URQUHART 2' OUTSIDE PL ****/ | 2018-06-11 | EXCAVATED 3 X 2 SIDEWALK CUT RENEWED OUTLET SERVICE LINE TO PROPERTY ALSO SET ONE 5/8 INCH METER BACKFILLED AND CLEANED THE AREA
201801077001 | 2018-05-30 | LEAD | 2101 | SONIAT | S LIBERTY | WILK | ML-METER LEAK ACCT#122986-570558 METER# B40367 INLET SERVICE LEAK BEHING CURB COCK FLOODING GRASSY AREA /** 1) MN: B032053 SN: 0041846, *TAP: SIZE: B LOC: 43 FEET FROM P LINE AT SONIAT, *MB: CODE: BDH LOC: SIDE ST ON S LIBERTY 43' P.L. SONIAT ****/ | 2018-06-12 | EXCAVATED IN MUD PLOT ON INLET LEAK MADE ALL REPAIRS TO STOP LEAK.BACKFILL WITH RIVERSAND ON LEAD REFER TO ZONE 3 TO REMOVE LEAD.
201801078301 | 2018-05-30 | LEAD | 7136 | E HERMES |  | WILK | MI-LEAK BETWEEN S/WALK & STREET. INLET SERVICE LEAK METER BOX OVERFLOWING RAISE METER BOX TO GRADE /** 1) MN: C011771 SN: 0122571, *TAP: SIZE: C LOC: 111 FEET FROM P LINE AT PANDORA, *MB: CODE: OOO LOC: ****/ | 2018-05-30 | EXCAVATED IN MUDPLOT. REPAIR 1INCH STOP & WASTE LEAD LINE . DRESS UP WITH RIVERSAND JOB REFER TO ZONE 5 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201801079401 | 2018-05-30 | LEAD/PLASTIC | 1212 | MAGAZINE | ERATO | WILK | ML-METER LEAK METER#A313929 ACCT#103217-536885 INLET SERVICE LEAK /** 1) MN: SN: 0005839, *TAP: SIZE: B LOC: 127 FEET FROM P LINE AT ERATO URPL, *MB: CODE: BDK3 LOC: 127FT FROM URPL ERATO ****/ | 2018-07-26 | EXAMINED WORK AREA PUMP DOWN METER BOX OBSERVED LEAK ON INLET SERVICE BROKE OUT CONCRETE EXPOSED LEAD ON INLET AND OUTLET REMOVED LEAD TO PROPERTY REPAIRED INLET SERVICE BACKFILLED CLEANED AREA
201801080801 | 2018-05-31 | LEAD | 7557 | AVALON WAY |  | WMTLK | WM-LEAK IN SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK FLOODING SIDEWALK & CURB ***HIGH GRASS***, ALSO RAISE TO GRADE ***(PER INSP R STANWOOD B LEAVE IN SYSTEM)*** /** 1) MN: 000000 SN: 0151370, *TAP: SIZE: B LOC: 194 FEET FROM P LINE AT HERITAGE DR, *MB: CODE: CDN1 LOC: ON AVALON WAY, 194' FROM P.L. HERITAGE DR., 10' ****/ | 2018-05-31 | EXCAVATED IN MUDPLOT ON INLET MADE ALL REPAIRS TO STOP LEAK ON LEAD BACKFILL WITH RIVERSAND REFER TO ZONE 5 TO REMOVE LEAD
201801083001 | 2018-05-31 | LEAD | 2223 | N JOHNSON | MARIGNY | WMBK | ML- METER LEAK METER # A430086 ACCT # 188844-483660 BROKEN METER BOX SHIFTED CAUSING INLET SERVICE TO LEAK /** 1) MN: A336874 SN: 0044767, *TAP: SIZE: A LOC: 115 FEET FROM P LINE AT MARIGNY, *MB: CODE: CE LOC: 114FT FROM PL MARIGNY MTRRON N JOHNSON 8FT OUTSD ****/ | 2018-06-11 | EXCAVATED 5 X 2 SIDEWALK CUT RENEWED OUTLET UP TO PROEPRTY ALSO REPLACED 5/8 INCH METER COCK BACKFILLED AND CLEANED THE AREA
201801084401 | 2018-05-31 | LEAD | 1924 | FRANKLIN AV | N PRIEUR | WILK | ML-METER LEAK METER#A248581 ACCT#113214-494464 INLET SERVICE LEAK AROUND CURBCOCK FOUND OFF LEFT OFF TURNED ON TO CHECK METER TURNED BACK OFF /** 1) MN: A267758 SN: 0045173, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT JOHNSON N, *MB: CODE: D LOC: METER ON FRANKLIN AVE 131.5 FT FROM PL N JOHNSON ****/ | 2018-06-14 | EXCAVATED 8 X 3 SIDEWALK CUT RENEWED OUTLET UP TO PROPERTY BACKFILLED AND CLEANED THE AREA
201801084501 | 2018-05-31 | LEAD | 963 | WILSON DR | DUMAINE | WILK | ML- METER LEAK METER# A375323 ACCT# 143378-514293 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A281261 SN: 0074730, *TAP: SIZE: B LOC: 470 FEET FROM P LINE AT DUMAINE, *MB: CODE: ADM2 LOC: ON WILSON DR 470FT FROM PL DUMAINE ****/ | 2018-06-15 | REPLACED 5/8 INCH WASHERS AT ABOVE LOCATION
201801084701 | 2018-05-31 | LEAD | 2330 | FLOOD |  | WMTLK | LOCATION ID-174966 MTR-A395393 BAD LEAK AT AND AROUND MTR/AREA SATURATED EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER GRASS AREA FLOODED /** 1) MN: A135047 SN: 0132896, *TAP: SIZE: B LOC: 234 FEET FROM P LINE AT TONTI N, *MB: CODE: ADL2 LOC: ON FLOOD 227FT FROM PL TONTI 7FT OUTSIDE ****/ | 2018-06-13 | EXCAVATED 3 X 3 MUD PLOT AROUND METER BOX ALSO 2 X 2 AT PROPERTY RENEWED OUTLET TO PROPERTY AND RAISED METER BOX TO GRADE BACKFILLED AND CLEANED THE AREA ****REFER TO ZONE 4 TO HERE LEAD REMOVED FROM STREET*****
201801089801 | 2018-06-01 | LEAD | 2152 | LAW |  | WOLK | LOCATION ID-159626 MTR-A349663 LEAK BETWEEN MTR AND STOP & WASTE/CONS REG ON MTR OUTLET SERVICE LEAK WITH CONSTANT REGISTRATION ON METER /** 1) MN: A267489 SN: 0097352, *TAP: SIZE: A LOC: 187 FEET FROM P LINE AT TOURO, *MB: CODE: AK LOC: ON LAW 187FT FROM PL OF TOURO 8FT OUTSIDE PL ****/ | 2018-06-29 | FOUND CONSTRANT REGISTRATION ON METER DID STOP -N-WASTE TEST METER STOP REGISTRATION CUSTOMER HAS LEAK ON PROPERTY COULDN'T CHANGE LEAD WHIP BECAUSE AIR COMPRESSOR IS OUT
201801092601 | 2018-06-04 | LEAD/PLASTIC | 429 | S SCOTT | BAUDIN | WMBK | LOCATION: 130033 MTR# A 368170 PER INSP M FRAZIER - METER BOX SHIFTED, CANNOT REMOVE METER. PLEASE REPAIR AND CHANGE METER. REPLACE BROKEN & SHIFTED METER BOX CASING, ALSO CHANGE METER /** 1) MN: A273586 SN: 0059337, *TAP: SIZE: A LOC: 122 FEET FROM P LINE AT BAUDIN, *MB: CODE: BDLM LOC: ON S SCOTT 120.8' FROM LSPL BAUDIN ****/ DOTTIE READY 6-8-18 EXP 6-28-18 | 2018-07-13 | EXCAVTED IN MUDPLOT OVER 5/8 OUTLET SERVICE REMOVED LEAD FROM METER TO PROPERTY REPLACED LEAD WITH 3/4 PLASTIC.REMOVED OLD METER SET NEW METER .RAISED TO GRADE. **************OLD METER INFO************** METER:A368170 FAC:70597385 MAKE:SENSUS READ:5631
201801093201 | 2018-06-04 | LEAD/PLASTIC | 4828 | PITT | UPPERLINE | WMTBG | INSPECTOR S BIBBINS STATED HE CANNOT CHANGE METER. SERVICE NEEDS TO BE RAISED TO GRADE. PLEASE REPAIR AND CHANGE METER A372830 LOC ID 120582 RAISE METER TO PROPER GRADE AND CHANGE METER /** 1) MN: A245838 SN: 0036406, *TAP: SIZE: A LOC: 90 FEET FROM P LINE AT UPPERLINE, *MB: CODE: CELM LOC: INSIDE AT EDGE OF SIDEWALK ON PITT 89 FT FROM PL ****/ DOTTIE READY 6-8-18 EXP 6-28-18 | 2018-07-15 | EXCAVTED 8FT .X 4 FT .SIDEWALK CUT .RAISED METER BOXES UP TO GRADE AND RENEW OUTLET.BACKFILLED AND CLEANED THE AREA.
201801095301 | 2018-06-04 | LEAD | 820-22 | N DUPRE | ST ANN | WMTLK | ML- METER LEAK MTR# A382705 ACCT# 122964-520982 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** AT 820: 1) MN: A257652 SN: 0041967, *TAP: SIZE: A LOC: 146 FEET FROM P LINE AT ST ANN, *MB: CODE: OOO LOC: ON N DUPRE 148FT FROM PL OF ST ANN ****/ | 2018-07-06 | EXCAVATED 2 X 2 MUD PLOT TO REPLACE 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801100501 | 2018-06-04 | LEAD/PLASTIC | 8539 | FORSHEY | LEONIDAS | WMTLK | ML- METER LEAK METER# A428747 ACCT# 302284-714590 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A280762 SN: 0095358, *TAP: SIZE: A LOC: 52 FEET FROM P LINE AT FORSHEY, *MB: CODE: CDHL LOC: ON LEONIDAS 51.5' FROM PL FORSHEY 7.5' OUTSIDE PL ****/ | 2018-06-06 | EXCAVATED IN MUDPLOT ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND AND COLDMILL IN SIDEWALK REFERRE TO ZONE 1 TO REMOVE LEAD
201801100502 | 2018-06-06 | LEAD/PLASTIC | 8539 | FORSHEY | LEONIDAS | WSNR | REFERRE TO ZONE 1 TO REMOVE LEAD /** 1) MN: A280762 SN: 0095358, *TAP: SIZE: A LOC: 52 FEET FROM P LINE AT FORSHEY, *MB: CODE: CDHL LOC: ON LEONIDAS 51.5' FROM PL FORSHEY 7.5' OUTSIDE PL ****/ | 2018-06-26 | MADE A 4 X 6 SIDE WALK CUT. EXCAVATED AND MADE REPAIRS FROM THE METER BOX TO PROPERTY. LEAD ON THE INLET. WILL REMOVE LEAD ON A LATER DATE. [ JOB CONTINUE ]
201801103401 | 2018-06-05 | LEAD/PLASTIC | 500 | LAKESHORE PK | RUBY | WILK | ML METER LEAK METER# C036033 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: C023579 SN: 0117039, *TAP: SIZE: C LOC: 633 FEET FROM P LINE AT RUBY, *MB: CODE: AFK LOC: ON LAKESHORE 630FT FROM PL RUBY 2FT OUTSIDE PL 9FT ****/ | 2018-06-25 | EXAMINED & FOUND WASHER LEAK. CHANGED WASHERS INSIDEMETERBOX. FOUND LEAD PIPE ON INLET SERVICE & PVC ON OUTLET SERVICE.
201801103501 | 2018-06-05 | LEAD | 2477 | N PRIEUR | ARTS | WILK | METER LEAK EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A306709 SN: 0065670, *TAP: SIZE: A LOC: 42 FEET FROM P LINE AT ARTS, *MB: CODE: OOO LOC: ON N PRIEUR ST 42' FROM PL ARTS ****/ | 2018-06-11 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE LINE AND REPLACED 5/8 INCH METER BOX COCK TO STOP DURING HEAVY RAIN BACKFILLED AND CLEANED THE AREA LEFT CONE ON JOB SITE DUE WETTNESS OF MATERIAL
201801104601 | 2018-06-05 | LEAD | 3204 | PRYTANIA | HARMONY | WILK | MI-CUT SERVICE ACCT#105464-576969 METER#C020601 CALLER UNSURE IF CUSTOMER IS W/O WATER *******DAMAGE CLAIM******* (L.THOMPSON @ 13:50PM) CUT INLET SERVICE CAUSING POOR PRESSURE BY MESCHE CONSTRUCTION /** 1) MN: C020601 SN: 0017848, *TAP: SIZE: C LOC: 56 FEET FROM P LINE AT HARMONY, *MB: CODE: BFK LOC: ON PRYTANIA 56FT FROM PL OF HARMONY ****/ | 2018-05-05 | EXCAVATED IN SIDEWALK ON INLET EXAMINE LEAD LINE AND FOUND NO LEAK ALSO CUSTOMER HAVE WATER AND GOOD PRESSURE BACKFILL WITH RIVERSAND AND COLDMILL REFERRE TO ZONE 3 TO REMOVE LEAD
201801104701 | 2018-06-05 | LEAD/PLASTIC | 1104 | NUNEZ |  | WMTLK | ML METER LEAK ACCOUNT #228869-401656 METER #A352679 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER BOX UNDER WATER FLOODING SIDEWALK /** 1) MN: A305266 SN: 0057013, *TAP: SIZE: B LOC: 48 FEET FROM P LINE AT DIANA, *MB: CODE: BDL LOC: ON NUNEZ 48FT FROM P.L. DIANA 8FT OUTSIDE P.L. ****/ | 2018-07-05 | EXAMINED AREA SEARCHED FOR METER NOTE CUSTOMER AT 1106 STATED THAT METER IS USED AT BOTH ADDRESSED 1106 NUNEZ EXCAVATED ON INLET AND OUTLET OBSERVED LEAK ON INLET AND OBSERVED LEAD ON OUTLET REPAIRED LEAK AND REPLACE LEAD TO PROPERTY
201801105901 | 2018-06-05 | LEAD | 8623 | MARKS | EAGLE | WILK | ML-METER LEAK INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A283985 SN: 0091647, *TAP: SIZE: A LOC: 143 FEET FROM P LINE AT LEONIDAS, *MB: CODE: BDL LOC: ON MARKS,143' FROM P.L. LEONIDAS,7' OUTSIDE P.L., ****/ | 2018-06-22 | EXCAVATED AND MADE REPIRS ON A 5/8 INLRT SERVICE LEAK. LEAD ON THE INLET AN OUTLET . NEED A MACHINE TO REPLACED THE LINE. [ JOB COMPLETE ]
201801108001 | 2018-06-06 | LEAD/PLASTIC | 446 | THAYER | ELIZA | WOLK | ML - METER LEAK MTR# C031514 ACCT # 228416-403350 **********DAMAGE CLAIM********** S SLACK 11:52 **********CUSTOMER OUT OF WATER********** CUT OUTLET SERVICE BY DURR HEAVY CONSTRUCTION /** 1) MN: C019605 SN: 0120758, *TAP: SIZE: C LOC: 3 FEET FROM P LINE AT THAYER, *MB: CODE: AD LOC: ON ELIZA, 3' FROM P.L. THAYER, 7' OUTSIDE ****/ | 2018-06-06 | EXAMINED AREA OBSERVED METER IN OFF POSITION TURNED METER ON AND OBSERVED LEAK ON OUTLET SERVICE MADE REPAIRS AND LEFT METER IN SITE OF CONTRACTIOR AREA
201801108401 | 2018-06-06 | LEAD | 3021 | PIETY |  | WILK | LOCATIONID#160146-434504 METER#A386626 UNDERWATER METER LEAKING INLET SERVICE LEAK /** 1) MN: A278153 SN: 0098107, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT ABUNDANCE, *MB: CODE: BDKL LOC: 136' PL ABUNDANCE 5' OUTSIDE PL 3' INSIDE CURB ****/ | 2018-06-27 | EXCAVATED DOWN ON INLET AND OUTLET SERVICES. FOUND LEAD AND METER COCK WAS LEAKING. MADE REPAIRS BY REPLACING COCK WASHERS, HANDWHEEL ALSO OUTLET SERVICE FROM METER TO PROPERTY. BACKFILLED
201801110301 | 2018-06-06 | LEAD/PLASTIC | 1017 | 1ST | MAGAZINE | WILK | WM- LEAK IN THE STREET ***********S.SLACK @ 13:34PM************** INLET SERVICE LEAK IN ASPHALT STREET FLOODING AREA CAUSING 2 DEPRESSION IN STREET /** 1) MN: A272641 SN: 0007570, *TAP: SIZE: B LOC: 206 FEET FROM P LINE AT MAGAZINE, *MB: CODE: CEL LOC: ON FIRST,206' FROM L.R.P.L. MAGAZINE ****/ | 2018-06-06 | EXAMINED AREA REMOVED BRICK FROM METERBOX EXCAVATED AND REMOVED LEAD ON OUTLET SERVICE RAISED TO GRADE BACKFILLED CLEANED AREA PLACED BRICKS ALONG PROPERTY LINE BACKFILLED 2 DEPRESSION IN STREET NO LEAK OBSERVED CUSTOMER METER CONSTANT REGISTRATION LEAK ON PROPERTY LEAD ON INLET SERVICE
201801110801 | 2018-06-06 | LEAD/PLASTIC | 6126 | MEMPHIS |  | WOLK | INSPECTOR M FRAZIER STATES OUTLET NEEDS TO BE REPLACED, HE IS UNABLE TO SET METER. CONTRACTOR IS WAITING ON WATER. PLEASE REPAIR AND SET 5/8 METER. LOC ID 304191 CHANGE OUTLET SERVICE & HANDWHEEL ***HOUSE UNDER RENOVATIONS*** /** 1) MN: A234730 SN: 0091822, *TAP: SIZE: A LOC: 218 FEET FROM P LINE AT GERMAIN, *MB: CODE: ADK LOC: 217FT FROM PL GERMAIN 10' OUTSIDE P/L 3'INSIDE ****/ | 2018-06-19 | EXCAVATED AND RAISED TO GRADE 5/8 METER BOX REPAIRED LEAK ON INLET AT CURB' RAN NOW 5/8 PLASTIC TO PROPERTY' AND SET NEW 5/8 WATER METER BACKFILLED JOB AREA . LEFT VALVE OFF IN METER BOX DELAYED WAITING ON MATERIAL
201801111701 | 2018-06-06 | LEAD | 5210 | COLISEUM | DUFOSSAT | WILK | ML-METER LEAK MTR# A 363181 ACC#102364-559361 INLET SERVICE LEAK BEHIND CURBCOCK /** 1) MN: A309054 SN: 0008466, *TAP: SIZE: B LOC: 83 FEET FROM P LINE AT DUFOSSAT, *MB: CODE: CD LOC: ON COLISEUM 82.6FT FROM PL OF DUFOSSAT ****/ DOTTIE READY 10-22-18 EXP 11-11-18 NEED BACK HOE MACHINE | 2018-10-25 | ARRIVED AT ABOVE LOCATION EXAMINED EXCAVATED BY HAND AND MADE REPAIRS TO STOP LEAK ON 5/8 INLET SERVICE LINE. BACKFILLED, CLEANED UP AND WASHED DOWN WORK AREA TO COMPLETE JOB. LEAD INLET
201801112401 | 2018-06-07 | LEAD | 309 | BARONNE | GRAVIER | WOLK | ML METERLEAK MTR#D005600 ACCT#106496-530138 CONS REG ON METER /** 1) MN: D005600 SN: 0002081, *TAP: SIZE: D LOC: 51 FEET FROM P LINE AT GRAVIER, *MB: CODE: BE LOC: IN MANHOLE ****/ | 2018-06-25 | EXAMINED JOB + FOUND JOB ALREADY COMPLETED
201801115401 | 2018-06-07 | LEAD | 1035-33 | MAZANT | ST CLAUDE AV | WILK | WM- LEAK BETWEEN STREET AND SIDEWALK INLET SERVICE LEAK IN THE STREET /** AT 1033: 1) MN: SN: 0043101, *TAP: SIZE: B LOC: 234 FEET FROM P LINE AT NO. RAMPART, *MB: CODE: ADE LOC: ON MAZANT, 234' FROM P.L. NO. RAMPART, 7' OUTSIDE, ** AT 1035: 2) MN: A221581 SN: 0043101, *TAP: SIZE: B LOC: 234 FEET FROM P LINE AT ST CLAUDE, *MB: CODE: CD LOC: ON MAZANT 234' FROM P.L. ST CLAUDE ****/ | 2018-06-20 | MADE 6 X 6 CUT IN BLACK TOP STRET REPLACED 3/4 INCH INELT SERVICE FROM THE MIDDLE OF THE STREET TO METER BOX UNABLE TO GO TO WATER MAIN BECAUSE CARS WAS ON JOB SITE BACKFILLED AREA
201801116401 | 2018-06-07 | LEAD | 915 | JOURDAN AV |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 186276-570838 METER NUMBER - C 033877 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: C022384 SN: 0140906, *TAP: SIZE: C LOC: 160 FEET FROM P LINE AT BURGUNDY, *MB: CODE: ADK7 LOC: 158FT FROM PL BURGUNDY 14' OUTSIDE PL 10' INSIDE C ****/ | 2018-06-20 | EXCAVATED 4 X 8 MUD PLOT FOUND LEAK COMING BACK IN STREET REFER TO ZONE 4 TO HAVE LEAD REMOVE RENEW 1 INCH OUTLET SERVICE FROM METER BOX TO PROPERTY TIE INTO GALVANIZE PIPE BACKFILL JOB WITH RIVERSAND
201801118201 | 2018-06-07 | LEAD/PLASTIC | 2632 | ERNEST | BELGRADE | WILK | ML-METER LEAK MTR# A 327145 ACC#237947-404526 INLET SERVICE LEAK IN ASPHALT STREET NO ONE AT LOCATION SPOKE WITH NEIGHBOR AT 2630 ERNEST /** 1) MN: A327145 SN: 0174836, *TAP: SIZE: A LOC: 200 FEET FROM P LINE AT GEN MEYER, *MB: CODE: CD LOC: ON ERNEST 200FT FROM GEN MEYER ****/ | 2018-06-25 | EXAMINED AREA EXCAVATED METER INLET AND OUTLET SERVICE OBSERVED LEAK ON INLET REPAIRED LEAK BACKFILLED CLEANED AREA
201801120301 | 2018-06-08 | LEAD | 1704 | ABUNDANCE |  | WILK | ML- METER LEAK ACCCT # 140711-492303 METER # A147570 EXAMINE INLET SERVICE LEAK, ALSO CASING COVERING WHEEL /** 1) MN: A147570 SN: 0072032, *TAP: SIZE: B LOC: 53 FEET FROM P LINE AT REPUBLIC, *MB: CODE: CDL1 LOC: ON ABUNDANCE 53' FROM PL OF REPUBLIC ****/ | 2018-06-18 | EXCAVATED 3 X 2 MUD PLOT AROUND METER BOX ALSO 2 X 2 MUD AT PROPERTY RENEWED OUTLET TO PROPERTY
201801120901 | 2018-06-08 | LEAD | 501 | NASHVILLE AV | LAUREL | WILK | ML METER LEAK METER#A237022 INLET SERVICE LEAK BEHIND CURB COCK /** 1) MN: A237022 SN: 0058636, *TAP: SIZE: A LOC: 60 FEET FROM P LINE AT NASHVILLE AVE, *MB: CODE: BFHL LOC: 60FT FROM PL NASHVILLE AVE 1' OUTSIDE PL 7' INSIDE ****/ | 2018-06-11 | EXCAVATED IN BRICK SIDEWALK ON INLET LEAK MADE ALL TO STOP LEAK ON LEAD BACKFILL WITH RIVERSAND AND COLDMILL REFER TO ZONE 3 TO REMOVE LEAD
201801122401 | 2018-06-08 | LEAD/PLASTIC | 1719 | ELIZARDI BL |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 227237-406160 METER NUMBER - C034522 INLET SERVICE LEAK IN THE MUD PLOT FLOODING CURB & DRIVEWAY /** 1) MN: C023698 SN: 0134096, *TAP: SIZE: B LOC: 127 FEET FROM P LINE AT MAGELLAN, *MB: CODE: BDK2 LOC: ON ELIZARDI 123' FROM PL MAGELLAN ****/ | 2018-06-19 | EXAMINED AREA CLEANED OUTL METER BOX EXCAVATED METER BOX EXPOSED INLET AND OUTLET OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK BACKFILLED CLEANED AREA
201801124401 | 2018-06-09 | LEAD | 5164 | ST FERDINAND DR |  | WILK | LEAK IN STREET INLET SERVICE LEAKING IN THE STREET /** 1) MN: A290751 SN: 0110605, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT DREUX AVE, *MB: CODE: BDM LOC: 110FT PL DREUX AVE 6' OUTSIDE PL 10' INSIDE CURB ****/ | 2018-07-02 | EXCAVATED IN STREET WITH BOBACAT AND MUDPLOT BY HAND TO REPAIR LEAK IN THE STREET, REMOVE LEAD FROM STREET TO METER BOX AND ALSO RAISED METER TO GRADE. DNR LEAD FROM METER BOX TO MAIN BECASUE BROKEN CAR WAS NOT ABLE TO MOVE. PLASTIC FOUND ON OUTLET. 8X5 STREET CUT 4X 4 MUDPLOT CUT
201801130901 | 2018-06-11 | LEAD/PLASTIC | 3934 | BUCHANAN | CATON | WILK | MI- LEAK BETWEEN THE SIDEWALK AND THE STREET INLET SERVICE LEAK IN THE MUD PLOT BY ABANDON HOUSE FLOODING SIDEWALK & CURB /** 1) MN: A286684 SN: 0116447, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT CATON, *MB: CODE: CDL LOC: ON BUCHANAN 75' FROM PL CATON 8' OUTSIDE PL 2' INS ****/ | 2018-06-28 | EXCAVATED A 4 X 8 MUDCUT AND MADE REPAIRS ON THE INLET SERVICE AND REPLACED LEAD WITH PLASTICE FROM THE METER TO PROPERY LEAD ON THE INLET BACKFILL AND CLEANUP. JOB COMPLETE (THIS ADDRESS DOES NOT HAVE A METER)
201801134001 | 2018-06-11 | LEAD | 6127 | KUEBEL DR |  | WILK | BAD LEAK IN BOX UNABLE TO PUMP OUT FILL BACK UP CUSTOMER IS SUPPOSE TO BE MOVING IN WAITING ON WATER PLEASE REPAIR NOT SURE IF ITS UNDERGROUND ALSO SET A 3/4 METER LOCATION #177559 BAD CURBCOCK IN METER BOX ALSO SET 5/8 METER /** 1) MN: B029187 SN: 0136341, *TAP: SIZE: B LOC: 40 FEET FROM P LINE AT SHUBERT, *MB: CODE: CDM2 LOC: 40FT PL SHUBERT 8' OUTSIDE ****/ | 2018-06-14 | EXCAVATED DOWN ON INLET SERVICE.FOUND LEAD AND METER COCK WAS LEAKIN. MADE REPAIRS BY REPLACING COCK, WASHERS ASLO INSTALLED 3/4 WATER METER.
201801145701 | 2018-06-13 | LEAD | 733 | ST ANN | BOURBON | WILK | MI -CUT SERVICE **** CUSTOMER IS WITHOUT WATER.*** ENTERGY GAS ***504-595-3709*** 3700 TULANE AVE NEW ORLEANS, LA 70119 *******DAMAGE CLAIM******* (J.,GILLIAM @ 11:57AM) CUT INLET SERVICE IN STREET, AREA EXPOSED CUSTOMER OUT OF WATER, BY ENTERGY GAS /** 1) MN: A342016 SN: 0019980, *TAP: SIZE: A LOC: 77 FEET FROM P LINE AT BOURBON, *MB: CODE: CD LOC: ON ST ANN 83FT FROM BOURBON 2FT OUTSIDE ****/ | 2018-06-13 | MADE REPAIRS ON INLET SERVICE LINE STRUCK BY ENTERGY FORCE ACCOUNT ENTERGY
201801147101 | 2018-06-13 | LEAD | 7020 | JEANNETTE |  | WOLK | LOCATION ID-140792 MTR-A375003 MTR ON/CUST NOT GETTING WATER/CUST WAITING ON WATER **********L THOMPSON 14:33********** **********CUSTOMER OUT OF WATER********** OUTLET TIE IN /** 1) MN: A237903 SN: 0071465, *TAP: SIZE: B LOC: 113 FEET FROM P LINE AT AUDUBON BLVD, *MB: CODE: BDL2 LOC: ON JEANNETTE ST 94' FROM PL AUDUBON BLVD ****/ | 2018-06-13 | EXCAVATED IN CONCRETE SIDEWALK. TOOK LEAD LINE OUT. RENEW 3/4 OUTLET SERVICE PLASTIC LINE FROM METER BOX TO PROPERTY LINE. UNABLE TO MAKE REPAIR ON INLET SERVICE PLASTIC LINE. BECAUSE CONTRACTOR TURN CUSTOMER OFF AT THE WATER MAIN & COULDN'T GET CAR MOVE EITHER. REFER TO ZONE 3 TO MAKE REPAIR 1ST AM
201801148101 | 2018-06-13 | LEAD | 1800 | FLOOD | N ROMAN | WILK | WM-LEAK IN SIDEWALK ***CUSTOMER IS NOW WITHOUT WATER*** CUT INLET SERVICE BY FLEMING CONSTRUCTION CUSTOMER OUT OF WATER GETTING OFF INTO DRAIN CATCH BASIN **DAMAGE CLAIM** /** 1) MN: A214854 SN: 0134898, *TAP: SIZE: A LOC: 43 FEET FROM P LINE AT FLOOD, *MB: CODE: CDH LOC: RES ON N ROMAN 43' P/L FLOOD 6' OUTSIDE ****/ | 2018-06-13 | EXCAVATED IN MUD PLOT ON CUT SERVICE CUSTOMER OUT OF WATER ON LEAD MADE ALL REPAIRS TO STOP LEAK ALSO TO RESTORE WATER BACKFILL REFER TO ZONE 4 TO REMOVE LEAD LINE.
201801148901 | 2018-06-13 | LEAD | 5741 | DAUPHINE | CHARBONNET | WMTLK | ML- METER LEAK ACCT# 145372-493789 METER# A364654 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A221355 SN: 0076980, *TAP: SIZE: B LOC: 48 FEET FROM P LINE AT CHARBONNET, *MB: CODE: AF LOC: ON DAUPHINE 48FT FROM PL CHARBONNET ****/ | 2018-06-22 | EXCAVATED IN SIDEWALK REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA MADE 2 X 4 CUT
201801149001 | 2018-06-13 | LEAD | 3513 | ROGER WILLIAMS | TENSAS | WILK | *****************PICKUP************** INLET SERVICE LEAK /** 1) MN: A303894 SN: 0096173, *TAP: SIZE: A LOC: 50 FEET FROM P LINE AT TENSAS, *MB: CODE: BDKO LOC: ON ROGER WILLIAMS, 52' FROM P.L. TENSAS,8' OUTSIDE ****/ | 2018-06-13 | EXCAVATED IN MUDPLOT ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND.
201801150201 | 2018-06-14 | LEAD | 1115 | BURGUNDY |  | WILK | MI- CLOSE FOR REPAIR INSIDE REPAIRS ACCT# 119471-529583 METER# A328920 BAD CURB COCK PASSING OFF IN OFF POSITION, UNABLE TO CLOSE SERVICE /** 1) MN: A328920 SN: 0031536, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: AEK LOC: 96' P.L. URSULINES AVE ****/ | 2018-06-27 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK AND RENEWED OUTLET UO TO PROPERTY BACKFILLED AND CLEANED THE AREA
201801150901 | 2018-06-14 | LEAD | 6611 | MEMPHIS | FILMORE | WMLK | WM - LEAK IN THE STREET CHANGED FROM 6600BL MEMPHIS BROKEN WATER MAIN IN CONCRETE STREET GETTING OFF IN DCB 6/16/18 CAUSING POOR PRESSURE @ 6611. UPGRADE TO PRIORITY B. LEAVE IN THE SYSTEM PER INSPECTOR B. BOURNES. (PET) 06/18/18 PER S/R 12844109 LEAK IN STREET FLOODING AREA (KSW) 06/28/18 LEAK CAUSING EXTREMELY LOW PRESURE PER SR#12845127 (AJR) 07/02/18 *****CUST STATED HE HAS LITTLE TO NO WATER PRESSURE***** (KSW) /** 1) MN: C023363 SN: 0106702, *TAP: SIZE: C LOC: 75 FEET FROM P LINE AT PORTEOUS, *MB: CODE: BDM5 LOC: ON MEMPHIS 71FT FROM PL PORTEOUS 11FT OUTSIDE PL ****/ | 2018-07-02 | EXCAVATED IN STREET ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND AND COLDMILL REFERRE TO ZONE 1 TO REMOVE LEAD
201801153701 | 2018-06-14 | LEAD | 1623 | N PRIEUR |  | WILK | MI-- LEAK INSIDE METER BOX ACCT # 148391-VACANT INLET SERVICE LEAK IN MUDPLOT BY VACANT HOUSE FLOODING CURB /** 1) MN: A239106 SN: 0025426, *TAP: SIZE: B LOC: 176 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: BD LOC: 176' P.L. LAPEYROUSE ****/ | 2018-06-25 | EXCAVATED 8X 2 SIDEWALK CUT ALSO 3 X 3 MUD PLOT AROUND METER BOX RENEWED OUTLET TO PROPERTY BACKFILLED AND CLEANED THE AREA (LUNCH WAS TAKEN BETWEEN TIME ON JOB ) REFER BACK TO ZONE4 TO HAVE LEAD REMOVED FROM STREET
201801157001 | 2018-06-15 | LEAD | 5466 | ROYAL |  | WMTLK | PP- POOR PRESSURE METER # A426806 ****CUSTOEMR REQUEST CALL UPON ARRIVAL**** EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER IN LOWLNE AREA /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-06-26 | EXCAVATED 4 X 2 MUD PLOT TO CURB FOUND LEAK IN THE STREET BACKFILL AND CLEANED THE AREA TESTED OUTSIDE FAUCAT FOUND 50- PSI REFER BACK TO ZONE 4 FOR LEAK IN THE STREET
201801157201 | 2018-06-15 | LEAD | 617 | N SCOTT | TOULOUSE | WMTLK | ML- METER LEAK ACCT# 136394-721869 METER # A 413567 IF NOT FOUND PLEASE CONTACT CUSTOMER. EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER IN LOWLINE AREA /** 1) MN: A226420 SN: 0066900, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT TOULOUSE, *MB: CODE: ADK3 LOC: 104' P.L. TOULOUSE ****/ | 2018-07-03 | EXCAVATED MUD PLOT AROUND METER BOX ALSO AT PROPERTY RAISED METER BOX TO GRADE
201801158301 | 2018-06-15 | LEAD | 1616 | TRICOU | N CLAIBORNE AV | WILK | MI-LEAK IN SIDEWALK ***CALLER STATES WATER FLOODING AREA, HOUSE IS ABANDONED, NO WATER METER, BUT WATER COMING OUT OF GROUND*** INLET ON ABANDON SERVICE @ VACANT HOUSE, FLOODING LOT, CUSTOMER HAVING PROBLEMS CUTTNG GRASS DUE TO LEAK /** 1) MN: A123901 SN: 0012612, *TAP: SIZE: B LOC: 163 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: BDKO LOC: RES ON TRICOU 163FT P/L N CLAIBORNE AV 7' OUTSIDE ****/ | 2018-06-26 | FOUND LEAK COMING FROM STREET REFER BACK TO ZONE 4 FOR LEAK IN STREET
201801159301 | 2018-06-15 | LEAD/PLASTIC | 3485 | WALL BL | HORACE | WILK | WM LEAK BETWEEN STREET & SIDEWALK INLET SERVICE LEAK IN MUDPLOT FLOODING CURB /** 1) MN: A345516 SN: 0164777, *TAP: SIZE: A LOC: 12 FEET FROM P LINE AT CYPRESS ACRES DR, *MB: CODE: __ LOC: ON WALL 25FT FROM PL CYPRESS ACRES 9FT OUTSD PL ****/ | 2018-06-25 | EXAMINED AREA EXCAVATED IN MUD PLOT ON INLET AND OUTLET SERVICE TRACED LINE ON INLET SERVICE EXPOSED LEAK ON INLET SERVICE REPAIRED LINE BACKFILLED CLEANED SITE
201801162001 | 2018-06-16 | LEAD/PLASTIC | 1246 | LEBOUEF | LAMARQUE | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-06-19 | EXAMINED AREA PUMPED DOWN WATER EXCAVATED METER EXPOSED LEAKS ON INLET SERVICE LINE OBSERVED LEAD ON OUTLET SERVICE REPLACED OLD METER BOX AND LEAD LINE TO PROPERTY WITH NEW SET UP AND RAISED TO GRADE LEFT 2 BARRICADES ON TOP DRESSED WITH SAND
201801166701 | 2018-06-18 | LEAD | 2600 | ARTS | LAW | WMTLK | WM-LEAK ON THE SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A266553 SN: 0090256, *TAP: SIZE: A LOC: 11 FEET FROM P LINE AT LAW, *MB: CODE: ADN1 LOC: 11FT FROM PL LAW 8' OUTSIDE PL 2' INSIDE CURB. ****/ | 2018-06-29 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201801168701 | 2018-06-19 | LEAD | 2527 | A P TUREAUD AV | LAW | WMBK | LOCATIONID#202999-490510 METER#A248942 UPPER METERBOX CASING BROKEN /** 1) MN: A226231 SN: 0067013, *TAP: SIZE: A LOC: 124 FEET FROM P LINE AT LAW, *MB: CODE: __ LOC: ON LONDON 197' FROM PL OF LAW ** 2) MN: A248942 SN: 0067013, *TAP: SIZE: B LOC: 124 FEET FROM P LINE AT LAW, *MB: CODE: __ LOC: ON A P TUREAUD 124FT FROM PL LAW 6FT OUTSD PL ****/ | 2018-07-02 | REPLACED UPPER METER BOX CASING
201801173301 | 2018-06-19 | LEAD/PLASTIC | 1160 | MAGAZINE | ERATO | WMTLK | MI- LEAK IN THE SIDEWALK. * CALLER STATES WATER IS SHOOTING OUT* EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER BUILDING UNDER CONSTRUCTION /** 1) MN: A151302 SN: 0003239, *TAP: SIZE: B LOC: 145 FEET FROM P LINE AT ERATO, *MB: CODE: __ LOC: 2ND METER FROM CURB ON MAGAZINE BET. CALLIOPE & ER ****/ | 2018-06-27 | EXAMINED AREA PUMP DOWN WATER EXPOSED LEAK ON INLET SERVICE REPAIRED LAK BACKFILLED AND CLEANED AREA
201801174201 | 2018-06-19 | LEAD | 2010 | MILAN | DANNEEL | WILK | MI- LEAK ON THE SIDEWALK IN FRONT OF HOUSE INLET SERVICE LEAK BAD BLEEDER VALVE FLOODING SIDEWALK, GUTTER BOTTOM & GRASSY AREA /** 1) MN: A331347 SN: 0056085, *TAP: SIZE: A LOC: 175 FEET FROM P LINE AT RAMPART S, *MB: CODE: AMFK LOC: ON MILAN,173.5' FROM U.S.P.L. SO. RAMPART ****/ DOTTIE READY 8-17-18 EXP 9-6-18 | 2018-08-17 | (IN-LET LEAK)REPLACED 5/8 CUB COCK TIED INTO LEAD.(SOC 3FT .X 3FT. S/W)
201801177501 | 2018-06-20 | LEAD/PLASTIC | 542 | WAGNER |  | WMRE | LOCATION: 226476 MTR# A 374305 PER INSP L MITCHELL - UNABLE TO LOCATE METER. PLEASE LOCATE AND RAISE TO GRADE ALSO REMOVE LEAD. LOCATE, MARK & RAISE METER TO GRADE /** 1) MN: A252009 SN: 0102048, *TAP: SIZE: A LOC: 16 FEET FROM P LINE AT EVELINA, *MB: CODE: CD LOC: ON WAGNER, 16' FROM P.L. EVELINA, 8' OUTSIDE P.L. ****/ | 2018-08-10 | ARRIVED ON JOB SITE EXAMINE AREA FOR METER EXCAVATED IN MUD PLOT SET UP NEW METER BOX COMPLETE AND RAISE TO GRADE BACKFILLED DRESS UP WORK SITE
201801178201 | 2018-06-20 | LEAD/PLASTIC | 517 | DIANA |  | WILK | **********PICK UP********** INLET SERVICE LEAK IN THE MUD PLOT NEAR ELECTIC POLE FLOODING DRIVEWAY /** 1) MN: SN: 0108072, *TAP: SIZE: A LOC: 119 FEET FROM P LINE AT NUNEZ, *MB: CODE: CDK2 LOC: ON DIANA, 119' FROM P.L. NUNEZ, 8' OUTSIDE P.L. ****/ | 2018-07-13 | WE EXCAVATED TO MAKE REPAIRS TO A 3/4 INLET WE BACKFILL PLUS
201801179701 | 2018-06-20 | LEAD | 803 | DESIRE |  | WILK | L UDUEBOR STATES SERVICE IS LEAKING FROM BLEEDER VALVE. PLEASE REPAIR METER A416897 LOC ID 176989 INLET SERVICE LEAK BAD BLEEDER VALVE /** 1) MN: A115208 SN: 0023858, *TAP: SIZE: A LOC: 57 FEET FROM P LINE AT DAUPHINE, *MB: CODE: AE23 LOC: 51FT FROM PL DAUPHINE ON DESIRE ****/ | 2018-07-06 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET ,OUTLET HAS PLASTIC LINE UP TO PROPERTY BACKFILLED JOB WITH RIVERSAND , COLDMILL
201801183701 | 2018-06-21 | LEAD/PLASTIC | 1928 | L B LANDRY AV | SHEPARD | WILK | PP POOR PRESSURE METER# A378628 ACCT# 239163-405909 INLET SERVICE LEAK IN THE MUD PLOT CAUSING POOR PRESSURE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-07-11 | WE EXCAVATED TO MAKE REPASIR TO A 5/8 HAND WHEEL WE BACKFILL PLUS CLEAN UP
201801191901 | 2018-06-22 | LEAD/PLASTIC | 4338 | ST CHARLES AV | NAPOLEON AV | WILK | MI - LEAK AT CURB NEAR TREE *************L.THOMPSON @ 12:04PM************** INLET SERVICE LEAK IN MUDPLOT COMING OUT MANHOLE NEAR TREE /** 1) MN: C017962 SN: 0098957, *TAP: SIZE: C LOC: 76 FEET FROM P LINE AT NAPOLEON AVE, *MB: CODE: ADLM LOC: ON ST CHARLES AVE 74' FROM PL NAPOLEON AVE 12' OUT ** 2) MN: D006896 SN: 0093413, *TAP: SIZE: C LOC: 20 FEET FROM P LINE AT NAPOLEON AVE, *MB: CODE: BDHP LOC: IN M/H ON NAPOLEON 29FT FROM PL OF ST CHARLES AVE ****/ DOTTIE READY 6-27-18 EXP 7-17-18 | 2018-06-27 | EXAMINEE WATER LEAK AT ABOVE LOCATION FOUND 1 1/2 SERVICE LEAKING.REPLACED 12 FT. OF 1 1/2 TUBING TIED INTO 1 1/2 PLASTIC TUBING.
201801195401 | 2018-06-22 | LEAD/PLASTIC | 2304 | FARRAGUT | AMAZON | WILK | WM-LEAK ON THE SIDEWALK FLOODING AREA INLET SERVICE LEAK AT MAIN FLOODING AREA NEXT TO 3110 FARRAGUT CUSTOMER OUT OF WATER SPOKE WITH CUSTOMER /** 1) MN: A234377 SN: 0137786, *TAP: SIZE: __ LOC: 0 FEET FROM P LINE AT FARRAGUT, *MB: CODE: BDL1 LOC: 59FT FROM P.L. AMAZON ****/ | 2018-06-22 | EXCAVATED IN MUDPLOT REPAIR 1INCH 1/2 LEAD LINE DRESS UP WITH RIVERSAND JOB REF TO ZONE 6 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201801199101 | 2018-06-25 | LEAD | 435 | BOURBON | ST LOUIS | WOLK | ACCT# 104860-527585 MTR# A266149 INSPECTOR FOUND CONSTANT REGISTRATION ON METER. /** 1) MN: A266149 SN: 0040827, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT ST LOUIS, *MB: CODE: BE LOC: ON BOURBON 47FT FROM URPL OF ST LOUIS ****/ | 2018-07-09 | EXAMINED JOB AT ABOVE LOCATION AND FOUND NO CONSTRANT NO VISIBLE STOP AND WAS GATE LOCK
201801199801 | 2018-06-25 | LEAD | 1704 | CONTI | N CLAIBORNE AV | WILK | WM-LEAK IN SIDEWALK CHANGED FROMO 1700 CONTI INLET ON ABANDON SERVICE NO METER IN BOX, ALSO REPLACED METER BOX COVER /** 1) MN: SN: 0005913, *TAP: SIZE: A LOC: 33 FEET FROM P LINE AT N CLAIBORNE AVE, *MB: CODE: __ LOC: ON CONTI 33FT FROM USPL OF N CLAIBORNE AVE ****/ | 2018-07-12 | MADE 2 X 4 SIDEWALK CUT WITH HAND AND MADE REPAIR ON 3/4 COPPER LINE FOR ABANDON LOT BACKFILLED AREA. JOB COMPLETE
201801203501 | 2018-06-25 | LEAD | 1124 | FLOOD | MARAIS | WILK | ML: METER LEAK, MTR # A349838, ACCT #167088-423216 INLET SERVICE LEAK IN MUDLOT NEAR METER RUNNING INTO STREET /** 1) MN: A246247 SN: 0107952, *TAP: SIZE: B LOC: 42 FEET FROM P LINE AT MARAIS, *MB: CODE: BD LOC: ON FLOOD 42FT FROM PL MARAIS 7.5' OUTSIDE PL ****/ | 2018-07-10 | EXCAVATED IN MUD PLOT AND REPLACED 3/4 INCH CURB COCK BACKFILLED AREA
201801205401 | 2018-06-25 | LEAD | 2232 | ST ANN |  | WILK | LOCATION: 305240 PER INSP L UDEBOR - BURIED SERVICE LINE, HOUSE UNDER CONSTRUCTION AND VACANT. PLEASE REPAIR AND SET 5/8 METER RENEW INLET SERVICE ALSO SET 5/8 METER /** 1) MN: A251899 SN: 0052178, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT MIRO N, *MB: CODE: CDL1 LOC: 49' P.L. N MIRO ****/ | 2018-07-06 | EXCAVATED 2 X 8 MUD PLOT SET ONE METER BOX COMPLETER LEAD LINE FROM MAIN TURNED OFF BACKFILLED AND CLEANED THE AREA ONE 5/8 INCH METER WAS SET *****REFER BACK TO ZONE 4 TO HAVE LEAD LINE REMOVED******
201801207601 | 2018-06-26 | LEAD | 1819 | ESPLANADE AV |  | WOLK | ML METER LEAK MTR#E008286 LOC#223092-487969 CONST REG ON METER /** 1) MN: C019694 SN: 0061476, *TAP: SIZE: D LOC: 170 FEET FROM P LINE AT ROMAN N, *MB: CODE: AE2 LOC: ON ESPLANADE 170FT FROM PL ROMAN ****/ | 2018-07-03 | EXAMINED JOB AND FOUND NO CONSTRANT REGISTRATION. (JOB COMPLETE)
201801208501 | 2018-06-26 | LEAD | 624 | BOURBON |  | WILK | MI- INLET SERVICE LEAK ***HOLE EXPOSED*** ****************B LEAVE IN SYSTEM****************** INLET @ THE MAIN INTERFERING WITH CONTRACTORS WORK, HOLE OPEN /** 1) MN: D006979 SN: 0171339, *TAP: SIZE: D LOC: 187 FEET FROM P LINE AT TOULOUSE, *MB: CODE: AEM1 LOC: IN MAN HOLE ON BOURBON,187' FROM P.L. TOULOUSE,4' ****/ | 2018-06-27 | MADE REPAIR ON 1 1/2 CORPORATION COCK + REPLACED 1 1/2 BEND ADAPTER AT ABOVE LOCATION
201801210101 | 2018-06-26 | LEAD | 2616 | N TONTI | FRANKLIN AV | WILK | ML-METER LEAK ACCT#304549-719249 METER#A302360 ********CUST HAS POOR PRESSURE INLET SERVICE LEAK CUSTOMER HAS GOOD PRESSURE ****HOUSE UNDER CONSTRUCTION***** /** 1) MN: A302360 SN: 0069184, *TAP: SIZE: A LOC: 124 FEET FROM P LINE AT PAINTERS, *MB: CODE: BDO2 LOC: ON NO. TONTI,123.5' FROM P.L. PAINTERS,8' OUTSIDE ****/ | 2018-07-02 | EXCAVATED 4 X 6 LIMESTONE GUTTER BOTTOM FOUND LEAK COMING FURTHER IN STREET REFER TO ZONE 4 TO LEAD REMOVE FROM STREET RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILL JOB WITH RIVERSAND COLDMILL
201801210301 | 2018-06-26 | LEAD/PLASTIC | 3807 | PERRIER | PENISTON | WMTLK | ML-METER LEAK EXAMINE INLET & OUTLET SERVICE FOR A LEAK SIDEWALK FLOODED METER BOX UNDER WATER /** 1) MN: A266847 SN: 0013184, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT PENISTON, *MB: CODE: AEM3 LOC: 93FT FROM UPL PENISTON ****/ | 2018-06-26 | EXCAVATED IN BRICK SIDEWALK ON INLET LEAK MADE ALL REPAIR TO STOP LEAK ON LEAD BACKFILL EITH RIVERSAND AND COLD MILL REFER TO ZONE 3 TO REMOVE LEAD
201801211001 | 2018-06-26 | LEAD | 2005 | PORT |  | WILK | ML- METER LEAK MTR# A366207 ACCT# 132719- INLET SERVICE PASSING WATER IN OFF POSITION, CON REG FOUND OFF /** 1) MN: A303978 SN: 0072581, *TAP: SIZE: A LOC: 41 FEET FROM P LINE AT JOHNSON N, *MB: CODE: BDM5 LOC: 42FT FROM PL N JOHNSON ****/ | 2018-07-05 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA ***2005 PORT IS NOW A SINGLE HOUSE.
201801212201 | 2018-06-26 | LEAD/PLASTIC | 2352 | LAUREL | 1ST | WILK | ML-METER LEAK ACCT# 128031-556655 METER # A292434 INLET SERVICE SERVICE /** 1) MN: A292434 SN: 0054764, *TAP: SIZE: A LOC: 108 FEET FROM P LINE AT FIRST, *MB: CODE: BEK6 LOC: ON LAUREL 107FT FR LRPL FIRST ****/ | 2018-07-11 | EXAMINED AREA CLEANE OUT METER BOX OBSERVED LEAK ON INLET SERVICE EXCAVATED ON INLET SERVICE REPAIRED LEAK BACKFILLED TESTED METER AND CLEANED AREA
201801215901 | 2018-06-27 | LEAD | 819 | MAZANT |  | WILK | LOCATION ID-119354 MTR-A369324 BAD MTR LEAK/AREA FLOODED EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A264878 SN: 0031624, *TAP: SIZE: A LOC: 131 FEET FROM P LINE AT DAUPHINE, *MB: CODE: BFK LOC: ON MAZANT 131FT FROM PL OF DAUPHINE ****/ | 2018-07-13 | REMOVED BRICK WORK IN SIDEWALK EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED AREA STACK BRICK ON CUSTOMER PROPERTY
201801216601 | 2018-06-27 | LEAD | 4219 | N JOHNSON | FRANCE | WMTLK | ML- SLOW LEAK AT METER PER INSPECTOR MTR # A-426114 ACCT # 257638-713264 /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-07-11 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA. JOB COMPLETE
201801220201 | 2018-06-28 | LEAD/PLASTIC | 823 | DE ARMAS |  | WOLK | ML-- METER LEAK METER # A401753 ACCT # 237282-720546 ***********S.SLACK @ 9:20AM************ REPLACE HANDWHEEL, CURB COCK AND WHEEL NOT LINING UP, CUSTOMER OUT OF WATER /** 1) MN: SN: 0057913, *TAP: SIZE: B LOC: 15 FEET FROM P LINE AT ELMIRA, *MB: CODE: CD LOC: ON DE ARMAS 15' FROM P.L. ELMIRA 5' OUTSIDE 12' ****/ | 2018-06-28 | EXCAVATED ON THE INLET AND OUTLET SERVICE AND RE PAIR THEN WE BACKFILL AND CLEAN UP JOB SITE
201801221001 | 2018-06-28 | LEAD | 3225 | TOULOUSE | N RENDON | WILK | MI-LEAK AT THE SIDEWALK EXAMINE INLET SERVICE FOR LEAK ON SIDEWALK /** 1) MN: A198978 SN: 0060066, *TAP: SIZE: B LOC: 185 FEET FROM P LINE AT RENDON N, *MB: CODE: BDKO LOC: ON TOULOUSE BET HAGAN/RENDON 186' P/L N RENDON 8' ****/ | 2018-07-12 | MADE 4 X 8 TRENCH CUT IN SIDEWALK WITH HAND MALL AND REPLACED OUTLET TO PROPERTY TIED INTO COPPER BACKFILLED AREA. (JOB COMPLETE)
201801223401 | 2018-06-28 | LEAD | 4986 | CORINNE |  | WILK | LOCATION ID-180038 MTR-A240502 LEAK AT AND AROUND METER INLET SERVICE LEAK IN THE MUD PLOT COMING FROM BAD BLEEDER VALVE /** 1) MN: A240502 SN: 0132110, *TAP: SIZE: B LOC: 707 FEET FROM P LINE AT PRESSBURG, *MB: CODE: BD24 LOC: ON CORINNE, 707' FROM P.L. PRESSBURG, 8' OUTSIDE, ****/ | 2018-07-17 | MADE A 3X4 CUT IN CONCRETE STREET. EXCAVATED DOWN ON INLET SERVICE IN STREET AND MUDPLOT. FOUND PLASTIC AND LEAD SERVICE. EVERY TIME REPAIRS WAS MADE SERVICES STARTED LEAKING FROM FURTHER BACK IN STREET. DIDNT HAVE ENOUGH TIME TO COMPLETE.
201801223501 | 2018-06-28 | LEAD/PLASTIC | 1724 | MURL | LAWRENCE ST | WMTLK | ML METER LEAK ACCT# 226154-406734 METER# A384097 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: A288899 SN: 0135964, *TAP: SIZE: B LOC: 153 FEET FROM P LINE AT MAGELLAN, *MB: CODE: BDK2 LOC: ON MURL 153' FROM PL MAGELLAN 8' OUTSIDE PL 4' IN ****/ | 2018-08-01 | EXAMINED AREA CLEANED OUT METER BOX EXCAVATED ON INLET AND OUTLET SERVICE OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK LEAD ON INLET BACKFILLED CLEANED AREA
201801223801 | 2018-06-28 | LEAD/PLASTIC | 2849 | GEN COLLINS AV |  | WILK | ML- METER LEAK MTR#C007073 ACCT# 232625-408955 INLET SERVICE LEAK 07/02/18 PER S/R 12845450 POOR PRESSURE (KSW) /** 1) MN: C007073 SN: 0146807, *TAP: SIZE: C LOC: 160 FEET FROM P LINE AT MAC ARTHUR BLVD, *MB: CODE: CDHK LOC: ON GEN. COLLINS AVE., 142' FROM P.L. MAC ARTHUR ****/ | 2018-07-03 | EXAMINED AREA PUMP DOWN WATER EXCAVATED TO EXPOSED INLET LEAK REPAIRED LEAK BACKFILLED CLEANED AREA
201801224301 | 2018-06-28 | LEAD | 3023 | CHARTRES | MONTEGUT | WMTLK | WM LEAK IN THE STREET EXAMINE INLET/OUTLET SERVICE FOR LEAK INSIDE MANHOLE /** 1) MN: E006794 SN: 0140151, *TAP: SIZE: E LOC: 225 FEET FROM P LINE AT MONTEGUT, *MB: CODE: E24 LOC: ON CHARTRES, 225' FROM P.L. MONTEGUT, 5' OUTSIDE, ****/ | 2018-07-13 | EXAMINED JOB AND PUMPED MANHOLE DOWN AND TIGHEN UNION UP ON 2 INCH INLET
201801228001 | 2018-06-29 | LEAD | 1424 | N ROMAN |  | WILK | WM - LEAK ON THE SIDEWALK EXAMINE INLET SERVICE FOR LEAK @ PROPERTY LINE CON REG /** 1) MN: B030187 SN: 0057296, *TAP: SIZE: B LOC: 147 FEET FROM P LINE AT KERLEREC, *MB: CODE: CEK LOC: ON N ROMAN 147FT FROM URPL OF KERLEREC ****/ | 2018-07-05 | EXCAVATED 2 X 6 CONCRETE SIDEWALK FOUND LEAK ON 3/4 INCH OUTLET SERVICE RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILL JOB WITH RIVERSAND COLDMILL
201801228101 | 2018-06-29 | LEAD | 4534 | URQUHART | JAPONICA | WILK | ML METER LEAK METER # A427922 ACCOUNT # 304731-492595 EXAMINE INLET SERVICE FOR LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-07-11 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 1 INCH INLET SERVICE BACKFILLED AREA
201801230601 | 2018-06-29 | LEAD | 1945 | INDUSTRY | ANNE MARIE CT | WILK | WM-LEAK IN SIDEWALK INLET ON ABANDON SERVICE INFRONT VACANT LOT, NO METER IN BOX /** 1) MN: A338098 SN: 0100739, *TAP: SIZE: A LOC: 11 FEET FROM P LINE AT ANNETTE, *MB: CODE: ADK LOC: ON INDUSTRY 11' FROM PL ANNETTE 8' OUTSIDE PL ****/ | 2018-07-10 | MADE 2 X 4 CUT IN SIDEWALK AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED AREA NO METER IN BOX
201801234101 | 2018-06-29 | LEAD | 1105 | DUBLIN | ZIMPEL | WILK | ML - METER LEAK ACCT#123463587467 METER#A427402 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A256928 SN: 0043197, *TAP: SIZE: A LOC: 38 FEET FROM P LINE AT ZIMPLE, *MB: CODE: BDN1 LOC: ON DUBLIN,36.5' FROM S.P.L. ZIMPLE ****/ | 2018-08-13 | EXCAVATED AND FOUND NO LEAKS BOTH INLET / OUTLET SERVICES. CLEANED AND DRESSED UP AREA. FROND LEAD ON INLET / OUTLET.
201801234201 | 2018-06-29 | LEAD/PLASTIC | 1754 | L B LANDRY AV |  | WILK | WM -LEAK IN THE SIDEWALK *********LEAVE IN SYSTEM******** INLET SERVICE LEAK IN FRONT OF ABANDON LOT @ CURB GETTING OFF IN DCB LEFT ONE CONE @ SITE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-07-25 | EXAMINED AREA SEARCHED FOR POSSIBLE METER BOX OR SERVICE EXCAVATED IN SIDEWALK EXCAVATED DOWN TO MAIN SERVICE 6" REPAIRED LEAK IN PROCERS LINE WAS PULLED IT WAS ATTACH TO ROOTS DURING EXCAVATION ATT LINE WHOLE WAS LEFT EXPOSED BARRACADED NEED SAND AND COAL MILL CLEANED AREA
201801239201 | 2018-07-02 | LEAD | 5436 | PRESS DR |  | LKST | LEAK IN THE STREET /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-07-13 | EXCAVATED IN TREE ROOTS BY HAND FOUND LEAK ON 3/4 LED
201801239301 | 2018-07-02 | LEAD | 3225-27 | DUMAINE | HAGAN AV | WILK | ML METER LEAK ACCOUNT # 126109-521631 METER # 395864 INLET SERVICE LEAKING INTO METER BOX, ALSO CASHING HAS SHIFTED /** AT 3225: 1) MN: A252443 SN: 0049539, *TAP: SIZE: A LOC: 107 FEET FROM P LINE AT HAGAN AVE, *MB: CODE: CD2M LOC: ON DUMAINE,107' FROM L.R.P.L. NO. HAGAN AVE. ****/ | 2018-07-12 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 5/8 INCH HAND WHEEL REPLACE GUTS IN WHEEL BACKFILLED AREA. JOB COMPLETE
201801239901 | 2018-07-02 | LEAD | 601 | WEBSTER | PATTON | WILK | ML-METER LEAK ACCT#110584-702698 METER#A428928 BAD BLEEDER VALVE /** 1) MN: A271461 SN: 0011654, *TAP: SIZE: B LOC: 84 FEET FROM P LINE AT WEBSTER, *MB: CODE: BDH3 LOC: ON PATTON 84FT FROM WEBSTER ****/ DOTTIE READY 7-10-18 EXP 7-30-18 | 2018-07-15 | EXCAVTED 3X 3 MUDPLOT .REPLACED 5/8 METER BOX TO STOP LEAK.BACKFILLED AND CLEANED THE AREA.
201801240702 | 2018-07-19 | LEAD | 4718 | PARIS AV | WICKFIELD DR | WILK | INLET SERVICE LEAK FLOODING CURB ( TRUCK PARKED ON SITE ) /** 1) MN: E006771 SN: 0105603, *TAP: SIZE: E LOC: 225 FEET FROM P LINE AT PARIS AVE, *MB: CODE: OOOO LOC: ON WAKEFIELD 225' FROM P.L. PARIS AVE 11' OUTSIDE ****/ | 2018-08-23 | EXCAVATED IN THE ASPHALT STREET AND CONCRETE SIDEWALK AND FOUND THE LEAK ON THE INLET SERVICE. NEED TO REPLACE THE LEAD LINE FROM MAIN TO PROPERTY. PUT 4 BARRELS AND 1 FLAG [JOB CONTINUE ]
201801241601 | 2018-07-02 | LEAD | 2536 | ANNETTE | LAW | WMTLK | MI - LEAK IN STREET EXAMINE INLET & OUTLET SERVICE FOR A LEAK IN THE STREET /** 1) MN: A227691 SN: 0080736, *TAP: SIZE: B LOC: 262 FEET FROM P LINE AT N DORGENOIS, *MB: CODE: ADK LOC: ON ANNETTE 262' FROM PL N DORGENOIS 9' OUTSIDE PL ****/ | 2018-07-12 | EXCAVATED 6 X 3 STREET CUT ALSO 4 X 4 MUD PLOT RELOCATED METER TO SIDEWALK AND MADE REPAIRS ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201801242101 | 2018-07-02 | LEAD/PLASTIC | 3701 | PITTARI PL | BERKLEY DR | WILK | ML - METER LEAK ACCOUNT NUMBER - 228358-420379 METER NUNBER - A366703 INLET SERVICE LEAK /** 1) MN: SN: 0120688, *TAP: SIZE: B LOC: 694 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: AD LOC: ON PITTARI PL 694' FROM PL BERKLEY DR 7' OUTSIDE P ****/ | 2018-07-10 | ARRIVED ON JOB SITE EXAMINE LEAK COMING FROM METER BOX EXCAVATED BY HAND MADE REPAIRS BACKFILLED DRESS WORK SITE
201801242601 | 2018-07-02 | LEAD/PLASTIC | 8205 | FRERET | DUBLIN | WILK | ML= METER LEAK METER # A299467 ACCT# 111564-564452 EXAMINE INLET SERVICE FOR LEAK 9/27/18 LEAK BETWEEN MTR & STOP & WASTE. CONST. REG ON THE METER. PER S/R # 12853048 (PET) /** 1) MN: A299467 SN: 0013027, *TAP: SIZE: A LOC: 56 FEET FROM P LINE AT DUBLIN, *MB: CODE: CDN1 LOC: FIRST METER ON FRERET 56' P.L. DUBLIN ****/ | 2019-02-06 | MADE A 2 X 8 MUDCUT EXCAVATED AND MADE REPAIS ON A 3/4 INLET FROM THE METER TO PROPERTY.
201801244701 | 2018-07-03 | LEAD | 8628 | CASTLE CT | GAWAIN DR | WMLK | ******************PICKUP****************** LEAK ON THE MAIN @ VACANT LOT NEXT TO ABOVE ADDRESS FLOODING CURB /** 1) MN: A341751 SN: 0134504, *TAP: SIZE: A LOC: 205 FEET FROM P LINE AT GAWAIN DR, *MB: CODE: CDLM LOC: RES 185' P/L GAWAIN DR 8' OUTSIDE 2' INSIDE CURB ****/ | 2018-07-09 | EXCAVATED IN CONCRETE DRIVEWAY. REPAIR 1INCH LEAD CONTROL LINE. DRESS UP WITH RIVERSAND & COLDMILL REFER TO ZONE 5 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201801244702 | 2018-07-09 | LEAD | 8628 | CASTLE CT | GAWAIN DR | WILK | REFER TO ZONE 5 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX /** 1) MN: A341751 SN: 0134504, *TAP: SIZE: A LOC: 205 FEET FROM P LINE AT GAWAIN DR, *MB: CODE: CDLM LOC: RES 185' P/L GAWAIN DR 8' OUTSIDE 2' INSIDE CURB ****/ | 2018-07-29 | FOUND JOB COMPLETED
201801246001 | 2018-07-03 | LEAD | 2471 | ROYAL | ST ROCH AV | WILK | ML-METER LEAK MTR# A 303442 ACC#115927-480253 EXAMINE INLET SERVICE INSIDE METER BOX ON THE SIDEWALK /** 1) MN: A303442 SN: 0048254, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT ST ROCH AVE, *MB: CODE: BFMN LOC: 75' P.L. ST ROCH AVE ****/ | 2018-07-16 | MADE 4 X 4 SIDEWALK CUT AND REPLACED OUTLET FROM METER BOX TO PROPERTY TIED INTO GALVENIZED BACKFILLED AREA
201801247601 | 2018-07-03 | LEAD | 3011 | ST CLAUDE AV | MONTEGUT | WILK | WM- LEAK IN THE SIDEWALK INLET SERVICE LEAK IN MUDPLOT BUBBLING UP ABOVE GROUND 07/11/18 LEAK HAS GOTTEN WORSE NOW CAUSING A DEPRSSION PER SR#12846220 (AJR) /** 1) MN: 000000 SN: 0041044, *TAP: SIZE: A LOC: 83 FEET FROM P LINE AT MONTEGUT, *MB: CODE: AFL1 LOC: ON ST CLAUDE AVE 83FT FROM PL OF MONTEGUT ****/ | 2018-07-13 | ARRIVED AT ABOVE LOCATION EXCAVATED IN MUD PLOT CLOSE TO PROPERTY FOUND 3/4 INCH LEAD LINE LEAKING + REPAIRED IT METER BOX ON PROPERTY LIKE OUTLET COPPER BACKFILLED + CLEANED AREA
201801248501 | 2018-07-03 | LEAD/PLASTIC | 4437 | KENNON AV |  | WILK | MI- SEE WHY NO WATER ACCOUNT # 171841-498509 METER# A428246 /** 1) MN: A278038 SN: 0114830, *TAP: SIZE: A LOC: 121 FEET FROM P LINE AT OWENS BLVD, *MB: CODE: ADN2 LOC: ON KENNON AVE., 121' FROM P.L. OWENS BLVD., 7' OUT ****/ INLET SERVICE LEAKING CAUSING POOR PRESSURE 10 PSI AT OUTSIDE FAUCET | 2018-07-04 | EXCVATED IN 3 X 5 CUT IN STREET AND DRIVEWAY OVER 5/8 INLET SERVICE.MADE REPAIR ON LEAD LINE AND TIED BACK INTO PLASTIC GOING TO METER BOX.
201801248901 | 2018-07-04 | LEAD | 1609 | DELERY | NINA | WILK | WM LEAK ON THE SIDEWALK ***********M.ROBINSON @ 11:31AM************** CUT INLET ON ABANDON SERVICE @ VACANT LOT NEXT TO ABOVE ADDRESS BY UNKNOWN CONTRACTORS FLOODING SIDEWALK /** 1) MN: SN: 0108419, *TAP: SIZE: A LOC: 72 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: ADL4 LOC: MTR ON DELERY 72FT FROM PL CLAIBORNE 8FT OUTSIDE ****/ | 2018-07-04 | FOUND ABANDON SERVICE CUT.INSTALLED STOP COCK AND BURRIED LINE.
201801251301 | 2018-07-05 | LEAD | 2138 | SPAIN | N MIRO | WILK | **********PICK UP********** INLET SERVICE LEAK ON ABANDON SERVICE IN FRONT VACANT LOT /** 1) MN: SN: 0109868, *TAP: SIZE: A LOC: 39 FEET FROM P LINE AT NO. MIRO, *MB: CODE: ADLM LOC: ON SPAIN, 38.5' FROM P.L. NO. MIRO, 7.5' OUTSIDE ****/ | 2018-07-12 | EXCAVATED 4 X 4 MUD PLOT RAISED METER BOX TO GRADE AND REPAIRED INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA (JOB COMPLETE)
201801253401 | 2018-07-05 | LEAD | 2415 | ST CHARLES AV |  | WMTLK | LOCATION ID-105021 MTR-B027853 MTR LEAK/AREA FLOODED EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER, FLOODING GRASS /** 1) MN: B027853 SN: 0007679, *TAP: SIZE: B LOC: 110 FEET FROM P LINE AT FIRST, *MB: CODE: CDN LOC: CURB NEAR WALK ****/ DOTTIE READY 8-16-18 EXP 9-5-18 | 2018-08-19 | ARRIVED ON JOB SITE EXAMINE LEAK IN MUD PLOT EXCAVATED BY HAND MADE ON SERVICE AND SET UP NEW METER BOX COMPLETE BACKFILLED DRESS UP
201801254301 | 2018-07-05 | LEAD | 2019 | FRANKLIN AV | N GALVEZ | WMTLK | ML-METER LEAK EXAMINE INLET AND OUTLET SERVICE INSIDE METER BOX, WATER FLOODING METER BOX & FILLED WITH SAND FLOODING SIDEWALK /** 1) MN: A334434 SN: 0067730, *TAP: SIZE: B LOC: 145 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CDLN LOC: ON FRANKLIN AVE 145' FROM N JOHNSON ****/ | 2018-07-26 | EXCAVATED 4 X6 SIDEWALK CUT USED CLAMP ON 1 1/2 INCH CONTROLLING LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801255201 | 2018-07-06 | LEAD | 5725 | WINGATE DR | PRENTISS AV | WILK | LEAK IN S/W /** 1) MN: A297257 SN: 0106783, *TAP: SIZE: A LOC: 295 FEET FROM P LINE AT PRENTISS AVE, *MB: CODE: ADLZ LOC: ON WINGATE DR., 295' FROM P.L. PRENTISS AVE., 7' ****/ | 2018-07-05 | EXCAVATED A 4X11 CONCRETE CUT IN THE SIDEWALK MADE REPAIRS ON THE INLET SERVICE STOP THE LEAK AND ALSO HER METER WAS CHOKE AND WE REPLACE THE METER WITH ANEW 1'' BACK FILL CLEAN-UP JOB COMPLETE LEAD ON INLET AND OUTLET ************OLD METER INFO************** METER:A297257 FAC:50334026 MAKE:SENSUS READ:195
201801256501 | 2018-07-06 | LEAD | 1218 | FRANCE | MARAIS | WMTLK | ML - METER LEAK ACCIOUNT NUMBER - 186775-431046 METER NUMBER - A304195 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: C016902 SN: 0142796, *TAP: SIZE: C LOC: 173 FEET FROM P LINE AT MARAIS, *MB: CODE: BEL2 LOC: ON FRANCE 171FT FROM PL OF MARAIS 6FT OUTSIDE PL ****/ | 2018-07-17 | EXCAVATED 2 X 6 CONCRETE DRIVEWAY FOUND LEAK ON 1 INCH INLET SERVICE MADE REPAIRS ON INLET AND OUTLET HAS COOPER LINE UP TO PROPERTY BACKFILLED JOB WITH RIVERSAND COLDMILL NO LEAK O OUTLET
201801256901 | 2018-07-06 | LEAD | 4801 | KENDALL DR | METROPOLITAN DR | WILK | ML- METER LEAK ACCT# 169809-469175 MTR# A430382 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A294209 SN: 0112004, *TAP: SIZE: A LOC: 512 FEET FROM P LINE AT METROPOLITAN, *MB: CODE: CD LOC: 512FT PL METROPOLITAN 7' OUTSIDE ****/ | 2018-07-11 | EXCAVATED IN MUDPLOT REPAIR 5/8 STOP & WASTE LEAD LINE. DRESS UP WITH RIVERSAND. JOB REFER TO ZONE 5 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201801263801 | 2018-07-09 | LEAD | 1322 | 7TH | COLISEUM | WOLK | ML-METER LEAK METER# A396983 ACCT # 111806-596500 OUTLET SERVICE LEAK BEHIND METER BOX HOLE OPEN /** 1) MN: A140747 SN: 0013412, *TAP: SIZE: B LOC: 80 FEET FROM P LINE AT COLISEUM, *MB: CODE: CEL1 LOC: 80' P.L. COLISEUM ****/ | 2018-07-09 | EXCAVATED IN BRICK SIDEWALK REPAIR INLET & OUTLET SERVICE PLASTIC LINE. ALSO RAISE TO GRADE. DRESS UP RIVERSAND. REFER TO ZONE 3 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX JOB REF TO ZONE 3 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201801264001 | 2018-07-09 | LEAD/PLASTIC | 404 | NOTRE DAME | TCHOUPITOULAS | WOLK | PP- POOR PRESSURE ACCT# 212665-529870 MTR# A294753 . OUTLET SERVICE LEAK, CON REG WHEN METER TURNED OFF *****NOT THE SAME AS WO#201701224201***** 07/11/18 DISONNECTION OUTLET IN BOX, CUSTOMER OUT OF WATER PER SR#12846198, ****S.SLACK @ 10:43AM**** (AJR) /** 1) MN: A294730 SN: 0173103, *TAP: SIZE: A LOC: 105 FEET FROM P LINE AT TCHOUPITOULAS, *MB: CODE: CD LOC: ON NOTRE DAME 105FT FROM TCHOUPITOULAS 5FT OUTSIDE ** 2) MN: A306512 SN: 0173103, *TAP: SIZE: A LOC: 109 FEET FROM P LINE AT TCHOUPITOULAS, *MB: CODE: CD LOC: ON NOTRE DAME 109FT FROM TCHOUPITOULAS 5' OUTSIDE THERE ARE 26 MORE NOT LISTED. ****/ | 2018-07-11 | EXAMINED AREA LOCATED METER EXCAVATED IN METER BOX EXPOSED PROBLEM REPAIRED LINE CLEANED AREA
201801265001 | 2018-07-09 | LEAD | 2721 | BIENVILLE | N BROAD | WILK | ML-METER LEAK ACCT#138290-519309 METER#A289713 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A289713 SN: 0068945, *TAP: SIZE: B LOC: 163 FEET FROM P LINE AT BROAD N, *MB: CODE: CDM LOC: ON BIENVILLE 163' FROM PL OF BROAD N ****/ | 2018-07-18 | FOUND METER BOX LEAKING IN MUD PLOT ON SIDEWALK AT ABOVE LOCATION EXCAVATED FOUND CURB COCK LEAKIG REPLACED CURB COCK BACKFILLED WITH SAND AND COLDMILL
201801267101 | 2018-07-09 | LEAD | 4208 | DALE | CHEF MENTEUR HW | WILK | /** 1) MN: A237411 SN: 0133815, *TAP: SIZE: A LOC: 85 FEET FROM P LINE AT SWAMP SIDE HYDT. #1, *MB: CODE: CDL2 LOC: ON DALE, 85' FROM S.S. HYDT. #1,6' OUTSIDE U.P.L., ****/ | 2018-07-09 | EXCAVATED IN MUDPLOT BY HAND TO REPAIR LEAK ON 5/8 CURB COCK (ABANDONED SERVICE) D.N.R LEAD FROM INLET 3X3 MUDPLOT.
201801272301 | 2018-07-10 | LEAD | 3423 | FRANKLIN AV |  | WILK | ML-METER LEAK ACCT#150175-475985 METER#A422293 INLET SERVICE LEAK IN GUTTER BOTTOM, CARS ROLLING OVER METER /** 1) MN: A322266 SN: 0049406, *TAP: SIZE: A LOC: 56 FEET FROM P LINE AT FRANKLIN, *MB: CODE: CD LOC: ON ELDER 56FT FROM FRANKLIN ****/ | 2018-07-17 | EXCAVATED IN MUDPLOT REPAIR 5/8 STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND JOB REFERRED TO ZONE 5 TO REMOVE LEAD
201801272901 | 2018-07-10 | LEAD | 620 | CONTI | CONTI | WILK | ML: METER LEAK METER # B031809 ACCT# 105141-527241 METER IN ALLEY INLET SERVICE LEAK FOUND METER OFF LEFT OFF /** 1) MN: B031809 SN: 0174775, *TAP: SIZE: B LOC: 46 FEET FROM P LINE AT CONTI, *MB: CODE: AE LOC: IN ALLEY 46FT P.L. CONTI ** 2) MN: A272268 SN: 0023092, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT CONTI, *MB: CODE: CD LOC: ON EXCHANGE 45FT FROM CONTI 1FT INSIDE CURB ****/ | 2018-07-20 | EXCAVATED 3 X 2 SIDEWALK THROUGH TILES REPLACED 3/4 INCH METER BOX TO STOP LEAK BACKFILLED AND CLEANED THE AREA TILES ARE STACK UP AGAINT THE WALL
201801273201 | 2018-07-10 | LEAD | 1960-58 | N PRIEUR | PAUGER | WOLK | ML-METER LEAK METER# A359885 ACCT# 190591-494790 EXAMINE OUTLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A233779 SN: 0047792, *TAP: SIZE: B LOC: 136 FEET FROM P LINE AT PAUGER, *MB: CODE: ADKO LOC: 139FT FROM PL PAUGER ON PRIEUR ****/ | 2018-07-20 | FOUND LEAKING AT ABOVE ADDRESS IN MUD PLOT IN METER BOX EXCAVATED FOUND LEAKING AT WHEEL REPLACED WHEEL MADE REPAIRS BACKFILLED WITH SAND AND COLDMILL
201801275201 | 2018-07-10 | LEAD/PLASTIC | 106 | SHERWOOD FOREST DR | CITY PARK | WILK | ML - METER LEAK ACCOUNT NUMBER - 128231-514764 METER NUMBER - A431331 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A324641 SN: 0055117, *TAP: SIZE: A LOC: 159 FEET FROM P LINE AT CITY PARK AVE, *MB: CODE: BDL2 LOC: ON SHERWOOD FOREST 160.4' FROM USPL CITY PARK AVE ****/ | 2018-08-03 | EXCAVATED IN MUDPLOT OVER A 5/8 INLET SERVIC LEAK BYHAND NEAR PARKED VEHICLE REPLACED THE COCK STOK THE LEAK BACKFILL AND DRESSUP WITH RIVERSAND [ LEAD INLET PLASTIC OUTLET ]
201801276601 | 2018-07-11 | LEAD | 1907 | LOUISA | N PRIEUR | WILK | MI- LEAK IN SIDEWALK FLOODING AREA ***PLEASE CALL OWNER**** INLET SERVICE PASSING N OFF POSITION, NO METER IN BOX, NO ANSWER @ PHONE /** 1) MN: A346432 SN: 0084206, *TAP: SIZE: B LOC: 11 FEET FROM P LINE AT NO. PRIEUR, *MB: CODE: BLF1 LOC: ON LOUISA, 10' FROM D.P.L. NO. PRIEUR, 2' OUTSIDE, ****/ | 2018-07-17 | EXCAVATED 2 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH ABANDON INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201801278301 | 2018-07-11 | LEAD/PLASTIC | 4329 | VIXEN |  | WILK | MI-- CUT SERVICES CUSTOMER W/O WATER SERVICES CUT BY: ALLSTAR ELECTRIC INC. 821 LITTLEFARMS AV. METAIRIE, LA. 70003 504-252-1659 ********DAMAGE CLAIM********** (S.SLACK @ 11:41AM) CUT INLET BY ALL STAR ELECTRIC, CUSTOMER OUT OF WATER /** 1) MN: A156890 SN: 0137187, *TAP: SIZE: C LOC: 26 FEET FROM P LINE AT PRANCER, *MB: CODE: B LOC: ON VIXEN 24FT FROM UPPER EXT. P.L. PRANCER 7FT OUT ****/ | 2018-07-11 | EXAMINED AREA OBSERVED LEAK ON INLET SERVICE EXCAVATED IN MUD PLOT AND IN DRIVEWAY TRACED THE LEAK REPAIRED LEAK REPLACED OLD BROKEN METERBOX SET UP WITH NEW AND RAISED TO GRADE CLEANED SITE AND BACKFILLED WITH SAND AND COAL MILL
201801278701 | 2018-07-11 | LEAD | 731 | N CARROLLTON AV | ORLEANS AV | WMTLK | ML-METER LEAK MTR# D 005593 ACC#113009-505559 EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN MUDPLOT METER UNDER WATER /** 1) MN: D005593 SN: 0015358, *TAP: SIZE: CCC LOC: 42 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: DMN LOC: 43' P.L. ORLEANS AV ****/ | 2018-07-20 | EXAMINED MAN HOLE IN MUD PLOT FOUND 1 1/2 INCH UNION LEAKING TIGTHEN UNION TO STOP LEAK
201801280201 | 2018-07-11 | LEAD | 2335 | URSULINES AV | N TONTI | WILK | ML METER LEAK METER# A403160 INLET SERVICE LEAK ON SIDEWALK /** 1) MN: A300857 SN: 0012420, *TAP: SIZE: A LOC: 55 FEET FROM P LINE AT TONTI N, *MB: CODE: BGM1 LOC: S&W LOCATED UNDER HOUSE 4FT UNDER RS 55' P/L TONTI ****/ | 2018-07-20 | FOUND LEAK IN METER BOX BEHIND CURB COCK LEAKING ON LEAD LINE REPLACED LEAD LEAD LINE WITH 3 FT OF PVC ALSO REPLACE 5/8 INCH CURB COCK
201801281201 | 2018-07-11 | LEAD/PLASTIC | 5600 | CHARLOTTE DR | MENDEZ | WILK | WM-LEAK IN THE STREET INLET SERVICE LEAK IN CONCRETE STREET **CHANGED FROM 5610 CHARLOTTE DR** /** 1) MN: B019479 SN: 0121780, *TAP: SIZE: B LOC: 475 FEET FROM P LINE AT CRESCENT, *MB: CODE: BDMK LOC: 478FT PL CRESCENT 8FT OUTSD 5FT INSD CURB ****/ | 2018-08-05 | FOUND NO LEAK. LEAK WAS AT 5611 CHARLOTTE DR. JOB COMPLETE
201801281801 | 2018-07-11 | LEAD | 1127 | N ROMAN | GOV NICHOLLS | WMBK | MI MISSING METER COVER METER# A123132 BROKEN METER BOX CASING /** 1) MN: A312510 SN: 0019906, *TAP: SIZE: A LOC: 238 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: BDKL LOC: ON N ROMAN ST 238' FROM PL URSULINES AVE ****/ | 2018-07-20 | REPLACED CASING AND COVER RAISED TO GRADE BACKFILLED WITH RIVER SAND AND COLDMILL
201801284801 | 2018-07-12 | LEAD | 2235 | REYNES | N TONTI | WMRE | ******************PICKUP***************** LOCATE SERVICE AND RAISE METER TO PROPER GRADE ACC#424233-161916 MN#B040462 /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-07-18 | EXCAVATED 3 X 2 MUD PLOT LOCATED METER BOX SPRAYED WITH BLUE PAINT BACKFILLED AND CLEANED THE AREA FT FROM REYNES INSTALLED ONE IN METER:43 FT FROM FROM P.L. ON N TONTI ST. 7 FT. OUTSIDE P.L. AND 3 FT.INSIDE CURB
201801285701 | 2018-07-12 | LEAD | 2325 | COLUMBUS | TONTI | WILK | ML: METER LEAK METER# A353920 ACCT# 104637-488511 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A298528 SN: 0006812, *TAP: SIZE: A LOC: 129 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BFK LOC: ON COLUMBUS 129FT FROM LRPL OF N ROCHEBLAVE ****/ | 2018-07-18 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CURB COCK LEAKING ON LEAD LINE + REPAIRED IT
201801287701 | 2018-07-12 | LEAD | 9413 | COLAPISSA |  | WILK | LOCATION ID-170791 MTR-A411033 MTR ON/STOP & WASTE OPEN CUST NOT GETTING WATER/CUST WAITING ON WATER *******CUSTOMER OUT OF WATER******** D SMITH @ 19:07PM INLET SERVICE LEAK IN GRASS FLOODING SIDEWALK /** 1) MN: A293494 SN: 0110992, *TAP: SIZE: A LOC: 109 FEET FROM P LINE AT COLAPISSA, *MB: CODE: CDM1 LOC: ON COLAPISSA, 109' FROM P.L. LIVE OAK, 9' OUTSIDE ****/ | 2018-07-12 | EXCAVATED IN MUDPLOT. REPAIR 5/8 STOP & WASTE LEAD LINE. DRESS UP WITH RIVERSAND REFER TO ZONE 1 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201801288901 | 2018-07-13 | LEAD | 610 | FRENCHMEN |  | WILK | LOCATION: 120596 MTR# A 420318 PER INSP L UDEBOR, LEAK COMING FROM BLEEDER VALVE. BAD BLEDER VALVE /** 1) MN: A331597 SN: 0038132, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT CHARTRES, *MB: CODE: OOOO LOC: METER ON FRENCHMEN 107 FT FROM PL CHARTRES ****/ | 2018-07-25 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH COCK TO STOP LEAK BACKFILLED AND CLEANED THE AEA REFER BACK TO ZONE 4 TO REMOVE LEAD FROM STREET
201801289801 | 2018-07-13 | LEAD | 2805 | N ROCHEBLAVE |  | WILK | ML-- METER LEAK METER # A313665 ACCT# 148334-484634 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A286917 SN: 0080521, *TAP: SIZE: B LOC: 43 FEET FROM P LINE AT EADS, *MB: CODE: ADL1 LOC: ON ROCHEBLAVE 43FT FROM PL EADS ****/ | 2018-07-23 | EXCAVATED 3 X 2 GUTTER BOTTOM THROUGH LIMESTONE ALSO 3 X 3 MUD PLOT AT PROPERTY RENEWED OUTLET TO PROPERTY AND 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA
201801289901 | 2018-07-13 | LEAD | 2628 | ALLEN | HOPE | WILK | ML-METER LEAK ACCT#150580-495536 MTR#A290164 EXAMINE INLET SERVICE FOR LEAK IN BOX /** 1) MN: A214208 SN: 0083495, *TAP: SIZE: B LOC: 211 FEET FROM P LINE AT LAW, *MB: CODE: CDN1 LOC: 211' P.L. LAW ****/ | 2018-07-24 | EXCAVATED 3 X 3 MUD PLOT AROUND METER BOX FOUND OUTLET RENEWED TO PROPERTY AND REPLACED 5/8 INCH METER COCK TO STOPLEAK BACKFILLED AND CLEANED THE AREA
201801291401 | 2018-07-13 | LEAD | 1313 | URSULINES AV |  | WILK | ML- METER LEAK ACCT# 108508-526438 METER# A346513 CUST STATES METER IS OFF, BUT WATER IS STILL COMING INTO PROPERTY, PLEASE CALL MELLISSA UPON ARRIVAL 504-524-9200 OR 504-325-4540 BAD CURB COCK PASSING IN OFF POSITION, FOUND OFF LEFT OFF /** 1) MN: A346513 SN: 0009549, *TAP: SIZE: A LOC: 121 FEET FROM P LINE AT TREME, *MB: CODE: AFKM LOC: ON URSULINES 121 FT FROM PL TREME ****/ | 2018-07-20 | WENT TO ABOVE LOCATION EXAMINED METER BOX FOUND CURB COCK LEAKING IN OFF POSITION BROKE SIDEWALK UP MADE REPAIR CHANGE CURB COCK MADE 4 X 4 CUT SIDEWALK
201801292401 | 2018-07-13 | LEAD | 302 | HOMEDALE | MILNE BL | WILK | **************PICKUP************* INLET SERVICE LEAK IN GRASS FLOODING GRASS/GUTTER BOTTOM /** 1) MN: A315329 SN: 0087047, *TAP: SIZE: B LOC: 62 FEET FROM P LINE AT MILNE BLVD, *MB: CODE: CDKL LOC: FRONT - 62' P.L. MILNE BLVD ****/ | 2018-07-16 | EXCAVATED IN MUDPLOT ON INLET LEAK MADE ALL REPAIR TO STOP LEAK BACKFILL WITH RIVERSAND REFER TO ZONE 1 TO REMOVE LEAD
201801293101 | 2018-07-13 | LEAD | 4516 | PALMYRA |  | WILK | MTR LEAK/MTR BOX OVER FLOWING/GREEN ALGAE/NO MTR IN BOX INLET SERVICE LEAK NO METER IN BOX CURBCOCK IN OFF POSITION PASSING WATER /** 1) MN: A135946 SN: 0042141, *TAP: SIZE: A LOC: 101 FEET FROM P LINE AT MURAT S, *MB: CODE: CE LOC: ON PALMYRA,101' FROM U.S.P.L. SO. MURAT ****/ | 2018-07-17 | EXCAVATED IN CONCRETE SIDEWALK REPAIR 5/8 STOP 7 WASTE LEAD LINE DRESS UP WITH RIVERSAND & COLDMILL. JOB REF TO ZONE 1 TO LEAD LINE FROM WATER MAIN TO METER BOX. (JOB REFERRED)
201801301101 | 2018-07-16 | LEAD | 3711 | N TONTI | INDEPENDENCE | WILK | WM - LEAK ON THE SIDEWALK INLET SERVICE LEAK IN MUDPLOT IN FRONT OF EMPTY LOT ON ABANDON SERVICE POURING OUT OF GROUND /** 1) MN: A306213 SN: 0086798, *TAP: SIZE: A LOC: 109 FEET FROM P LINE AT INDEPENDENCE, *MB: CODE: BF LOC: ON TONTI 80FT FROM INDEPENDENCE 8FT OUTSIDE ****/ | 2018-07-25 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801301401 | 2018-07-16 | LEAD | 2516 | ANNETTE | LAW | WILK | ML METER LEAK METER # A294130 ACCOUNT # 161567-496093 INLET SERVICE LEAKING IN GUTTER BOTTOM /** 1) MN: A294130 SN: 0079902, *TAP: SIZE: A LOC: 158 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: BDK LOC: ON ANNETTE 158.5' FROM PL N DORGENOIS 7.5' OUTSIDE ****/ | 2018-07-31 | EXCAVATED 3 X 2 GUTTER BOTTOM REPLACED 5/8 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA REFER BACK TO ZONE 4 TO HAVE LEAD REMOVED FROM THE STREET
201801310801 | 2018-07-18 | LEAD | 2441 | PAUGER | N ROMAN | WOLK | ACCT#119495-461502. THE METER HAS A CON REG. NO S&W VALVE TO PERFORM TEST. METER#A375053 /** 1) MN: A285573 SN: 0058753, *TAP: SIZE: A LOC: 43 FEET FROM P LINE AT PAUGER, *MB: CODE: AFL1 LOC: SIDE ST ON N ROMAN 43' P.L. PAUGER ****/ | 2018-07-26 | EXAMINED JOB AN DFOUND NO CONSTANT REGISTRATION
201801312301 | 2018-07-18 | LEAD | 1413 | PAULINE | N VILLERE | WILK | ML-METER LEAK METER#A408620 ACCT#153136-527541 INLET SERVICE LEAKING IN MUDPLOT /** 1) MN: A344898 SN: 0020212, *TAP: SIZE: B LOC: 111 FEET FROM P LINE AT VILLERE S, *MB: CODE: CDLM LOC: 110'FROM VILLERE 2' OUTSIDE P L ON PAULINE ****/ | 2018-07-30 | EXCAVATED 3X 2 MUD PLOT IN FLOWER AROUND METER REPLACED 5/8 INCH METER COCK BACKFILLED AND CLEANED THE AREA
201801316201 | 2018-07-19 | LEAD | 1620 | PHILIP |  | WILK | ML- METER LEAK ACCT# 185172-711104 METER # A251472 BAD BLEEDER VALVE MN#A368534 /** 1) MN: A242963 SN: 0031791, *TAP: SIZE: A LOC: 154 FEET FROM P LINE AT ST CHARLES AVE, *MB: CODE: CEL1 LOC: ON PHILIP 153FT FROM PL OF ST CHARLES AVE ****/ | 2018-10-26 | ARRIVED AT ABOVE LOCATION EXAMINED METER ,BAD BLEEDER WAS FOUND .BUST OUT CONCRETEE SIDEWALK BY HAND PUT NEW COCK BACKFILLED AND CLEANED UP. COULD NOT ET CAR MOVED TO REMOVE LEAD FROM INLET HAD TO HAND DIG. (SOC3FT .X 3 FT .S/W)
201801319801 | 2018-07-20 | LEAD | 4429 | BACCICH |  | WILK | ML- METER LEAK ACCT# 118227-477147 METER# A230770 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A230770 SN: 0085822, *TAP: SIZE: A LOC: 232 FEET FROM P LINE AT GENTILLY RD, *MB: CODE: CDT LOC: BY 2ND TREE 230' P.L. GENTILLY ROAD ****/ | 2018-07-29 | EXCAVATED IN MUDPLOT BY HAND TO CHANGE BAD 5/8 CURB COCK, HANDWHEEL AND RAISE METERBOX TO GRADE. FOUND LEAD ON BOTH INLET AND OUTLET SERVICES AND REMOVED LEAD FROM OUTLET. D.N.R LEAD FROM INLET. 5 X 4 MUDPLOT CUT
201801324201 | 2018-07-21 | LEAD/PLASTIC | 1606 | BODENGER BL | PARK BL | WMTLK | LOCATIONID#225657-402867 METER#B026497 LEAK AT WHEEL SIDE OF METER /** 1) MN: SN: 0092886, *TAP: SIZE: A LOC: 126 FEET FROM P LINE AT PARK BLVD, *MB: CODE: AD LOC: 126'FROM P L PARK INSIDE RES ** 2) MN: B026497 SN: 0085215, *TAP: SIZE: B LOC: 89 FEET FROM P LINE AT PARK BLVD., *MB: CODE: __ LOC: ON BODENGER BLVD., 89' FROM P.L. PARK BLVD. ****/ | 2018-08-07 | EXAMINED AREA CLEANED OUT METER BOX OBSERVED LEAK ON OUTLET SERVICE EXCAVATED THROUGH ROOTS EXCAVATED TO PROPERTY REPAIRED LEAK TO PROPERTY BACKFILLED CLEANED AREA
201801324801 | 2018-07-21 | LEAD | 4631 | METROPOLITAN DR | MIRABEAU AV | WOLK | MI LEAK ON SIDEWALK OUTLET SERVICE LEAK IN THE SIDEWALK /** 1) MN: A253821 SN: 0112232, *TAP: SIZE: A LOC: 495 FEET FROM P LINE AT STEPHEN GIRARD AVE, *MB: CODE: CDN1 LOC: ON METROPOLITAN 495' FROM PL STEPHEN GIRARD AVE 7' ****/ | 2018-07-29 | EXCAVATED IN MUDPLOT BY HAND TO CHANGE BAD 5/8 CURB COCK HANDWHEEL AND RAISE METERBOX TO GRADE. FOUND LEAD ON BOTH INLET AND OUTLET SERVICES AND REMOVED LEAD FROM OUTLET. D.N.R LEAD FROM INLET. BACKFILLED 6 X3 MUDPLOT CUT
201801326401 | 2018-07-23 | LEAD/PLASTIC | 6020 | WARWICK CT |  | WOLK | MI LEAK BETWEEN SIDEWALK/STREET FLOODING AREA EXAMINE OUTLET SERVICE LEAK AT PROPERTY LINE 07/30/18 LEAK IS GETTING WORST. FLOODING AREA. (KSW) /** 1) MN: A138714 SN: 0177117, *TAP: SIZE: B LOC: 164 FEET FROM P LINE AT WESTCHESTER, *MB: CODE: ADD LOC: ON WARWICK 164' FROM PL WESTCHESTER 9' OUTSIDE PL ****/ | 2018-08-06 | EXAMINED AREA PUMPED DOWN WATER EXCAVATED AT BOIL SITE EXPOSED LINE REPAIRED LEAK BACKFILLED CLEANED AREA DRESSED CUT WITH SAND
201801327303 | 2018-10-26 | LEAD/PLASTIC | 1015 | NASHVILLE AV | CHESTNUT | WINE | INSTALL NEW SERVICE FROM CONTROLLING LINE /** 1) MN: A346245 SN: 0063056, *TAP: SIZE: A LOC: 167 FEET FROM P LINE AT CHESTNUT, *MB: CODE: ADK2 LOC: LPL CURB ON NASHVILLE AVE 138.5 FT PL CHESTNUT ****/ | 2018-10-27 | REPLACED 1" CONTROLLING LINE FROM 1 1/2 CONTROLING LINE TO METER BOX.(SOC 6FT. X 36 FT. CONCRETE BASE)
201801328001 | 2018-07-23 | LEAD | 1016 | CADIZ | CAMP | WOLK | ML-METER LEAK ACCT#137863-703122 METER#A235449 OUTLET SERVICE LEAK FROM HANDWHEEL /** 1) MN: A235449 SN: 0068884, *TAP: SIZE: B LOC: 148 FEET FROM P LINE AT CAMP, *MB: CODE: CDL1 LOC: ON CADIZ ST 147.5' FROM LPL CAMP ****/ | 2018-07-26 | EXCAVATED IN MUDPLOT. REPAIR 5/8 STOP & WASTE LEAD LINE. DRES UP WITH RIVERSAND REFER TO ZONE 3 TO TAKE LEAD LINE OUT FROM WATER MAIN TO METER BOX
201801329401 | 2018-07-23 | LEAD | 713 | BURGUNDY | ORLEANS AV | WILK | WM- LEAK ON SIDEWALK INLET SERVICE LEAK IN BOX /** 1) MN: B030935 SN: 0012973, *TAP: SIZE: B LOC: 45 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: OOO LOC: ****/ | 2018-08-01 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 3/4 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801331901 | 2018-07-23 | LEAD/PLASTIC | 1278 | CASA CALVO | SOCRATES | WILK | ML-METER LEAK METER#A397800 ACCT#229592-404839 INLET SERVICE (C) /** 1) MN: A239110 SN: 0130361, *TAP: SIZE: B LOC: 112 FEET FROM P LINE AT SOCRATES, *MB: CODE: CDN1 LOC: ON CASA CALVO, 112' FROM P.L. SOCRATES, 7' OUTSIDE ****/ | 2018-08-02 | EXAMINED AREA OBSERVED LEAK ON OUTLET SERVICE REMOVED ON INLET AND OUTLET SERVICE EXPOSED LEAD LINE REMOVED LEAD LINE TO PROPERTY ON OUTLET BACKFILLED CLEANED AREA
201801332901 | 2018-07-24 | LEAD | 2134 | N ROCHEBLAVE | TOURO | WILK | LEAK ON MUD PLOT /** 1) MN: B031747 SN: 0065258, *TAP: SIZE: B LOC: 37 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BDHM LOC: ON TOURO 39FT FROM PL OF N ROCHEBLAVE ****/ | 2018-08-02 | EXCAVATED 3X 2 MUD PLOT REPLACED 3/4 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801333001 | 2018-07-24 | LEAD | 2138 | N ROCHEBLAVE | TOURO | WILK | METER LEAK IN MUD PLOT /** 1) MN: A330441 SN: 0104494, *TAP: SIZE: A LOC: 51 FEET FROM P LINE AT TOURO, *MB: CODE: CDLM LOC: ON N ROCHEBLAVE 51FT FROM PL TOURO 8FT OUT PL 2FT ****/ | 2018-08-02 | REPLACED 5/8 INCH HANDWHEEL INSIDE METER BOX TO STOP LEAK
201801333101 | 2018-07-24 | LEAD | 1676 | N MIRO | D"ABADIE | WILK | METER LEAK IN MUD PLOT /** 1) MN: SN: 0063586, *TAP: SIZE: A LOC: 58 FEET FROM P LINE AT D'ABADIE, *MB: CODE: __ LOC: ****/ | 2018-08-07 | EXCVAVATED 4 X 4 MUD PLOT MADE REPAIRS ON INLET RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILLED JOB WITH RIVERSAND
201801333201 | 2018-07-24 | LEAD | 1667 | N MIRO | ONZAGA | WILK | METER LEAK MUD PLOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-08-01 | EXCAVATED 3 X 3 MUD PLOT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA. *REFER BACK TO ZONE 4 TO REMOVE LEAD FROM STREET*
201801333401 | 2018-07-24 | LEAD | 606 | N ROCHEBLAVE |  | WOLK | METER LEAK IN MUD PLOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-08-01 | EXCAVATED 2 X 2 SIDEWALK CUT ALSO 2 X 2 MUD PLOT MADE REPAIR ON 1 INCH SERVICE LINE TO STOP LEAK BACKFILLD AND CLEANED THE AREA. (JOB COMPLETE)
201801337501 | 2018-07-24 | LEAD/PLASTIC | 1837 | SHIRLEY DR | VESPASIAN BL | WMTLK | ML- METER LEAK METER # B026997 ACCT # 226442-702197 EXAMINE INLET AND OUTLET SERVICE FOR LEAAK IN BOX FLOODING SIDEWALK /** 1) MN: B026997 SN: 0122944, *TAP: SIZE: B LOC: 449 FEET FROM P LINE AT VESPASIAN, *MB: CODE: BE25 LOC: 471FT FROM P.L. VESPASIAN MTR ON SHIRLEY DR ****/ | 2018-08-06 | EXAMINED AREA OBSERVED LEAK ON INLET AND OUTLET SERVICE REMOVED LEAD TO PROPERTY RAISED METER TO GRADE REPLACED OLD METER CASE WITH NEW METER BOX COMPLETE SOME DELAY DUE TO WEATHER BACKFILLED DRESSED UP MUDPLOT CLEANED AREA
201801339301 | 2018-07-24 | LEAD | 1000 | ORLEANS AV | BURGUNDY | WMTLK | ML- METER LEAK METER # 203565-528546 ACCT# 203565-528546 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A259081 SN: 0012973, *TAP: SIZE: B LOC: 44 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: OOO LOC: ON BURGUNDY 44' FROM PL ORLEANS 3' OUTSIDE PL 6' I ****/ | 2018-08-14 | EXAMINED JOB AT ABOVE LOCATION FOUND NO LEAK ON OUTLET JOB WAS COMPLETE AT AN EARLIER DATE
201801339501 | 2018-07-24 | LEAD | 2831 | N TONTI | ST FERDINAND | WILK | MI-LEAK AT THE SIDEWALK INLET SERVICE LEAK IN MUDPLOT /** 1) MN: SN: 0076006, *TAP: SIZE: A LOC: 181 FEET FROM P LINE AT PORT, *MB: CODE: BDK6 LOC: ON NO. TONTI, 181' FROM P.L. PORT ****/ | 2018-08-09 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK ON 5/8 INCH INELT SERVICE MADE REPAIR ON INLET RENEW ON INLET RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILL JOB WITH RIVERSAND
201801343201 | 2018-07-25 | LEAD/PLASTIC | 4315 | VIXEN | ST NICK | WILK | ML METER LEAK ACCT# 230571-409803 METER# A388188 ********DAMEGE CLAIM******* (S.SLACK @ 13:25PM) CUT INLET SERVICE BY ALLSTAR ELECTRIC, CUSTOMER OUT OF WATER *****FOREMAN LANCE BERRY***** /** 1) MN: A302837 SN: 0137191, *TAP: SIZE: B LOC: 132 FEET FROM P LINE AT ST NICK DR, *MB: CODE: B LOC: ON VIXEN 128FT EXT P.L. ST NICK 7FT OUTSIDE P.L. ****/ | 2018-07-25 | ARRIVE ON JOB SITE EXAMINE CUSTOMER OUT OF WATER DUE TO CONTRACT EXCAVATED BY HAND IN MUD PLOT MADE REPAIRS ON SERVICE. JOB COMPLETE
201801343301 | 2018-07-25 | LEAD/PLASTIC | 417 | ELMIRA AV |  | WMTLK | LOCATION ID-231551 MTR-C013095 LEAK BETWEEN MTR AND STOP & WASTE/CONS ON MTR EXAMINE INLETAND OUTLET SERVICE FOR LEAK ALSO REPLACE LOWER BROKEN METER BOX CASING /** 1) MN: C013095 SN: 0142625, *TAP: SIZE: C LOC: 122 FEET FROM P LINE AT ALIX, *MB: CODE: ADM LOC: ON ELMIRA 123FT FROM ALIX 7FT OUTSIDE ****/ | 2018-08-09 | EXAMINED AREA CLEANED OUT METER BOX BROKE OUT CONCRETE EXCAVATED ON INLET AND OUTLET SERVICE OBSERVED LEAK ON INLET AND OUTLET SERVICE REPAIRED LEAK BACKFILLED CLEANED AREA
201801344701 | 2018-07-25 | LEAD | 715 | TOPAZ | SARDONYX | WILK | ML METER LEAK METER# C007292 INLET SERVICE LEAK IN MUDPLOT NEAR BOX /** 1) MN: C007292 SN: 0129589, *TAP: SIZE: C LOC: 143 FEET FROM P LINE AT SARDONYX, *MB: CODE: CGM LOC: ON TOPAZ, 140' FROM P.L. SARDONYX, 2' OUTSIDE ****/ | 2018-08-13 | EXCAVATED AROUND 1'' METERBOX FOUND ON LEAK ON BOTH INLET / OUTLET. CLEANED AND DRESSED UP AREA . FOUND LEAD ON INLET / OUTLET.
201801346401 | 2018-07-25 | LEAD/PLASTIC | 3640 | RUE DENISE |  | WILK | ML-METER LEAK ACCT#232626-416965 METER#A412293 INLET SERVICE LEAK /** 1) MN: A298498 SN: 0146580, *TAP: SIZE: B LOC: 29 FEET FROM P LINE AT CARLISLE CT, *MB: CODE: CDMN LOC: ON RUE DENISE, 29' FROM D.P.L. CARLISLE CT., 2' ****/ | 2018-08-21 | EXAMINED LEAK EXCAVATED ON INLET AND OUTLET SERVICE EXPOSED LEAK ON INLET SERVICE OBSERVED LEAK ON OUTLET SERVICE REPAIRED LEAKS BACKFILLED AND CLEANED AREA
201801346501 | 2018-07-25 | LEAD/PLASTIC | 3730 | RUE DENISE | CARLISLE CT | WILK | ML-METER LEAK ACCOUNT#232649-416986 METER#A408052 INLET SERVICE LEAK 08/20/18 LAEAK HAS GOTTEN WORSE PER SR#12849687 (AJR) /** 1) MN: A236867 SN: 0146672, *TAP: SIZE: B LOC: 99 FEET FROM P LINE AT CARLISLE CT, *MB: CODE: CD LOC: ON RUE DENISE, 100' FROM P.L. CARLISLE CT., 7' ****/ | 2018-08-21 | EXAMINED AREA EXCAVATED INLET AND OUTLET SERVICE PUMPED WATER DOWN EXPOSED LEAK ON INLET SERVICE REPAIRED LEAK BACKFILLED CLEANED AREA
201801348301 | 2018-07-26 | LEAD | 2229 | DELERY | N TONTI | WILK | ML- METER LEAK MTR# A267232 ACCT# 173724-421945 INLET SERVICE LEAK IN BOX /** 1) MN: A242230 SN: 0129943, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT MIRO N, *MB: CODE: BDMO LOC: RES ON DELERY 100FT P/L N MIRO 7' OUTSIDE ****/ | 2018-08-03 | EXCAVATED 2 X 2 GUTTER ALSO 3 X 2 MUD PLOT AT PROPERTY RENEWED OUTLET SERVICE LINE TO PROPERTY BACKFILLED AND CLEANED THE AREA
201801350301 | 2018-07-26 | LEAD/PLASTIC | 2430 | NASHVILLE AV | CLARA | WILK | WM-LEAK ON THE SIDEWALK INLET SERVICE LEAK IN AN ASPHALT STREET FLOODING STREET & GUTTER BOTTOM /** 1) MN: A223159 SN: 0061012, *TAP: SIZE: A LOC: 133 FEET FROM P LINE AT CLARA, *MB: CODE: ADK2 LOC: ON NASHVILLE AVE 134' FROM LRPL CLARA ****/ DOTTIE READY 8-2-18 EXP 8-22-18 | 2018-08-05 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND LEAK FOR 2430 NASHVILLE AVE .REPLACED 3/4 SERVICE FROM 6"WATER MAIN TO CANAL WALL TIED IN TO LEAD.(SOC 9FT .X 12 FT CONCRETEE BASE.)
201801350501 | 2018-07-26 | LEAD | 2819 | N RAMPART | PRESS | WILK | ML - METER LEAK ACCT#113060703407 METER#A190246 BAD BLEEDER VALVE IN BOX /** 1) MN: A190246 SN: 0053614, *TAP: SIZE: A LOC: 131 FEET FROM P LINE AT ST FERDINAND, *MB: CODE: AFHT LOC: 131FT FROM RPL ST FERDINAND ON N RAMPART ****/ | 2018-08-14 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLETRENEW OUTLET SERVICE FROM METER BOX TO LEAD GOING UNDER FOUNDATION BACKFILLED JOB WITH RIVERSAND COLDMILL
201801352001 | 2018-07-26 | LEAD | 5442 | CHARTRES | FLOOD | WILK | WM-LEAK ON THE SIDEWALK INLET SERVICE LEAK IN MUDPLOT FLOODING SIDEWALK/CURB IN FRONT OF ABANDON HOUSE /** 1) MN: A296222 SN: 0054887, *TAP: SIZE: A LOC: 183 FEET FROM P LINE AT FLOOD, *MB: CODE: BEL LOC: OPP WINDOW CURB 185' P.L. FLOOD ****/ | 2018-08-09 | EXCAVATED AND MADE REPAIRS ON ABANDON INLET SERVICE IN SIDEWALK BACKFILLED JOB WITH RIVERSAND COLDMILL OUTLET HAS PLASTIC LINE
201801354401 | 2018-07-27 | LEAD | 1833 | BENTON | N PRIEUR | WILK | INLER SERVICE LEK IN MUD PLOT /** 1) MN: A342586 SN: 0142168, *TAP: SIZE: B LOC: 85 FEET FROM P LINE AT PRIEUR N, *MB: CODE: CEN2 LOC: RES ON BENTON 83FT FROM PL PRIEUR N 7' OUTSIDE PL ****/ | 2018-08-06 | ARRIVED AT ABOVE LOCATION EXCAVATED IN MUD PLOT FOUND 5/8 INCH CURB COCK LEAKING ON COPPER LINE + REPAIRED IT (NO METER) *BACKFILLED & CLEANED AREA* JOB COMPLETE
201801359201 | 2018-07-27 | LEAD | 534 | VERRET |  | WLPR | PP- POOR PRESSURE MN:A353659 ACCT#224423-400393 **********1ST AM********** CHANGED FROM 534 VERRET EXAMINE INLET SERVICE FOR POOR PRESSURE CUSTOMER HAS 25 PSI @ OUTSIDE FAUCET /** 1) MN: A322023 SN: 0035601, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT EVELINA, *MB: CODE: BFOK LOC: 100'FROM L/R P L EVELINA RES ****/ | 2018-07-28 | EXCAVATED IN SIDEWALK WITH BOBCAT TO REPAIR LEAK ON 3/4 LEAD LINE. LEAD FOUND ON INLET PLASTIC FOUND ON OUTLET. BACKFILLED. ALSO RAISE METER TO GRADE.
201801362401 | 2018-07-29 | LEAD | 2232 | ST PHILIP |  | WILK | ML-METER LEAK ACCT#108931-524182 METER#A416704 INLET SERVICE LEAK /** 1) MN: A303351 SN: 0020156, *TAP: SIZE: A LOC: 58 FEET FROM P LINE AT MIRO N, *MB: CODE: ADL1 LOC: ON ST PHILIP 58FT FROM PL OF N MIRO ****/ | 2018-08-20 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201801362701 | 2018-07-29 | LEAD | 5210 | HAWTHORNE PL | CANAL BL | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK @ THE CURB. ***LEFT 1 CONE FOR PROTECTION /** 1) MN: A120050 SN: 0086909, *TAP: SIZE: B LOC: 157 FEET FROM P LINE AT CANAL BLVD, *MB: CODE: AEM1 LOC: ON HAWTHORNE PL 157' FROM PL CANAL BLVD ****/ | 2018-08-18 | EXCAVATED AND MADE REPAIR ON 3/4 INCH INLET SERVICE LEAK MADE 4 X 4 SIDEWALK CUT BACKFILL HOLE. JOB COMPLETE
201801364901 | 2018-07-30 | LEAD | 4400 | EDEN | S LOPEZ | WOLK | ML- METER LEAK ACCT# 145770-576867 METER# A258633 OUTLET SERVICE LEAK BEHIND HANDWHEEL, FLOODING GRASSY AREA /** 1) MN: A258633 SN: 0077713, *TAP: SIZE: B LOC: 14 FEET FROM P LINE AT LOPEZ S, *MB: CODE: CDL1 LOC: ON EDEN 14' FROM PL OF LOPEZ S ****/ DOTTIE READY 8-2-18 EXP 8-22-18 | 2018-08-04 | EXCVATED IN MUDPLOT OVER SERVICE.REPLACED 5/8 CURB COCK ,NEED TO REMOVE LEAD FROM WATER MAIN TO METER BOX OUTLET PLASTIC ALREADY.
201801368301 | 2018-07-30 | LEAD/PLASTIC | 3226 | BLAIR | GEN MEYER AV | WILK | WM LEAK BETWEEN STREET & SIDEWALK INLET SERVICE LEAK AT SIDEWALK /** 1) MN: B013750 SN: 0129276, *TAP: SIZE: B LOC: 779 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: CD LOC: ON BLAIR, 779' FROM P.L. GEN. MEYER AVE., 7' OUT- ****/ | 2018-08-14 | EXAMINED AREA PUMP DOWN WATER BROKE OUT STREET EXCAVATED IN STREET DOWN TO MAIN EXPOSED LEAK ON INLET SERVICE REPAIRED LEAK BACKFILLED CLEANED AREA
201801368401 | 2018-07-30 | LEAD | 6422 | CARTIER AV | ST BERNARD AV | WILK | C-Y NO WATER METER #C-023189 ACCT #179466-527685 ******CUSTOMER OUT OF WATER******* C MALLET @ 18:06PM INLET SERVICE LEAK /** 1) MN: C023189 SN: 0125995, *TAP: SIZE: C LOC: 63 FEET FROM P LINE AT CARTIER AVE, *MB: CODE: CDHM LOC: ON ORIOLE 63' FROM PL CARTIER AVE 8' OUTSIDE PL 2' ****/ | 2018-07-30 | EXCAVATED BY SHOVEL IN MUD PLOT AND REPAIRED INLET LEAD LINE. REFER TO 1ST AM TO BACKFILL HOLE AND REMOVE LEAD LINE. (JOB REFERRED)
201801372201 | 2018-07-31 | LEAD | 3128 | MUSIC | BENEFIT | WILK | MI- LEAK ON SIDEWALK INLET SERVICE LEAKING IN MUDPLOT /** 1) MN: A126316 SN: 0102339, *TAP: SIZE: A LOC: 83 FEET FROM P LINE AT BENEFIT, *MB: CODE: BDKO LOC: ON MUSIC, 83' FROM P.L. BENEFIT, 6' OUTSIDE P.L. ****/ | 2018-08-08 | EXCAVATED IN A 4X4 MUDPLOT FOUND LEAD LINE LEAKING. REPLACE WITH A 3/4 STOP COCK RAISE METER BOX TO GRADE BACKFILL AND DRESS
201801372901 | 2018-07-31 | LEAD/PLASTIC | 538 | BOUNY | ELIZA | WOLK | NEED LEAD WHIP CHANGED HOLE IS OPEN METER#A352825 ACCT#224330-400615 CHANGE LEAD WHIP LINE EXPOSED SPOKE WITH CUSTOMER 08/01/18 CUSTOMER NOW OUT OF WATER PER INSPC B BOURNES, UPDATE AND GIVE OUT (S.SLACK @ 12:03PM) /** 1) MN: A198899 SN: 0031265, *TAP: SIZE: A LOC: 57 FEET FROM P LINE AT BOUNY, *MB: CODE: BFH2 LOC: ON ELIZA 57FT FROM BOUNY ****/ | 2018-08-01 | EXAMINED AREA BROKE OUT CONCRETE EXCAVATED TO PROPERTY REMOVED LEAD LINE TP PROPERTY BACKFILLED CLEANED AREA NEED COAL MILL FOR DRESS UP
201801376301 | 2018-08-01 | LEAD/PLASTIC | 1102 | SONIAT |  | WILK | MI- METER LEAK ACCT 110728-560600 METER # A215771 EXAMINE INLET SERVICE FOR LEAK 08/07/18 CUST STATED LEAK HAS GOTTEN MUCH WORSE "GUSHING" FROM METER (KSW) 08/13/18 CUST STATES WATER GUSHING OUT AND SOMEONE HAS FELL PER SR#12848986 (AJR) /** 1) MN: A215771 SN: 0012472, *TAP: SIZE: A LOC: 11 FEET FROM P LINE AT CHESTNUT, *MB: CODE: AFM5 LOC: METER ON SONIAT 12.6 FT FROM PL CHESTNUT ****/ | 2018-09-02 | EXCAVTED IN MUDPLOT OVER INLET SERVICE AND OUTLET SERVICE ,REMOVED LEAD FROM METER BOX TO PROPERTY ON TH OUTLET SERVICE REPLACEDWITH PLASTIC.CHANGED BOTH OF METER BOX CURB COCKS TIED BACK ONTO LEAD ON THE INLET NEED TO REMOVE LEAD ON THE INLET TO WATER MAIN CHANGED 5/8 METER. ************OLD METER INFO************** METER:A215771 FAC:28676040 MAKE:ROCKWELL READ:4051
201801376601 | 2018-08-01 | LEAD | 3155 | ROYAL |  | WILK | ML- METER LEAK ACCT# 124558-427407 METER# A299213 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A332455 SN: 0045669, *TAP: SIZE: A LOC: 86 FEET FROM P LINE AT LOUISA, *MB: CODE: BEK2 LOC: 87FT FROM LRPL LOUISA ON ROYAL ****/ | 2018-08-14 | EXCAVATED IN SIDEWALK + REPLACED 5/8 INCH HANDWHEEL + 3/4 INCH LEAD OUTLET FROM METER BOX TO PROPERTY .BACKFILLED + DRESSED UP AREA
201801376701 | 2018-08-02 | LEAD | 1521 | S LIBERTY | MARTIN LUTHER KING BL | WOLK | MI- LEAK NEAR CURB ************L.THOMPSON @ 7:17AM************* OUTLET SERVICE LEAK IN MUDPLOT FLOODING AREA /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ DOTTIE READY 8-8-18 EXP 8-28-18 | 2018-08-04 | EXCAVTED IN MUDPLOT ON OLD SERVICE.MADE REPAIR IN MUDPLOT.
201801377901 | 2018-08-02 | LEAD | 5733 | CONGRESS DR |  | WILK | LOCATION: 176388 MTR# B 022144 CURB COCK FROZEN, UNABLE TO CHANGE METER. PLEASE REPAIR AND CHANGE METER. INLET SERVICE LEAKING FROM CURB COCK ALSO CHANGE METER /** 1) MN: B022144 SN: 0120288, *TAP: SIZE: B LOC: 168 FEET FROM P LINE AT PRENTISS AVE, *MB: CODE: CDLM LOC: 168FT PL PRENTISS AV 8' OUTSIDE 2' INSIDE CURB ****/ | 2018-08-16 | EXCAVATED IN MUDPLOT BY HAND TO CHANGE BAD 3/4 CURB COCK AND RAISE METER BOX TO GRADE. ALSO CHANGED OUT 3/4 METER AS REQUEST IN WORK OREDER. FOUND PLASTIC ON OUTLET AND LEAD ON INLET. D.N.R LEAD NEED MACHINE. BACKFILLED. 3 X 4 MUDPLOT CUT ********OLD METER INFO************ METER:B022144 FAC:32637185 MAKE:ROCKWELL READ:9848
201801378901 | 2018-08-02 | LEAD | 10122 | SEAWOOD |  | WOLK | ML- METER LEAK ACCT# 177834 - 435576 METER# B 030451 OUTLET SERVICE LEAK IN SIDEWALK CON REG /** 1) MN: B030451 SN: 0123145, *TAP: SIZE: B LOC: 220 FEET FROM P LINE AT READ RD, *MB: CODE: BDL LOC: BET WARREN & READ 200' P/L READ RD 8' OUTSIDE 2' ****/ | 2018-08-18 | EXAMINED AREA EXCAVATED ON INLET+ OUTLET SERVICE TRACED TO PROERTY NO LEAK OBSERVED BACKFILLED CLEAN AREA
201801381401 | 2018-08-02 | LEAD | 3363 | ESPLANADE AV | VERNA | WILK | ML- METER LEAK METER# A399126 ACCT# 118621-490759 BAD BLEEDER VALVE LEAKING INSIDE METER BOX /** 1) MN: A143121 SN: 0028610, *TAP: SIZE: A LOC: 80 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: BFH LOC: ON VERNA ST 80' FROM LSPL ESPLANADE AVE ****/ | 2018-08-15 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201801381601 | 2018-08-02 | LEAD/PLASTIC | 5300 | CANAL BL | RAIL RD TRACK | WOLK | MI- CHANGE LEAD WHIP CUSTOMER READY FOR OUTLET TIE IN **********D RANDOLPH 09:39********** 08/14/18 PER C PLAINS UPGRD GIVE OUT ( A ) ******CUSTOMER OUT OF WATER***** OUTLET SERVICE LEAK BEHIND HANDWHEEL FLOODING AREA /** 1) MN: C023953 SN: 0094827, *TAP: SIZE: C LOC: 76 FEET FROM P LINE AT RAIL RD TRACK, *MB: CODE: BEN2 LOC: ON CANAL BLVD., 78' FROM RAILROAD TRACKS,9' OUT- ****/ | 2018-08-14 | EXCAVATED A 3 X 4 MUDCUT AND RENEWED THE OUTLET SERVICE FROM METER TO PROPERTY AND BACKFILL N CLEANUP . ALSO THEY HAVE LEAD ON INLET SERVICE. JOB COMPLETE
201801383301 | 2018-08-03 | LEAD | 13120 | BISCAY | TOULON | WMEX | LOCATIONID#192552-438000 METER#A279506 CEMENT INSIDE METERBOX /** 1) MN: A279506 SN: 0152259, *TAP: SIZE: B LOC: 630 FEET FROM P LINE AT TOULON, *MB: CODE: AE LOC: RES 632FT FROM PL TOULON 8' OUTSIDE PL 4' INSIDE C ****/ | 2018-08-18 | EXAMINED AREA LOCATED METER BROKE OUT CONCRETE ON AND IN METER BOX CLEANED AREA
201801383401 | 2018-08-03 | LEAD | 10915 | DREUX AV | PAPANIA DR | WMTLK | LOCATIONID#171872-436404 METER#A122551 LEAK INSIDE METERBOX /** 1) MN: A122551 SN: 0114781, *TAP: SIZE: A LOC: 109 FEET FROM P LINE AT PAPANIA DR, *MB: CODE: CDN1 LOC: RES 109FT PL PAPANIA DR 7' OUTSIDE PL 3' INSIDE ****/ | 2018-08-19 | ARRIVED ON JOB SITE EXAMINE LEAK INSIDE METER BOX EXCAVATED I MUD PLOT BY HAND MADE REPAIRS ON INLET BACKFILED DRESS UP WORK SITE
201801383701 | 2018-08-03 | LEAD | 6300 | PATTON |  | WMRE | L MITCHELL STATES HE IS UNABLE TO LOCATE SERVICE. PLEASE LOCATE AND CHANGE METER A268658 LOC ID 110990 LOCATE, MARK, RAISE TO GRADE AND CHANGE METER /** 1) MN: A299868 SN: 0016519, *TAP: SIZE: A LOC: 77 FEET FROM P LINE AT PATTON, *MB: CODE: ADHO LOC: ON CALHOUN 76FT FROM PATTON ****/ DOTTIE READY 9-13-18 EXP 10-3-18 | 2019-01-06 | EXCAVATED AND RAISED METER BOX TO GRADE REPAIRED INLET SERVICE LEAK AND REPLACED DEFECTIVE WATER METER\ (TREE ROOTS SLOWED PROGRESS) 3' X 3' MUD CUT - BACKFIILLED- NO DRESS - UP NEEDED *************OLD METER INFO************ METER:A4199081 FAC:15485327 MAKE:HERSEY READ:391
201801383901 | 2018-08-03 | LEAD | 56 | PRATT DR |  | WOLK | LOCATION: 168043 MTR# B 025125 METER BOX BELOW GRADE, PLEASE RAISE TO GRADE AND CHANGE METER BROKEN 3/4 HANDWHEEL ALSO CHANGE METER /** 1) MN: B025125 SN: 0109689, *TAP: SIZE: B LOC: 169 FEET FROM P LINE AT KING DR, *MB: CODE: ADK LOC: 161FT PL KING DR 8' OUTSIDE ****/ | 2018-08-23 | EXCAVATED IN CONCRETE DRIVERWAY REPAIR INLET AND OUTLET SERVICE LINE ALSO RAISE TO GRADEAN RESET3\4 METER DRESSUP WITH RIVERSAND AN COLDMILL JOB REF TO ZONE 1 TO TAKE LEAD LIVE FROM WATER MAIN TOMETER BOX ************OLD METER INFORMATION**************** METER:B025125 FAC:36608842 MAKE:SENSUS READ:2256
201801384201 | 2018-08-03 | LEAD | 2815 | CLOUET |  | WMRE | L UDUEBOR STATES SERVICE IS BURIED. PLEASE RAISE TO GRADE AND SET 5/8 METER. LOC ID 305516 LOCATE, RAISE TO GRADE AND SET 5/8 METER 08/13/18 ALSO EXAMINE OUTLET SERVICE FOR LEAK IN MUDPLOT, UNDER RENOVATION PER SR#12849053 (AJR) /** 1) MN: SN: 0097629, *TAP: SIZE: C LOC: 114 FEET FROM P LINE AT INDUSTRY, *MB: CODE: __ LOC: ON CLOUET, 114' FROM P.L. INDUSTRY, 1.5' OUTSIDE ****/ | 2018-08-19 | ARRIVED ONJOB SITE EXCAVATED IN MUD PLOT BY HAND RAISE METER BOX TO GRADE HOUSE ALREADY HAD METER BACKFILLED DRESS UP AREA
201801384901 | 2018-08-03 | LEAD | 3227 | MONTEGUT | HUMANITY | WMLK | MI- LEAK IN STREET ***FLOODING AREA*** CHANGED FROM 3321 MONTEGUT LEAK ON THE MAIN IN ASPHALT STREET CAUSING STREET TO BUCKLE, FLODING STREET /** 1) MN: A294487 SN: 0127950, *TAP: SIZE: B LOC: 142 FEET FROM P LINE AT BENEFIT, *MB: CODE: ADLM LOC: 142' PL BENEFIT 6' OUTSIDE ****/ | 2018-08-18 | EXAMINED AREA BROKE OUT + EXCAVATED IN STREET EXPOSED ABANDON SERVICE LINE REPAIRED LEAK BACKFILLED + CLEANED AREA. JOB COMPLETE
201801387101 | 2018-08-03 | LEAD | 4725 | CHARLENE DR | GRANT AV | WILK | ML: METER LEAK A279638, ACCT # 180188-446449 INLET SERVICE LEAKING INSIDE METER BOX /** 1) MN: A279638 SN: 0129071, *TAP: SIZE: B LOC: 85 FEET FROM P LINE AT HYDT #2, *MB: CODE: ADLM LOC: RES 85FT FROM R/S HYDT #2 8' OUTSIDE PL 2' INSIDE ****/ | 2018-08-19 | EXCAVATED AND MADE REPAIR ON 3/4 INCH INLET SERVICE MADE 4 X 4 MUD PLOT BACKFILL HOLE.
201801387701 | 2018-08-03 | LEAD | 1127 | FRANCE | MARAIS | WILK | ML-METER LEAK METER#A403154 ACCT#134740-430915 INLET SERVICE LEAKING INSIDE METER BOX /** 1) MN: A260254 SN: 0065444, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT FRANCE, *MB: CODE: CDH7 LOC: ON MARAIS,49' FROM P.L. FRANCE ****/ | 2018-08-24 | EXCAVATED 4 X 8 GUTTER BOTTOM RENEW INLET SERVICE FROM STREET TO METER BOX RENEW OUTLET SERVICE FROM METER BOX TO PROPETY BACKFILED JOB WITH RIVERSAND COLDMILL RAISE METER BOX UP TO GRADE
201801389301 | 2018-08-04 | LEAD | 2125 | ORLEANS AV | N GALVEZ | WILK | INLET SERVICE LEAK /** 1) MN: A138162 SN: 0051297, *TAP: SIZE: A LOC: 1194 FEET FROM P LINE AT GALVEZ N, *MB: CODE: BDL2 LOC: ON ORLEANS AVE.,119.4' FROM L.R.P.L. NO. GALVEZ ****/ | 2018-08-20 | EXCAVATED IN 2 X 4 SIDEWALK CUT MADE REPAIRS ON 3/4 INCH INLET SERVICE AND REPLACE CURB COCK BACKFILLED AREA JOB COMPLETE
201801390601 | 2018-08-04 | LEAD | 3115 | MARIGNY | TREASURE | WILK | ML- METER LEAK ACCT# 162756-474427 MTR# A410707 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A254440 SN: 0101976, *TAP: SIZE: A LOC: 119 FEET FROM P LINE AT TREASURE, *MB: CODE: ADK2 LOC: 119FT FROM PL TREASURE 7' OUTSIDE ****/ | 2018-08-19 | EXCAVATED AND MADE REPAIRS ON 3/4 INCH INLET SERVICE MADE 4 X 4 MUD PLOT BACKFILLED HOLE. JOB COMPLETE
201801392301 | 2018-08-05 | LEAD | 837 | BURGUNDY | DUMAINE | WILK | ML- METER LEAK ACCT# 115535-528638 MTR# A371450 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A331391 SN: 0019012, *TAP: SIZE: A LOC: 38 FEET FROM P LINE AT DUMAINE, *MB: CODE: AEN1 LOC: FRONT 38' P.L. DUMAINE ****/ | 2018-08-20 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201801394102 | 2018-08-05 | LEAD/PLASTIC | 526 | ROBERT |  | WMRE | LOCATIONID#127028-560155 METER#A389448 LOCATE & RAISE TO GRADE /** 1) MN: A274236 SN: 0052002, *TAP: SIZE: A LOC: 101 FEET FROM P LINE AT ANNUNCIATION, *MB: CODE: ADL1 LOC: ON ROBERT,102.2' FROM R.P.L. ANNUNCIATION ****/ /** 1) MN: A274236 SN: 0052002, *TAP: SIZE: A LOC: 101 FEET FROM P LINE AT ANNUNCIATION, *MB: CODE: ADL1 LOC: ON ROBERT,102.2' FROM R.P.L. ANNUNCIATION ****/ | 2018-08-18 | EXCAVATED 3 X 4 MUD PLOT LOCATED AND RAISED METER USED 3/4 METER BOX COMPLETE. BACKFILLED AND CLEANED AREA. STILL HAVE LEAD COMING FROM INLET TO THE MAIN.
201801396001 | 2018-08-06 | LEAD | 2408-10 | DUMAINE | N TONTI | WILK | WM-- LEAK IN SIDEWALK INLET SERVICE LEAK @ VACANT LOT /** AT 2408: 1) MN: A297335 SN: 0038930, *TAP: SIZE: A LOC: 80 FEET FROM P LINE AT TONTI N, *MB: CODE: CEL1 LOC: ON DUMAINE 79.6FT FROM PL OF N TONTI ****/ | 2018-08-17 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON ABANDON INLET SERVICE BACKFILLED JOB WITH RIVERSAND JOB COMPLETE
201801396201 | 2018-08-06 | LEAD/PLASTIC | 2324 | NASHVILLE AV |  | WMTLK | ML- METER LEAK ACCT# 140051-568251 MTR# A385343 //////////////CAUSING POOR PRESSURE????????????????? EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER 08/10/18 CUTOMER NOW OUT OF WATER PER R JACKSO GIVE OUT ***M.ROBINSON @ 12:55PM) /** 1) MN: A138905 SN: 0070764, *TAP: SIZE: Y LOC: 100 FEET FROM P LINE AT MAGNOLIA, *MB: CODE: BDN LOC: ON NASHVILLE AVE 138' FROM PL MAGNOLIA ST ****/ DOTTIE READY 8-14-18 EXP 9-3-18 | 2018-08-13 | EXCAVATED IN MUDPLOT OVER 1"CONTROL LINE,MADE REPAIR ON SERVICE,TIED SERVICE BACK INTO METER BOX,CONTROL LINE IS LEAD. JOB COMPLETE
201801414301 | 2018-08-06 | LEAD | 1320 | MANDEVILLE | URQUHART | WILK | ML METER LEAK *********CSM DOWN ACCT # UNAVAILABLE******* METER# A327616 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A256837 SN: 0064518, *TAP: SIZE: A LOC: 171 FEET FROM P LINE AT URQUHART, *MB: CODE: CEN LOC: ON MANDEVILLE ST 170.5' FROM PL URQUHART 4' FROM ****/ | 2018-08-20 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201801415701 | 2018-08-06 | LEAD/PLASTIC | 4836 | ELYSIAN FIELDS AV | MIRABEAU AV | WOLK | MI- LEAK IN THE SIDEWALK EXAMINE OUTLET SERVICE @ PROPERTY LINE FLOODNIG SIDEWALK & DRIVEWAY ON MIRABEAU AVE, WITH CONSTANT REGISTRATION ***PER INSP R STANWOOD B LEAVE IN SYSTEM*** /** 1) MN: C019855 SN: 0123903, *TAP: SIZE: C LOC: 68 FEET FROM P LINE AT ELYSIAN FIELDS AVE, *MB: CODE: BDH2 LOC: ON MIRABEAU 70FT FROM PL ELYSIAN FIELDS 7FT OUTSD ****/ | 2018-08-14 | EXCAVATED A 2 X 4 CUT IN CONCRETE SIDEWALK TO REPAIR A 1'' OUTLET SERVICE LEAK [ LEAD OUTLRT & PLASTIC INLET ] REPLACED 8FT OF 1'' PVC PIPE FROM THE BOX TO PROPETY BACKFILLED. LET 2 CONES ON JOB SITE JOB COMPLETE PAVING: 2 X 4 CUT C/S
201801416001 | 2018-08-06 | LEAD | 4682 | NOTTINGHAM DR | PRENTISS AV | WMLK | **********PICK UP********** EXAMINE FOR A LEAK ON WATER MAIN /** 1) MN: C012788 SN: 0126969, *TAP: SIZE: C LOC: 35 FEET FROM P LINE AT PRENTISS AVE, *MB: CODE: CDL1 LOC: ON NOTTINGHAM 35FT FROM PRENTISS 8FT OUTSIDE ****/ | 2018-08-19 | ARRIVED ON JOB SITE EXAMINE LEAK IN MUD PLOT EXCAVATED IN MUD PLOT MADE REPAIRS ON SERVICE AT WATER MAIN BACKFILLED DRESS UP WORK SITE
201801416401 | 2018-08-06 | LEAD | 7324 | NELSON | LOWERLINE | WILK | ML METER LEAK ACCT# 139493-579433 METER# A417216 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A295326 SN: 0070115, *TAP: SIZE: B LOC: 61 FEET FROM P LINE AT LOWERLINE, *MB: CODE: CDLM LOC: ON NELSON 61FT FROM LOWERLINE ****/ DOTTIE READY 9-19-18 EXP 10-9-18 | 2018-09-30 | REPLACED 5/8 CURB COCK TIED INTO LEAD.
201801417401 | 2018-08-06 | LEAD/PLASTIC | 2613 | MAGNOLIA | 4TH | WMTLK | MI- LEAK ON THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE AT SIDEWALK FOR A LEAK /** 1) MN: A290212 SN: 0032437, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT 3RD, *MB: CODE: CD LOC: CURB AT 2613 111' P.L. 3RD ****/ DOTTIE READY 8-10-18 EXP 8-30-18 | 2018-08-11 | EXAMINED AREA EXCAVATED IN MUD PLOT EXPOSED LEAK ON INLET SERVICE REPAIRED LEAK UNABLE TO REMOVE LEAD SERVICE LINE DUE TO TIME REPLACE OID METER BOX CASE BACKFILLED CLEANE AREA
201801417501 | 2018-08-06 | LEAD | 3021 | TOULOUSE |  | WMTBG | M FRAZIER STATES SERVICE IS BELOW GRADE. PLEASE RAISE TO GRADE AND CHANGE METER A425545 LOC ID 301112 ADJUST METER BOX TO PROPER GRADE/CHANGE METER /** 1) MN: 000000 SN: 0140096, *TAP: SIZE: A LOC: 177 FEET FROM P LINE AT GAYOSO N, *MB: CODE: CDMN LOC: ON TOULOUSE,175.5' FROM L.S.P.L. NO. GAYOSO ****/ | 2018-08-23 | EXCAVATED IN LIME STONE LOCATED METER BOX ADFJUSTED TO GRADE ABD SET A 5/8 INCH METER BACKFILLED AREA **************OLD METER INFO********* METER:A425545 FAC:16310557 MAKE:HERSEY READ:853
201801417701 | 2018-08-06 | LEAD | 1308 | MOSS | GRAND RTE ST JOHN | WILK | ML- METER LEAK METER# A277544 ACCT# 103849-521918 INLET SERVICE LEAK /** 1) MN: A277544 SN: 0055020, *TAP: SIZE: A LOC: 94 FEET FROM P LINE AT GRAND RTE ST JOHN IRPL, *MB: CODE: AFN2 LOC: 94' FROM IRPL GRAND RTE. ST JOHN ****/ | 2018-08-28 | EXCAVATED 4 X 2 MUD PLOT .REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801418401 | 2018-08-07 | LEAD | 1820 | BENTON | N ROMAN | WMLK | WATER MAIN LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-08-07 | EXCAVATED AND MADE REPAIRS ON ABANDON 1 INCH INLET SERVICE BAKFILLED JOB WITH RIVERSAND COLDMILL
201801419801 | 2018-08-07 | LEAD | 1732 | MILAN | CARONDELET | WRMS | EXCAVATE AND RELOCATE EXISTING 3/4 INCH WATER METER BOX ON MILAN ST 102 FT FROM PL AT BARONNE ST MOVE METER BOX TO 92 FT FROM PL AT BARONNE ST FOR 1730 MILAN ST FOR THE FLAT SUM OF $861.17 DOTTIE READY 8-10-18 EXP 8-30-18 BLAIR PLBG 504-733-9113 AP#122573 WFA 2694 /** 1) MN: A335743 SN: 0056052, *TAP: SIZE: B LOC: 203 FEET FROM P LINE AT CARONDELET, *MB: CODE: AFKL LOC: INSIDE NR FENCE ON MILAN 100' FROM URPL BARONNE ****/ | 2018-08-25 | RELOCATED 5/8 WATER METER 10 FT. OVER TIED INTO LEAD DUE TO CAR PARKED IN FRONT OF LOCATION.(SOC 4FT .X 12 FT. MUDPLOT.) *NOTE 1730 + 1732 IS THE SAME ADDRESS* (JOB COMPLETE)
201801421201 | 2018-08-07 | LEAD/PLASTIC | 2911 | PRESTON PL | ZION | WILK | WM-LEAK IN BETWEEN STREET AND SIDEWALK ********DAMAGE CLAIM******* (S.SLACK @ 11:58AM) CUT INLET SERVICE BY ALL STAR ELECTRIC CUSTOMER OUT OF WATER /** 1) MN: A304240 SN: 0150989, *TAP: SIZE: B LOC: 54 FEET FROM P LINE AT ZION, *MB: CODE: BDL2 LOC: ON PRESTON 54FT FROM ZION ****/ | 2018-08-07 | EXAMINED AREA OBSERVED LEAK ON OUTLET SERVICE EXCAVATED ON OUTLET SERVICE REPAIRED LEAK TO PROPERTY BACKFILLED CLEANED AREA
201801423901 | 2018-08-07 | LEAD | 1912 | SPAIN |  | WILK | ML- METER LEAK ACCT# 129735-483371 METER# A416699 INLET SERVICE LEAK /** 1) MN: A336625 SN: 0059199, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT PRIEUR N, *MB: CODE: CD LOC: 109' P.L. N PRIEUR ****/ | 2018-08-22 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201801424101 | 2018-08-07 | LEAD | 1913 | BENTON | N PRIEUR | WMLK | MI- LEAK AT SIDEWALK ****CUST STATES IT'S FLOODING SIDEWALK AND FRONT LAWN**** BROKEN WATER MAIN IN ASPHALT STREET FLOODING AREA /** 1) MN: A190269 SN: 0133712, *TAP: SIZE: A LOC: 123 FEET FROM P LINE AT NO. PRIEUR, *MB: CODE: ADKO LOC: ON BENTON, 123' FROM P.L. NO. PRIEUR, 7' OUTSIDE ****/ | 2018-08-21 | ARRIVED AT ABOVE LOCATION FOUND SIGNS OF RECENT REPAIRS EXAMINED + FOUND NO LEAK
201801425601 | 2018-08-08 | LEAD | 2741 | ORLEANS AV |  | WMRE | M FRAZIER STATES HE IS UNABLE TO LOCATE BOX TO CHANGE METER. PLEASE LOCATE AND CHANGE METER A373659 LOC ID 126863 LOCATE, RAISE TO GRADE AND CHANGE METER /** 1) MN: A120996 SN: 0055167, *TAP: SIZE: A LOC: 162 FEET FROM P LINE AT WHITE N, *MB: CODE: ADL LOC: ON ORLEANS AVE.,159.7' FROM L.R.P.L. NO. WHITE ****/ | 2018-08-24 | LOCATED METER BOX EXCAVATED IN MUD PLOT + RAISED 5/8 INCH METER BOX BOTTOM TO GRADE ALSO REPLACED 5/8 INCH WATER METER BACKFILLED + DRESSED UP AREA **************OLD METER INFO*********** METER:A373659 FAC:73265730 MAKE:SENSUS READ:14806
201801425801 | 2018-08-08 | LEAD | 2757 | ST PETER |  | WMRE | M FRAZIER STATES SERVICE IS BELOW GRADE, UNABLE TO CHANGE. PLEASE RAISE TO GRADE AND CHANGE METER A290297 LOC ID209960 LOCATE, RAISE TO GRADE AND CHANGE METER /** 1) MN: A290297 SN: 0040931, *TAP: SIZE: B LOC: 10 FEET FROM P LINE AT N WHITE, *MB: CODE: CDLM LOC: ON ST. PETER 11FT. FROM DIV. PL N. WHITE 9FT. ****/ | 2018-08-28 | EXCAVATED 8 X 5 SIDEWALK CUT FOUND METER BOX LOCATED UNDERNEATH STEPS BACKFILLED AND CLEANED THE AREA MARK SIDEWALK + METER TOP WITH BLUE PAINT
201801428501 | 2018-08-08 | LEAD | 1508 | FRANCE | N ROBERTSON | WILK | MI- LEAK IN THE STREET * CALLER STATES WATER IS TURNING GREEN* INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A322980 SN: 0075515, *TAP: SIZE: A LOC: 88 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: BDK2 LOC: ON FRANCE ST 88' FROM PL N ROBERTSON ST ****/ | 2018-08-24 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH ABANDON INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND. JOB COMPLETE
201801431101 | 2018-08-09 | LEAD | 2621 | CLARA | 4TH | WMTLK | METER # A420882 LOCATION# 116806-544543 LEAK INSIDE METER BOX /** 1) MN: A289224 SN: 0023333, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT 4TH, *MB: CODE: CDN1 LOC: OPP DOOR CURB 12FT LPL CURB 115' P.L. 4TH ****/ DOTTIE READY 8-16-18 EXP 9-5-18 | 2018-08-19 | EXAMINED AREA EXCAVATED ON INLET + OUTLET SERVICE CLEAQNED OUT METER BOX OBSERVED LEAK ON OUTLET SERVICE REPAIRED LEAK BACKFILLED + CLEANED AREA
201801431201 | 2018-08-09 | LEAD | 1522 | ORETHA CASTLE HALEY BL | MELPOMENE AV | WMTLK | METER# A399043 LOCATION# 105513-549751 LEAK INSIDE METER BOX /** 1) MN: A304372 SN: 0002076, *TAP: SIZE: A LOC: 122 FEET FROM P LINE AT MELPOMENE AVE, *MB: CODE: BDMW LOC: IN ALLEY CENTER METER,122' FROM P.L. MELPOMENE AVE ****/ DOTTIE READY 8-16-18 EXP 9-5-18 | 2018-08-19 | EXAMINED AREA LOCATED METER NO METER FOUND IN METER BOX + NO LEAK OBSERVED CLEANED AREA
201801434001 | 2018-08-09 | LEAD | 3009 | BIENVILLE |  | WMRE | L UDUEBOR STATES SERVICE IS BURIED UNDER NEW DRIVEWAY, UNABLE TO SET METER. PLEASE RAISE AND SET 5/8 METER. LOC ID305581 LOCATE, RAISE TO GRADE AND SET 5/8 METER, RENNOVATED HOUSE /** 1) MN: A300882 SN: 0051134, *TAP: SIZE: B LOC: 96 FEET FROM P LINE AT GAYOSO N, *MB: CODE: ADL LOC: ON BIENVILLE 96FT FROM PL N GAYOSO OPP GATE ****/ | 2018-08-31 | MADE 2 X 4 CUT IN DRIVEWAY AND LOCATED METER BOX AT MEASUREMENT GIVEN SET 5/8 INCH METER BACKFILLED AREA
201801436301 | 2018-08-09 | LEAD | 2879 | ANNETTE | INDUSTRY | WILK | ML-METER LEAK ACCOUNT#187593-496176 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A291413 SN: 0143909, *TAP: SIZE: B LOC: 117 FEET FROM P LINE AT INDUSTRY, *MB: CODE: AD LOC: ON ANNETTE 117FT FROM PL INDUSTRY 8FT OUTSIDE PL ****/ | 2018-08-24 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK 5/8 INCH SERVICE MADE REPIAR ED ON INLET BACKFILLED JOB WITH RIVERSAND
201801439201 | 2018-08-10 | LEAD/PLASTIC | 5701 | NORLAND AV | CHELSEA DR | WILK | ML- METERLEAK ACCT# 231793-418126 METER# A411308 INLET SERVICE LEAK IN MUDPLOT, METER UNDER WATER /** 1) MN: A243239 SN: 0143716, *TAP: SIZE: B LOC: 391 FEET FROM P LINE AT CHELSEA DR, *MB: CODE: CDN1 LOC: ON NORLAND 33FT FROM DIV P/L CHELSEA 3FT INSIDE ****/ | 2018-10-29 | EXAMINED AREA CLEANED OUT MAKE BOX EXCAVATED ON INLET AND OUTLET SERVICE EXPOSED LEAK ON OUTLET SERVICE REPAIRED LEAK BACKFILLED CLEANED AREA
201801442602 | 2018-09-07 | LEAD | 2228 | REYNES | N MIRO | WMRE | EXCAVATED 4 X 6 MUD PLOT UNABLE TO LOCATE METER BOX REFER TO ZONE 4 TO LOCATE WITH MACHINE BACKFILL JOB WITH MUD /** 1) MN: A293583 SN: 0130333, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT MIRO N, *MB: CODE: ADL1 LOC: RES ON REYNES 73' P/L N MIRO OPP END OF HOUSE ****/ | 2018-09-13 | EXCAVATED 4 X 12 MUD PLOT TRENCH AND LOCATED METER BOX REPLACED METER BOX CASING AND MARKED METER LOCATED BACKFILLED AREA
201801443401 | 2018-08-11 | LEAD | 632 | ELYSIAN FIELDS AV | ROYAL | WLPR | MI SEE WHY NO WATER ACCT# 128502-485383 METER# A268039 EXAMINE INLET SERVIE FOR POOR PRESSURE, NO OUTSIDE FAUCET, CUSTOMER HAS WATER PER INSPC /** 1) MN: A295612 SN: 0055648, *TAP: SIZE: A LOC: 40 FEET FROM P LINE AT ROYAL, *MB: CODE: CEMD LOC: 42' P.L. ROYAL ****/ | 2018-08-23 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK ALSO REPLACED DAMAGED 5/8 INCH WATER METER BACKFILLED + DRESSED UP AREA REFER BACK TO ZONE 4 TO HAVE LEAD REMOVED FROM STREET *CUSTOMER HAS EXCELLENT PRESSURE AT METER ***********OLD METER INFO********** METER:A268039 FAC:39732007 MAKE:ROCKWELL READ:2665
201801447901 | 2018-08-12 | LEAD | 1120 | FRANKLIN AV | MARAIS | WILK | WM LEAK BETWEEN STREET & SIDEWALK CHANGED FROM 1200 FRANKLIN AV INLET SERVICE LEAKING IN MUDPLOT NEAR GAS SERVICE FOR DOMINO'S FLOODING CURB AND STREET LEAK IS ON MARAIS /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-08-28 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH ABANDONED INLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201801448101 | 2018-08-12 | LEAD | 222 | N TONTI | BIENVILLE | WILK | ML METER LEAK ACCT# 116005-522780 METER# A337566 INLET SERVICE LEAKING IN MUDPLOT NEAR SIDEWALK SPOKE WITH CUSTOMER /** 1) MN: A337566 SN: 0020189, *TAP: SIZE: A LOC: 86 FEET FROM P LINE AT BIENVILLE, *MB: CODE: AFLN LOC: ON TONTI 86FT FROM BIENVILLE ****/ | 2018-09-20 | EXCAVATED IN GUTTER BOTTOM + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201801448601 | 2018-08-12 | LEAD | 220 | S WHITE | PALMYRA | WILK | ML METER LEAK ACCT# 152211-531561 METER# A431397 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: SN: 0039906, *TAP: SIZE: B LOC: 175 FEET FROM P LINE AT CLEVELAND AVE, *MB: CODE: CFL LOC: ON SO. WHITE, 175.3' FROM P.L. CLEVELAND AVE., 2' ****/ | 2018-08-24 | REPLACED BROKEN HANDWHEEL IN METER BOX AT ABOVE LOCATION
201801448901 | 2018-08-12 | LEAD | 2308 | A P TUREAUD AV | N TONTI | WILK | WM LEAK @ THE CURB ****CHANGED FROM 2304 A P TUREAUD*** INLET SERVICE LEAK ON SIDEWALK, FLOODING CURB & STREET (C) /** 1) MN: A234336 SN: 0069894, *TAP: SIZE: B LOC: 92 FEET FROM P LINE AT TONTI N, *MB: CODE: BD LOC: ON A.P. TUREAUD AVE.,86' FROM U.S.P.L. NO. TONTI ****/ | 2018-08-27 | EXCAVATED 8 X 2 SIDEWALK CUT RENEW OUTLET SERVICE LINE FROM METER BOX UP TO PROPERTY BACKFILLED AND CLEANED THE AREA
201801452001 | 2018-08-13 | LEAD | 1467 | N WHITE |  | WILK | METER LEAK ACCOUNT #133762-490859 METER #A403398 EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX FOUND METER OFF LEFT METER OFF /** 1) MN: A296124 SN: 0064636, *TAP: SIZE: B LOC: 279 FEET FROM P LINE AT LEPAGE, *MB: CODE: DM LOC: ON NO. WHITE, 277' FROM P.L. LEPAGE ****/ | 2018-08-24 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801454101 | 2018-08-13 | LEAD/PLASTIC | 2329 | ODIN | SPAIN | WILK | ML - METER LEAK ACCT#162962-471346 METER#A400561 INLET SERVICE LEAK IN MDPLOT /** 1) MN: A157141 SN: 0102679, *TAP: SIZE: A LOC: 86 FEET FROM P LINE AT SPAIN, *MB: CODE: ADK6 LOC: 88FT FROM PL SPAIN 7' OUTSIDE PL 3' INSIDE CURB ****/ | 2018-08-21 | EXCAVATED A 3 X 4 MUDPLOT AND 2 X 2 IN STREET REPLACED 5/8 METER BOX COCK DISCOVERED LEAD ON INLET TO MAIN ,TRIED TO REPLACED LEAD WITH PLASTIC BUT HAD A PROBLEM WITH THE BACKHOE. OUTLET HAD PIPE TO THE PROPERTY BARRICADED AREA OFF
201801455101 | 2018-08-13 | LEAD | 1718 | DUFOSSAT |  | WILK | ML METER LEAK ACCOUNT #128160-571137 METER #A339441 BAD BLEEDER VALVE /** 1) MN: A144292 SN: 0055427, *TAP: SIZE: A LOC: 172 FEET FROM P LINE AT DRYADES, *MB: CODE: CD1 LOC: ON DUFOSSAT,134.6' FROM S.P.L. DRYADES ****/ | 2018-09-30 | REPLACED 5/8 CURB COCK TIED INTO LEAD. (SOC 3FT X 3 FT S/W)
201801455402 | 2018-08-13 | LEAD | 3825 | CONSTANCE |  | WMRE | LOCATIONID#120087-716550 METER#A380895 METER BURIED,LOCATE & RAISE -- NEED MACHINE /** 1) MN: A327391 SN: 0034884, *TAP: SIZE: B LOC: 40 FEET FROM P LINE AT GEN TAYLOR, *MB: CODE: CFK1 LOC: INSIDE 39' P.L. GEN TAYLOR ****/ /** 1) MN: A327391 SN: 0034884, *TAP: SIZE: B LOC: 40 FEET FROM P LINE AT GEN TAYLOR, *MB: CODE: CFK1 LOC: INSIDE 39' P.L. GEN TAYLOR ****/ | 2018-08-19 | EXCAVATED 11 X 8 MUDPLOT ON PROPERTY SIDE AND 10 X 2 ON CURB SIDE. LOCATED AND RAISED METER . REMOVED LEAD FROM OUTLET SIDE. ALSO REPLACED METER WITH A NEW METER. LEAD NEEDS TO BE REMOVED FROM INLET TO MAIN. *************OLD METER INFO*********** METER:A380895 FAC:73275326 MAKE:SENSUS READ:7927
201801457301 | 2018-08-13 | LEAD/PLASTIC | 3633 | HAVANA | ST DENIS | WOLK | WM-LEAK BETWEEN SIDEWALK AND STREET OUTLET SERVICE LEAKING IN GRASS /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-08-22 | EXCAVATED RAISED 3/4 METER TO GRADE. REMOVED LEAD FROM OUTLET TO PROPERTY . REPLACED WITH 9 FEET OF PLASTIC REFER BACK TO ZONE BECAUSE IMMOBLE VEHICLE IN WAY THERFORE UNABLE TO RENEW INLET FROM MAIN BACKFILLED AND DRESSED CUT.
201801463401 | 2018-08-15 | LEAD | 2523 | DUMAINE | N BROAD | WMTLK | LOCATIONID#211077-700380 METER#A421547 LEAK INSIDE METERBOX /** 1) MN: A289168 SN: 0006357, *TAP: SIZE: B LOC: 17 FEET FROM P LINE AT BROAD, *MB: CODE: BE1 LOC: ON DUMAINE 16' FROM DIV. P.L. BROAD 8FT OUTSIDE ****/ | 2018-08-23 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801464001 | 2018-08-15 | LEAD | 2556 | CLOVER |  | WMRE | M FRAZIER SAYS HE IS UNABLE TO LOCATE SERVICE. PLEASE LOCATE AND CHANGE METER A324703 LOC ID 148749 LOCATE, RAISE TO GRADE AND CHANGE METER /** 1) MN: A125573 SN: 0085130, *TAP: SIZE: A LOC: 708 FEET FROM P LINE AT CLEMATIS, *MB: CODE: BD4 LOC: ON CLOVER ST 708' FROM PL CLEMATIS ****/ | 2018-09-10 | EXCAVATED DOWN ON INLET AND OUTLET SERVICES. FOUND LEAD ALSO INLET WAS LEAKING AND UPPERCASING WAS SHIFTED. MADE REPAIRS BY REPLACING COCK, WASHERS, HADWHEEL, BOTTOM, CASING, AND SERVICES FROM CURB TO PROPERTY. BACKILLED
201801467401 | 2018-08-15 | LEAD | 1278 | CASA CALVO | SOCRATES | WOLK | ML- METER LEAK METER# A397800 LOCATION# 229592 EXAMINE OUTLET SERVICE FOR A LEAK @ PROPERTY LINE **NOT A DUPLICATE** /** 1) MN: A239110 SN: 0130361, *TAP: SIZE: B LOC: 112 FEET FROM P LINE AT SOCRATES, *MB: CODE: CDN1 LOC: ON CASA CALVO, 112' FROM P.L. SOCRATES, 7' OUTSIDE ****/ | 2018-08-22 | EXCAVATED IN MUDPLOT ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND REFERRE TO ZONE TO REMOVE LEAD
201801467901 | 2018-08-15 | LEAD | 1007 | DESIRE | N RAMPART | WMTLK | ML-METER LEAK ACCT#132991-427964 METER#A415323 CUST IS EXPERIENCING POOR PRESSURE EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A252390 SN: 0063838, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT RAMPART N, *MB: CODE: AEMN LOC: 76FT FROM PL N RAMPART ****/ | 2018-08-28 | REPLACED 5/8 ICH WASHERS IN METER BOX .. CUSTOMER HAS EXCELLENT WATER PRESSURE
201801468101 | 2018-08-15 | LEAD | 2923 | LEPAGE | N DUPRE | WMTLK | ML-METER LEAK EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: B024476 SN: 0023265, *TAP: SIZE: B LOC: 208 FEET FROM P LINE AT DUPRE N, *MB: CODE: BFL5 LOC: 208FT FROM ISPL DUPRE ****/ | 2018-08-23 | EXAMINED + FOUND NO LEAK
201801468301 | 2018-08-15 | LEAD | 2551 | CLOVER | CLEMATIS | WILK | WM-LEAK BETWEEN SIDEWALK & STREET INLET SERVICE LEAK IN MUDPLOT LEAKING FROM BLEEDER VALVE /** 1) MN: A311462 SN: 0085022, *TAP: SIZE: A LOC: 673 FEET FROM P LINE AT CLEMATIS, *MB: CODE: AD LOC: 673' P.L. CLEMATIS ****/ | 2018-09-12 | EXCAVATED IN MUDPLOT BY HAND TO CHANGE BAD 5/8 CURB COCK AND REMOVE LEAD FROM OUTLET. D.N.R LEAD FROM INLET SERVICE NEED MACHINE. BACKFLL
201801470901 | 2018-08-16 | LEAD | 1628 | FRENCHMEN | DERBY PL | WMTLK | ACCT# 102834-493616 MTR# A399553 INSPECTOR FOUND CONSTANT REGISTRATION AND A LEAK AT HANDWHEEL /** 1) MN: A243772 SN: 0027556, *TAP: SIZE: B LOC: 101 FEET FROM P LINE AT DERBIGNY N URPL, *MB: CODE: OOO LOC: 100.6' FROM URPL DERBIGNY ****/ | 2018-08-27 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801471501 | 2018-08-16 | LEAD | 700 | PAULINE |  | WMBC | LOCATION: 113546 MTR# A 287501 PER INSP UDEBOR, METER CASING OVER CURB IN CONCRETE SIDEWALK. PLEASE REPAIR AND CHANGE METER. TOP CASING SHIFTED OVER CURB COCK. REPAIR & CHANGE METER /** 1) MN: A287501 SN: 0050214, *TAP: SIZE: A LOC: 80 FEET FROM P LINE AT PAULINE, *MB: CODE: AEHK LOC: SIDE ST ON ROYAL 80' P.L. PAULINE ** 2) MN: SN: 0000000, *TAP: SIZE: H LOC: 41 FEET FROM P LINE AT DAUPHINE, *MB: CODE: __ LOC: VALVE ON PAULINE, 40.6' FROM P.L. DAUPHINE,6' IN- ****/ | 2018-08-31 | ADJUSTED METER BOX CASING PROPERLY + REPLACED 5/8 INCH WATER METER ***************OLD METER INFO************* METER:A287501 FAC:49137095 MAKE:SENSUS READ:8684
201801475601 | 2018-08-16 | LEAD | 2620 | MISTLETOE |  | WILK | S BIBBINS STATES SERVICE IS LEAKING BEHIND CURB COCK, FILLING BOX TOO QUICKLY FOR HIM TO PUMP OUT AND SET METER. PLEASE REPAIR AND SET 5/8 METER. LOC ID 134146 INLET SERVICE LEAK BEHIND CURB COCK ALSO SET 5/8 METER /** 1) MN: A293485 SN: 0038374, *TAP: SIZE: A LOC: 169 FEET FROM P LINE AT APPLE, *MB: CODE: BDN1 LOC: ON MISTLETOE, 169.6' FROM U.S.P.L. APPLE ****/ | 2018-08-25 | EXCAVATED IN MUDPLOT & TREE ROOTS.REPAIR 5/8 STOP COCK & COCK LEASD LINE.ALSO RESET 5/8 A415496. DRESS UP WITH RIVERSAND. JOB REF TO ZONE 1 TO TAKE LEAD LINEOUT FROM WATER MAIN TO METERBOX
201801481602 | 2018-08-22 | LEAD | 818 | LESSEPS | DAUPHINE | WILK | INLET SERVICE LEAK /** 1) MN: A151957 SN: 0046912, *TAP: SIZE: B LOC: 127 FEET FROM P LINE AT DAUPHINE, *MB: CODE: ADL LOC: CURB ON LESSEPS 134 FT FROM PL DAUPHINE ****/ | 2018-09-06 | EXCAVATED IN ASPHALT STRET + MADE REPAIRS ON 3/4 INCH INLET SERVICE LINE COMPACTED BACKFILLED + DRESSED UP AREA
201801482001 | 2018-08-17 | LEAD | 1312 | GORDON |  | WMRE | INSP L UDUEBOR STATES SERVICE IS BURIED. PLEASE RAISE TO GRADE AND SET 5/8 METER. LOC ID 305639 LOCATE, RAISE & SET 5/8 METER /** 1) MN: SN: 0088622, *TAP: SIZE: A LOC: 111 FEET FROM P LINE AT URQUHART, *MB: CODE: CD LOC: RES ON GORDON 111FT FROM PL URQUHART ****/ | 2018-09-04 | EXCAVATED IN MUD PLOT + SIDEWALK + LOCATED 5/8 INCH METER BOX + SET 5/8 INCH METER BACKFILLED+ DRESSED UP AREA
201801483601 | 2018-08-17 | LEAD | 4534 | CHESTNUT | CADIZ | WILK | LOCATION ID-104781 MTR-A249184 MTR ON/CUST NOT GETTING WATER EXAMINE INLET SERVICE , *****CUSTOMER OUT OF WATER HOUSE UNDER RENOVATIONS***** /** 1) MN: A249184 SN: 0002173, *TAP: SIZE: A LOC: 15 FEET FROM P LINE AT CADIZ, *MB: CODE: CGLM LOC: ON CHESTNUT 15FT FROM URPL OF CADIZ ****/ | 2018-10-26 | EXAMINED 5/8 SERVICE FOUND WATER ON SERVICE GUT 5/8 CURB COCK LEAKING.REPLACED 5/8 CURB COCK LEAKING.REPLACED CURB COCK TIED INTO LEAD.(SOC 3FT .X 3 FT .S/W)
201801483801 | 2018-08-17 | LEAD | 1116 | ST CLAUDE AV | URSULINES AV | WMTLK | ML: METER LEAK ACCT# 112076-526161 METER# A427573 PLEASE REPAIR ASAP EXAMINE INLET & OUTLET SERVICE FOR A LEAK WITH CONSTANT REGISTRATION ON THE METER. CUSTOMER COMPLAINING ABOUT A HIGH BILL /** 1) MN: A274292 SN: 0039334, *TAP: SIZE: A LOC: 160 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: AE2 LOC: ON ST CLAUDE 160' FROM IRPL URSULINES AVE 4' FROM ****/ | 2018-09-24 | EXAMINED METER AT ABOVE LOCATION + FOUND NO CONSTANT COCK IS LEAKING FROM BLEEDER EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801491901 | 2018-08-20 | LEAD | 1032 | BARTHOLOMEW | ST CLAUDE AV | WOLK | LOCATIONID#127724-428311 METER#A396411 CONSTANT REG.LEAK INSIDE METERBOX /** 1) MN: A240505 SN: 0054130, *TAP: SIZE: A LOC: 135 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: BELM LOC: ON BARTHOLOMEW 135FT FROM LRPL ST CLAUDE ****/ | 2018-08-31 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801492401 | 2018-08-20 | LEAD | 3318 | CASTIGLIONE | ROMULUS | WOLK | LOCATIONID#168160-493019 METER#A295842 CONSTANT ON REG.,LEAK INSIDE METERBOX /** 1) MN: A295842 SN: 0109881, *TAP: SIZE: A LOC: 229 FEET FROM P LINE AT ROMULUS, *MB: CODE: ADM3 LOC: 229FT PL ROMULUS 7' OUTSIDE ****/ | 2018-09-27 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801496501 | 2018-08-20 | LEAD/PLASTIC | 3313 | LAUREL | TOLEDANO | WILK | ML- MEAK LEAK***ACCT#117458-538486 METER LEAK#A406866 BAD NLET SERVICE LEAK FROM CURB COCK /** 1) MN: A260790 SN: 0020519, *TAP: SIZE: A LOC: 114 FEET FROM P LINE AT TOLEDANO, *MB: CODE: CD LOC: ON LAUREL 113FT FROM PL OF TOLEDANO ****/ | 2018-10-17 | ARRIVED AT ABOVE LOCATION EXAMINED ,EXCAVATED BYHAND AND MADE REPAIRS TO STOP LEAK ON R/8 INLET SERVICE LINE.BACKFILLED CLEANED UP AND WASHED DOWN AREA TO COMPLETE JOB ALSO RENEWED OUTLET BY REMOVING LEAD AND REPLACED WITH PLASTIC TUBING FROM METER BOX TO PROPERTY LINE (LEAD INLET)(SOC 3FT .X 4 FT .S/W)
201801501901 | 2018-08-20 | LEAD/PLASTIC | 102 | KINGSTON CT | WOODLAND | WMTLK | WM-LEAK ON THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE @ SIDEWALK FOR A LEAK LEFT ( 1) ONE CONE FOR PROTECTION /** 1) MN: A218002 SN: 0114479, *TAP: SIZE: A LOC: 160 FEET FROM P LINE AT WOODLAND, *MB: CODE: BDL7 LOC: ON KINGSTON CT., 160' FROM P.L. WOODLAND, 10' OUT- ****/ | 2018-08-27 | BROKE CONCRETE TO EXCAVATE ON THE INLET AND OUTLET TO MAKE REPAIR CHANGED OUTLET TO PROPERTY NEED TO RETURN WITH MACHINE EXCAVATE ON INLET TO WATER MAIN
201801507301 | 2018-08-21 | LEAD | 5624 | ABBEY DR | CHELSEA DR | WILK | ML- METER LEAK ACCT# 231351-417982 METER# A 265208 INLET SERVICE LEAK 10/12/18 CUSTOMER STATES LEAK IS GETTING WORSE (KSW) /** 1) MN: A265208 SN: 0141947, *TAP: SIZE: B LOC: 55 FEET FROM P LINE AT CHELSEA DR, *MB: CODE: __ LOC: ON ABBEY DR 55' FROM DPL CHELSEA DR 2' INSIDE CURB ****/ | 2018-11-03 | EXAMINED AREA PUMPED DOWN + CLEANED OUT METER BOX CDSERVED LEAK ON INELT SERVICE REPAIRED LEAK CLEANED THE AREA
201801507701 | 2018-08-21 | LEAD/PLASTIC | 835 | WHITNEY AV | HOMER | WILK | ML - METER LEAK ACCT#224880-403601 METER#A370531 **FLOODING AREA** INLET SERVICE LEAK /** 1) MN: A300878 SN: 0094544, *TAP: SIZE: A LOC: 35 FEET FROM P LINE AT HOMER, *MB: CODE: AE LOC: ON WHITNEY AVE., 35' FROM P.L. HOMER ****/ | 2018-09-10 | EXAMINED AREA EXCAVATED ON INLET AND OUTLET SERVICE EXPOSED LEAK ON OUTLET SERVICE REPAIRED LEAK BACKFILLED AFTER REMOVING LEAD TO PROPERTY CLEANED AREA
201801510801 | 2018-08-22 | LEAD | 1757 | N GAYOSO |  | WILK | ML-- METER LEAK METER# A123242 ACCT# 188628-512281 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A125949 SN: 0059364, *TAP: SIZE: A LOC: 125 FEET FROM P LINE AT AUBRY, *MB: CODE: BDO2 LOC: 125FT FROM LSPL AUBRY BY TREE ****/ | 2018-09-24 | REPLACED 5/8 INCH WASHER IN METER BOX
201801513001 | 2018-08-22 | LEAD | 2213 | MONTICELLO | N TONTI | WILK | MI- DEPRESSION IN THE STREET INLET SERVICE LEAK IN GRAVEL ROAD ON MAIN CAUSING LARGE HOLE LEFT ONE (1) BARRICADE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-09-13 | MADE 8 X 8 CUT IN BLACK TOP STREET AND MADE REPAIRS ON 3/4 INCH INLET SERVICE FOR ABANDON LOT BACKFILLED AREA
201801513601 | 2018-08-22 | LEAD | 1522 | ROUSSELIN DR | LAPEYROUSE | WILK | MI- LEAK AT THE SIDEWALK INLET SERVICE LEAK NO METER IN BOX /** 1) MN: A328247 SN: 0061984, *TAP: SIZE: A LOC: 147 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: CELM LOC: ON ROUSSELINE 147' FROM URPL LAPEYROUSE ST ****/ | 2018-09-12 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA NO METER
201801513701 | 2018-08-22 | LEAD | 4608 | S ROBERTSON | CADIZ | WILK | MI- LEAK BETWEEN STREET AND SIDEWALK CHANGED FROM 4604 S ROBERTSON INLET SERVICE LEAK NO METER IN BOX, CURB COCK IN OFF POSITION WATER PASSING THROUGH FLOODING GUTTER BOTTOM TO HOUSES DOWN /** 1) MN: A320741 SN: 0025780, *TAP: SIZE: B LOC: 60 FEET FROM P LINE AT CADIZ, *MB: CODE: ADK LOC: 60FT FROM PL CADIZ 8' OUTSIDE PL 2' INSIDE CURB ****/ | 2018-08-23 | EXCAVATED IN MUDPLOT ON INLET LEAK ON LEAD MADE ALL REPAIRS TO STOP LEAK BACKFILL WITH RIVERSAND REFERRE TO ZONE 3TO REMOVE LEAD
201801515301 | 2018-08-22 | LEAD | 2223 | MARIGNY |  | WILK | ML METER LEAK ACCOUNT #122300-483860 METER #A268753 INLET SERVICE LEAK FLOODING SIDEWALK /** 1) MN: A268753 SN: 0040847, *TAP: SIZE: B LOC: 150 FEET FROM P LINE AT TONTI N, *MB: CODE: CFM1 LOC: ON MARIGNY 150FT FROM PL OF N TONTI ****/ | 2018-09-19 | EXCAVATED 3 X 2 SIDEWALK CUT RENEWED OUTLET TO PROPERTY AND REPLACED 5/8 ICH METER COCK TO STOP LEAK REFER BACK TO ZONE 4 TO REMOVE FROM STREET
201801519701 | 2018-08-23 | LEAD | 612 | DUMAINE |  | WMBK | INSP SAID HE IS UNABLE TO CHANGE METER. CASING OVER WHEEL IN CONCRETE. PLEASE REPAIR AND CHANGE METER A332638 LOC ID 118010 METER BOX SHIFTED OVER CURB COCK, UNALBE TO CHANGE METER /** 1) MN: A332638 SN: 0026708, *TAP: SIZE: B LOC: 69 FEET FROM P LINE AT CHARTRES, *MB: CODE: AFR5 LOC: APT 75' P.L. CHARTRES ****/ | 2018-09-13 | RE-ADJUSTED 5/8 INCH METER BOX CASING + REPLACED 5/8 METER **********************OLD METER INFO******************** METER:A332638 FAC:56043228 MAKE:SENSUS READ:15593
201801520201 | 2018-08-23 | LEAD | 2303 | ST BERNARD AV |  | WOLK | INSP SAID INLET AND OUTLET NOT LINING UP, CAUSING LEAK. PLEASE REPAIR METER A418409 LOC ID 144609 EXAMINE OUTLET SERVICE FOR LEAK /** 1) MN: A329234 SN: 0076140, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT ST BERNARD AVE, *MB: CODE: BDHK LOC: ON N TONTI 64FT FROM PL OF ST BERNARD AVE ****/ | 2018-09-12 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801521701 | 2018-08-23 | LEAD | 2538 | JASMINE | FRANKLIN AV | WILK | ML- METER LEAK MTR#-A4030407 ACCT# 127465-476258 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A315690 SN: 0087200, *TAP: SIZE: A LOC: 314 FEET FROM P LINE AT IRIS, *MB: CODE: ADM LOC: FRONT 312' P.L. IRIS ****/ | 2018-09-13 | EXCAVATED IN A 4X4 MUDPLOT BY HAND FOUND LEAD ON INLET AND PLASTIC ON OUTLET WTIH 5/8 CURB COCK LEAKING. REPLACE 5/8 CURB .RAISE METER TO GRADE AND BACKFILL AND DRESS WITH RIVER SAND. JOB COMPLETE
201801521802 | 2018-08-23 | LEAD | 2541 | JASMINE | FRANKLIN AV | WSNR | RENEW LEAD FROM MAIN TO METER PR H RICHARD /** 1) MN: A128309 SN: 0086700, *TAP: SIZE: A LOC: 281 FEET FROM P LINE AT IRIS, *MB: CODE: AD2 LOC: UPL - 281' P.L. IRIS ****/ | 2018-09-27 | EXCAVATED IN A 5X7 STREET CUT FOUND LEAD ON INLET . COULDNT FINISH JOB DO TO THE HEAVY RAIN IN THE FORECAST.
201801523101 | 2018-08-23 | LEAD | 1356 | ANNETTE |  | WMTLK | ML METER LEAK ACCOUNT #267163-722611 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-09-17 | EXCAVATED IN SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801523202 | 2018-10-08 | LEAD/PLASTIC | 1531 | SUMNER | PTOLEMY | WILK | LEAK ON SIDEWALK /** 1) MN: A239449 SN: 0112441, *TAP: SIZE: B LOC: 216 FEET FROM P LINE AT PTOLEMY, *MB: CODE: BFLM LOC: 216FT FROM P.L. PTOLEMY ****/ | 2018-10-08 | WE EXCAVATED TO MAKE REPAIRS TO A 3/4 INLET LEAK UNDER A TREE WE HAD TO RELOCATE A 3/4 METER BOX WE HAVE TO COME BACK TO DRESS UP TWOCUT ONEIN THE STREET AND ATFER ON THE SIDEWALK. JOB COMPLETE
201801524801 | 2018-08-23 | LEAD | 1601 | FRANCE | N CLAIBORNE AV | WILK | ML-METER LEAK METER#A153133 ACCT#182008-702121 INLET SERVICE LEAK INSIDE METER BOX IN SIDEWALK /** 1) MN: A269581 SN: 0079690, *TAP: SIZE: A LOC: 14 FEET FROM P LINE AT NO. CLAIBORNE AVE., *MB: CODE: BDL1 LOC: ON FRANCE,12' FROM L.S.P.L. NO. CLAIBORNE AVE. ****/ | 2018-09-21 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801525601 | 2018-08-24 | LEAD | 3221 | ST CLAUDE AV |  | WOLK | LOCATION: 136730 MTR# A 418309 PER L UDEBOR, OUTLET SERVICE LEAKING BEHIND WHEEL. OUTLET SERVICE LEAK IN BOX BEHIND HANDWHEEL /** 1) MN: A265874 SN: 0031425, *TAP: SIZE: B LOC: 163 FEET FROM P LINE AT LOUISA, *MB: CODE: CDM2 LOC: 163FT FROM PL LOUISA ****/ | 2018-10-01 | EXCV FOUND LEAK AT 3221 REPLACE WHEEL AND WASHERS THEN BACKFILL AND WENT TO WAREHOUSE TO GET 4 BAGS OF SAND. LEAD ON INLET AND OUTLET.
201801525701 | 2018-08-24 | LEAD | 2224 | CAFFIN AV |  | WILK | LOCATION: 170210 MTR# A 292150 PER INSP UDEBOR, LEAK COMING FROM BEHIND CURB COCK. INLET SERVICE LEAK IN BOX /** 1) MN: B018647 SN: 0127607, *TAP: SIZE: B LOC: 185 FEET FROM P LINE AT MIRO N, *MB: CODE: AFK LOC: RES ON CAFFIN 187' PL N MIRO 5TH MTR FROM N MIRO ****/ | 2018-09-21 | EXCAVATED 3 X 2 MUD PLOT MADE ON 1 INCH INLET SERVICEAND REPLACED 5/8 INCH METER COCK BACKFILLED AND CLEANED THE AREA
201801528201 | 2018-08-24 | LEAD | 1336 | ST FERDINAND | N VILLERE | WMTLK | ML- METER LEAK METER# C035202 ACCT# 178281-701348 EXAMINE INLET AND OUTLET SERVICE FOR LEDAK FLOODING CURB AND STREET, SPOKE WITH CUSTOMER /** 1) MN: C023272 SN: 0123894, *TAP: SIZE: C LOC: 54 FEET FROM P LINE AT VILLERE N, *MB: CODE: CDN3 LOC: FRONT BY POST 54FT PL N VILLERE 7' OUTSIDE 1' IN- ****/ | 2018-09-13 | EXCAVATED IN MUD PLOT + REPLACED 1 INCH HANDWHEEL BACKFILLED + DRESSED UP AREA
201801528601 | 2018-08-24 | LEAD/PLASTIC | 1829 | VALENCE | BARONNE | WILK | MI- LEAK ON THE SIDEWALK INLET SERVICE LEAK IN THE MUD PLOT IN FRONT OF METER FLOODNIG MUD PLOT IN TREE ROOTS 10/02/18 PER S/R #12853398 TRUCK HAS BEEN MOVED (KSW) /** 1) MN: A255895 SN: 0006966, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT DRYADES LRPL, *MB: CODE: B3 LOC: 75' FROM RPL OF DRYADES ****/ DOTTIE READY 11-16-18 EXP 12-6-18 | 2018-11-17 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 5/8 HANDWHEEL LEAKING.REPLACED HANDWHEEL AND 3FT . OF 3/4 TUBING TIED INTO LEAD.
201801530201 | 2018-08-24 | LEAD/PLASTIC | 1009 | MARENGO | CAMP | WILK | ML-METER LEAK METER#A403681 ACCT#120834-565029 INLET SERVICE LEAK IN MUDPLOT NEAR SIDEWALK /** 1) MN: A270448 SN: 0037009, *TAP: SIZE: A LOC: 986 FEET FROM P LINE AT CAMP, *MB: CODE: CDM LOC: ON MARENGO,97.8' FROM S.P.L. CAMP ****/ | 2018-10-09 | ARRIVED AT ABOVE LOCATION ,EXAMINED EXCAVTED BY HAND AND MADE REPAIR TO STOP LEAK ON 5/8 INLET SERVICE LINE .BACKFILLED CLEANED UP AND WASHED DOWN JOBSITE TO COMPLETE JOB. "LEAD INLET"
201801530701 | 2018-08-24 | LEAD | 1918 | DAUPHINE | TOURO | WILK | ML - METER LEAK MTR# A277575 ACCT # 109459-485392 INLET SERVICE LEAK BAD BLEEDER VALVE /** 1) MN: A277575 SN: 0024331, *TAP: SIZE: B LOC: 140 FEET FROM P LINE AT PAUGER, *MB: CODE: CEMD LOC: ON DAUPHINE 142FT FROM PL PAUGER ****/ | 2018-09-17 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED CURB COCK BACKFILLED + DRESSED UP AREA. (NO METER)
201801537302 | 2018-08-26 | LEAD | 122 | N JEFFERSON DAVIS PK | IBERVILLE | WMTLK | NEED MACHINE, LEAK ON METER /** 1) MN: B031293 SN: 0011196, *TAP: SIZE: C LOC: 195 FEET FROM P LINE AT CANAL, *MB: CODE: CDM2 LOC: ON JEFF DAVIS 193FT FROM CANAL ****/ | 2018-10-07 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 3/4 INCH INLET SERVICEMADE REPAIRS ON INLET BACKFILED JOB WITH RIVERSAND
201801537802 | 2018-08-26 | LEAD/PLASTIC | 2210 | N BROAD |  | WMRE | NEED MACHINE TO RAISE METER TO GRADE. MI-RAISE METER TO GRADE /** 1) MN: A240496 SN: 0078390, *TAP: SIZE: C LOC: 175 FEET FROM P LINE AT LONDON AVE, *MB: CODE: CFLN LOC: ON NO. BROAD, 68' FROM L.S.P.L. HYDT IN CENTER OF ****/ /** 1) MN: A240496 SN: 0078390, *TAP: SIZE: C LOC: 175 FEET FROM P LINE AT LONDON AVE, *MB: CODE: CFLN LOC: ON NO. BROAD, 68' FROM L.S.P.L. HYDT IN CENTER OF ****/ | 2018-09-06 | EXCAVATED AROUND METER BOX EXPOSED INLET AND OUTLET LEAD FOUND ON INLET RAISED METER BOX TO GRADE. CLEANED DRESS AND BACKFILLED JOB.
201801538601 | 2018-08-26 | LEAD | 1551 | N MIRO | LAHARPE | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: B030722 SN: 0083256, *TAP: SIZE: C LOC: 49 FEET FROM P LINE AT MIRO N, *MB: CODE: DHM LOC: ON LAHARPE 49FT FROM MIRO N ****/ | 2018-09-14 | EXCAVATED IN MUD PLOT + REPLACED 3/4 INCH CURB COCK BACKFILED + DRESSED UP AREA
201801539001 | 2018-08-26 | LEAD | 1435 | N ROMAN | KERLEREC | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. ***LEAK ON KERLEREC.*** /** 1) MN: A253207 SN: 0049389, *TAP: SIZE: A LOC: 49 FEET FROM P LINE AT ROMAN N, *MB: CODE: BDHL LOC: ON KERLEREC 49' FROM USPL N ROMAN ST ****/ | 2018-09-14 | REPLACED BROKEN HANDWHEEL + GUTS IN METER BOX
201801539501 | 2018-08-26 | LEAD | 2186 | N DORGENOIS | ELYSIAN FIELDS AV | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A284529 SN: 0169139, *TAP: SIZE: B LOC: 4 FEET FROM P LINE AT ELYSIAN FIELDS AVE, *MB: CODE: OOOO LOC: ON N DORGENOIS BET ELYSIAN FIELDS & FRENCHMEN 4' F ****/ | 2018-09-17 | EXCAVATED 3 X 3 NUD PLOT REPLACE 5/8 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA REFERRED TO DAPHNY (METER SHOP) TO REMOVE METER (PET) NO ACCOUNT
201801543601 | 2018-08-27 | LEAD | 2325 | 6TH |  | WOLK | LOCATION: 181300 MTR# A 406487 PER INSP SB - INLET & OUTLET TO CLOSE, ALSO ROCKS IN BOX. PLEASE REPAIR AND CHANGE METER. DOTTIE READY 8-31-18 EXP 9-20-18 RENEW OUTLET SERVICE AND CHANGE METER /** 1) MN: A158918 SN: 0067969, *TAP: SIZE: C LOC: 169 FEET FROM P LINE AT LIBERTY S, *MB: CODE: CDL LOC: ON SIXTH 197FT FROM PL LIBERTY S 7' OUTSIDE PL 2' ****/ | 2018-09-08 | EXCAVTED JOB BY HAND IN SIDEWALK FOUND LEAK ON 5/8 CURB COCK MADE REPAIR ALSO LOCATED ANOTHER METER BOX THAT WAS BURIED BACKFILLED AND CLEANED AREA.(SOC 4FT .X 4 FT .CONCRETE.)
201801544501 | 2018-08-27 | LEAD | 1922 | ROBERT |  | WSNR | FOUND LEAD FROM INLET TO MAIN THAT NEEDS TO BE REPLACED. /** 1) MN: A301142 SN: 0066728, *TAP: SIZE: A LOC: 144 FEET FROM P LINE AT SARATOGA S, *MB: CODE: BD25 LOC: XXX - 144' P.L. S SARATOGA ****/ /** 1) MN: A301851 SN: 0066728, *TAP: SIZE: B LOC: 144 FEET FROM P LINE AT SARATOGA S, *MB: CODE: AD25 LOC: XXX XX - 142' P.L. S SARATOGA ****/ | 2018-08-23 | EXCAVATED 10 X 10 CUT IN STREET. REMOVED LEAD FROM INLET AND OUTLET REPLACED WITH PLASTIC. REPLACED TAP WITH 4 INCH CLAMP AND 1' TAP. SEE W/O 201801502402 CLEANED AND BACKFILL JOB SITE JOB COMPLETE
201801544801 | 2018-08-27 | LEAD | 2514 | PAINTERS |  | WILK | LOCATION: 160571 MTR# 418242 PER INSP UDEBOR - LEAK COMING FROM BLEEDER VALVE. PLEASE REPAIR INLET SERVICE LEAK BAD BLEEDER VALVE /** 1) MN: A128289 SN: 0099012, *TAP: SIZE: A LOC: 102 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: ADLN LOC: ON PAINTERS, 103.5' FROM P.L. NO. DORGENOIS, 7'OUT ****/ | 2018-09-19 | EXCAVATED 3 X 2 MUD PLOT REPLACED BROKEN METER BOTTOM AND 5/8 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801545101 | 2018-08-27 | LEAD | 7922 | LEHIGH | HAYNE BL | WILK | ML-METER LEAK ACCT#183174-465506 METER#A407568 INLET SERVICE LEAK IN SIDEWALK /** 1) MN: A249603 SN: 0137451, *TAP: SIZE: B LOC: 209 FEET FROM P LINE AT WALES, *MB: CODE: BE LOC: 209FT FROM PL WALES 7' OUTSIDE PL 2' INSIDE CURB ****/ | 2018-09-17 | EXAMINE AND FOUND INLET SERVICE LEAKING MADE REPAIRS ALSO NEED TO REMOVE LEADER BACKFILL
201801548601 | 2018-08-27 | LEAD | 4947 | DODT AV | DWYER RD | WILK | PP-POOR PRESSURE METER #A292241 ACCT # 171092-445338 **********1ST AM********** INLET SERVICE UNDERGROUND LEAK IN CONCRETE BASE STREET CAUSING POOR PRESSURE ***CUSTOMER BARELY ABLE TO FUNCTION /** 1) MN: A292241 SN: 0140451, *TAP: SIZE: A LOC: 4 FEET FROM P LINE AT HYDT #11, *MB: CODE: OOO LOC: 2' FROM HYDT #11 7' OUTSIDE ****/ | 2018-09-24 | MADE A 23X6 CUT IN CONCRETE BASE STREET. EXCAVATED DOWN ON INLET AND OUTLET SERVICES ALSO AT WATER MAINL MADE SEVERAL ATTEMPTS TO FIND TAP BUT WAS NOT SUCCESSFULL. NEED TO COME BACK AND MAKE REPAIRS. (JOB CONTINUED)
201801549401 | 2018-08-27 | LEAD | 1924 | ST CLAUDE AV | PAUGER | WILK | ML -METER LEAK MN:A422653 ACCT#144521-424427 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A317604 SN: 0075958, *TAP: SIZE: C LOC: 190 FEET FROM P LINE AT PAUGER, *MB: CODE: BE LOC: METER ON ST CLAUDE AVE 190 FT FROM PL PAUGER ****/ | 2018-09-12 | EXAMINED AND FOUND 5/8 INCH WHEEL LOOSE MADE REPAIR OUTLET ALREADY PLASTIC
201801551303 | 2018-12-28 | LEAD/PLASTIC | 721 | RICHARD | CHIPPEWA | WMTLK | ML METER LEAK METER # E006605 ACCT# 187839-537565 NEED MACHINE EXAMINE INLET/OUTLET SERVICE FOR LEAK ON LARGE CAPACITY METER /** 1) MN: E006605 SN: 0144254, *TAP: SIZE: E LOC: 132 FEET FROM P LINE AT RICHARD, *MB: CODE: ADH7 LOC: IN MH ON CHIPPEWA 128FT PL RICHARD 3' OUTSIDE 3' ** 2) MN: E006113 SN: 0144254, *TAP: SIZE: E LOC: 158 FEET FROM P LINE AT ST THOMAS, *MB: CODE: CEH5 LOC: IN MH ON ORANGE 158FT PL ST THOMAS 3' OUTSIDE ****/ | 2018-12-28 | EXAMINED AREA PUMPED DOWN WATER CONTINUED TO BREAK OUT MANHOLE AND EXCAVATED BACK ON INLET AND OUTLET SERVICE CUT ON 2" PLASTIC AND PLACED 2" STOP COCK RENEWED METER AND OUTLET SERVICE UNABLE TO CLEAN UP ROCKS AND MUD BACRRICADED OFF DUE TO TIME WEATHER CASUSE SOME DELAY OLD METER INFO: E006605 FACT: 46238453 MAKE: SENSUS READ: 21427
201801551401 | 2018-08-27 | LEAD | 1022 | AMELIA | MAGAZINE | WILK | ML- METER LEAK MN:A425434 ACCT#123291-712731 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A128955 SN: 0042631, *TAP: SIZE: A LOC: 152 FEET FROM P LINE AT MAGAZINE, *MB: CODE: CDMN LOC: CURB 153' P.L. MAGAZINE ****/ | 2018-10-26 | REPLACED 5/8 CURB COCK TIED INTO LEAD.(SOC 3 FT. X 3 FT .MUD-PLOT)
201801555701 | 2018-08-28 | LEAD | 1426 | N PRIEUR | KERLEREC | WOLK | ML- METER LEAK MTR# A115073 ACCT# 110507-487505 EXAMINE OUTLET SERVICE FOR A LEAK WITH CONSTANT REGISTRATION /** 1) MN: A115073 SN: 0015211, *TAP: SIZE: A LOC: 109 FEET FROM P LINE AT KERLEREC, *MB: CODE: BDM LOC: ON N PRIEUR 108.5' FROM URPL KERLEREC ****/ | 2018-10-01 | EXCV FOUND LEAD ON INLET AND OUTLET REPLACED WHEEL AND WASHERS.
201801556501 | 2018-08-28 | LEAD | 2629 | URSULINES AV | N DORGENOIS | WMTLK | ML METER LEAK ACCT# 111136-449666 METER# A401092 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** 1) MN: SN: 0013590, *TAP: SIZE: B LOC: 227 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CFL LOC: IN GARDEN 227' P.L. N DORGENOIS ****/ | 2018-09-14 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201801556801 | 2018-08-28 | LEAD | 2916 | PARIS AV |  | WILK | M FRAZIER SAYS HE IS UNABLE TO CHANGE METER. CURB COCK IS IN OFF POSITION BUT ON. PLEASE REPAIR AND CHANGE METER C021438 LOC ID 132817 INLET SERVICE LEAK BAD CURB COCK UNABLE TO CLOSE OFF /** 1) MN: C021438 SN: 0063788, *TAP: SIZE: D LOC: 177 FEET FROM P LINE AT ABUNDANCE, *MB: CODE: AEM2 LOC: 176FT FROM PL ABUNDANCE ****/ | 2018-09-24 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 1 INCH CURB COCK ALSO REPLACED 1 INCH METER BACKFILLED UP AREA ***************OLD METER INFO********** METER:C021438 FAC:39529351 MAKE:ROCKWELL READ:3951
201801557801 | 2018-08-28 | LEAD/PLASTIC | 2929 | PINE | FIG | WILK | ML- METER LEAK METER#A47505 ACCT#303972-716575 INLET SERVICE LEAK /** 1) MN: A257589 SN: 0071661, *TAP: SIZE: B LOC: 245 FEET FROM P LINE AT PRITCHARD PL, *MB: CODE: AD LOC: ON PINE, 244' FROM P.L. PRITCHARD PL. ****/ DOTTIE READY 9-19-18 EXP 10-9-18 | 2018-09-25 | ARRIVED AT ABOVE LOCATION ,EXAMINED EXCAVTED BY HAND AND MADE REPAIR ON 5/8 INLET SERVICE LINE .BACKFILLED CLEANED UP AND WASHED DOWN AREA TO COMPLETE JOB. "LEAD INLET"
201801560701 | 2018-08-29 | LEAD | 1007 | ST MAURICE AV |  | WMRE | LOCATION: 123370 MTR# A 404007 PER INSP LU - DEBRIS, ROCKS AND SAND OVER METER BOX. PLEASE LOCATE AND CHANGE METER LOCATE & CHANGE METER /** 1) MN: A315124 SN: 0065323, *TAP: SIZE: B LOC: 115 FEET FROM P LINE AT RAMPART N, *MB: CODE: CDL1 LOC: ON ST MAURICE AVE.,74' FROM L.S.P.L. NO. RAMPART ****/ | 2018-09-21 | EXAMINED + FOUND METER BOX IN DRIVEWAY REPLACED 5/8 INCH WASHERS AND STILL WORK
201801561201 | 2018-08-29 | LEAD | 5715 | DEBORE DR | PRENTISS AV | HGRD | LEAK IN SIDEWALK *****************1ST AM******************** EXAMINE DEPRESION IN GROUND BETWEEN CURB AND STREET BY METER BOX, 3 BARRELS NEEDED /** 1) MN: A338764 SN: 0120557, *TAP: SIZE: B LOC: 295 FEET FROM P LINE AT PRENTISS AVE, *MB: CODE: CDLM LOC: 295FT PRENTISS AV 9' OUTSIDE 4' INSIDE CURB ****/ | 2018-09-20 | EXCAVATED IN 15X8 STREET CUT FINDING LEAK ON LEAD. FIXED LEAK AT SPOT AND RAN PLASTIC TUBING TO METER BOX. CHANGED LEAD ON OUTLET AS WELL. JOB WILL BE CONTINED ON 9-21-18 MATERIAL NEEDED JOB BARRELED OFF.
201801561701 | 2018-08-29 | LEAD | 1832-30 | ST ROCH AV | N ROMAN | WMTLK | WM-- LEAK IN STREET EXAMINE INLET & OUTLET SERVICE FOR A LEAK INSIDE METER BOX /** AT 1830: 1) MN: A254064 SN: 0058429, *TAP: SIZE: C LOC: 92 FEET FROM P LINE AT PRIEUR N, *MB: CODE: BDN4 LOC: LPL FRONT 66' P.L. N PRIEUR ****/ | 2018-09-18 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801562401 | 2018-08-29 | LEAD | 1720 | MARIGNY | ELYSIAN FIELDS AV | WILK | WM-LEAK IN STREET CHANGED FROM 1700BLK MARIGY INLET SERVICE LEAK ON ABANDON SERVICE NO METER IN BOX ***HOUSE UNDER RENOVATIONS*** /** 1) MN: A211553 SN: 0057967, *TAP: SIZE: A LOC: 132 FEET FROM P LINE AT ROMAN N, *MB: CODE: BDLM LOC: SW GUTTER ON MARIGNY 132' FROM URPL N ROMAN ****/ | 2018-09-18 | EXCAVATED IN CONDRETE SIDEWALK & REPLACED 5/8 INCH CURB COCR. BACKFILLED & DRESSED UP AREA
201801564801 | 2018-08-29 | LEAD | 632 | CHARTRES |  | WOLK | *********PICKUP JOB********* OUITLET SERVICE LEAK /** 1) MN: A288495 SN: 0155462, *TAP: SIZE: C LOC: 88 FEET FROM P LINE AT ST. PETERS, *MB: CODE: CD LOC: ON CHARTRES, 60' FROM P.L. ST. PETERS, 3' OUTSIDE ** 2) MN: A288424 SN: 0155462, *TAP: SIZE: C LOC: 88 FEET FROM P LINE AT ST. PETERS, *MB: CODE: CD LOC: ON CHARTRES, 57' FROM P.L. ST. PETERS, 4' OUTSIDE THERE IS 1 MORE NOT LISTED. ****/ | 2018-09-17 | EXCAVATED IN FLAGSTONE SIDEWALK + MADE REPAIR ON 1 INCH INLET SERVICE LINE UNDER DUCT + OTHER METER BOX BACKFILLED + DRESSED UP AREA. JOB COMPLETE
201801564901 | 2018-08-29 | LEAD/PLASTIC | 5101 | PITT | SONIAT | WMTLK | WM-LEAK IN SIDEWALK EXAMINE INLET/OUTLET SERVICE FOR LEAK 08/31/018 BAD UNDER GROUND LEAK CAUSING LARGE DEPRESSION BETWEEN SIDEWALK AND METER PER INSPC L GOMEZ, GIVE OUT ***M.ROBINSON @ 9:28AM*** (AJR) /** 1) MN: A118545 SN: 0005342, *TAP: SIZE: B LOC: 64 FEET FROM P LINE AT PITT, *MB: CODE: BFHK LOC: ON SONIAT 64FT FROM LSPL OF PITT ****/ | 2018-08-31 | EXCVATED IN SIDEWALK OVER 3/4 INLET SERVICE.REMOVE LEAD FROM METER BOX TO THE CURB,NEED TO RETURN AND REMOVE LEAD FROM WATER MAIN TO TO THE CURB .WATER MAIN IS ON THE SHORT SIDE.DOTTIE IS MARKED ALREADY. (SOC 3 FT. X 5FT. S/W CONCRETE)
201801567501 | 2018-08-30 | LEAD | 1721 | JOSEPH | RAMPART | WILK | MI: METER LEAK ACCT#150230-711219 METER # A415908 CUSTOMER STATES LEAK IS GETTING WORSE **** C9-17-18/R 9-20-18/EXP. 10-10-18 **** INLET SERVICE LEAK BEHND CURB COCK FLOODING GRASSY AREA /** 1) MN: A286697 SN: 0030659, *TAP: SIZE: A LOC: 176 FEET FROM P LINE AT RAMPART S, *MB: CODE: CD LOC: ON JOSEPH 175FT FROM RAMPART S ****/ | 2018-09-19 | ARRIVED AT ABOVE LOCATION, EXAMINED, FOUND LEAK ON 5/8 SERVICE INLET, EXCEVATED BY HAND AND MADE REPAIRS TO STOP LEAK. BACKFILLED CLEANED UP AND WASHED DOWN JOB SITE TO COMPLETE JOB. LEAD INLET
201801572604 | 2018-09-07 | LEAD/PLASTIC | 3106 | LAWRENCE ST | TITA | WMTLK | ARRIVED AT JOB SITE CUSTOMER REFUSED TO REMOVE VEHICLE FROM WORK AREA /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-09-19 | EXAMINED AREA PUMPED DOWN WATER EXCAVATED ON INLET AND OUTLET SERVICE OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK BACKFILLED AND CLEANED AREA AND DRESSED CUT
201801589002 | 2018-09-03 | LEAD | 7118 | E HERMES | PANDORA | WMTBG | NEED MACHINE TO RAISE TO GRADE ACCT#131006044 METER#C025291 METER CASING BELOW GRADE /** 1) MN: C018973 SN: 0122569, *TAP: SIZE: C LOC: 292 FEET FROM P LINE AT PANDORA, *MB: CODE: ADL6 LOC: ON E.HERMES 292FT PANDORA 8FT OUTSIDE ****/ /** 1) MN: C018973 SN: 0122569, *TAP: SIZE: C LOC: 292 FEET FROM P LINE AT PANDORA, *MB: CODE: ADL6 LOC: ON E.HERMES 292FT PANDORA 8FT OUTSIDE ****/ | 2018-09-14 | EXCAVATED BY HAND DUE TO GAS LINE AROUND METER BOX 3 1/2 FEET DEEP RAISED METER TO GRADE.
201801595301 | 2018-09-05 | LEAD | 931 | GOV NICHOLLS | BURGUNDY | WMTLK | ML-METER LEAK ACCT#183231-529641 METER#C007570 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER OVERFLOWING FLOODING CURB /** 1) MN: C007570 SN: 0052042, *TAP: SIZE: C LOC: 226 FEET FROM P LINE AT DAUPHINE, *MB: CODE: BE LOC: 226FT. PL DAUPHINE 5' OUTSIDE ****/ | 2018-09-21 | REPLACED 1 INCH WASHERS IN METER BOX ALSO REPLACED DAMAGED 1 INCH METER *************OLD METER INFO********* METER:C007570 FAC:000077227 MAKE:ROCKWELL READ:6173
201801598301 | 2018-09-05 | LEAD | 1472 | N BROAD |  | WILK | M FRAZIER STATES SERVICE HAS A BLEEDER VALVE LEAK. HAD TO LEAVE WATER OFF. PLEASE REPAIR METER A417644 LOC ID 305825 INLET SERVICE LEAK BAD BLEEDER VALVE /** 1) MN: A276299 SN: 0042255, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT BAYOU RD, *MB: CODE: BEKO LOC: 76FT FROM LRPL BAYOU RD ****/ | 2018-09-27 | MADE 4 X6 CUT IN SIDEWALK IN STORM RAIN AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201801598801 | 2018-09-05 | LEAD | 3338 | BELL |  | WILK | LOCATIONID#126831-717748 METER#A304853 LEAK INSIDE METERBOX INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A304853 SN: 0051283, *TAP: SIZE: A LOC: 154 FEET FROM P LINE AT MOSS, *MB: CODE: CD LOC: 152' P.L. MOSS ****/ | 2018-09-27 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 INCH INLET SERVICE IN STORM RAIN BACKFILLED AREA
201801599101 | 2018-09-05 | LEAD | 3914 | MARAIS | ALVAR | WILK | ML-METER LEAK***ACCT#152172-430438***METER#A414054 INLET SERVICE LEAK IN MUDPLOT FROM BLEEDER VALVE /** 1) MN: A296538 SN: 0114138, *TAP: SIZE: A LOC: 93 FEET FROM P LINE AT ALVAR, *MB: CODE: BDL1 LOC: ON MARAIS, 92.5' FROM P.L. ALVAR ****/ | 2018-10-03 | EXCAVATED IN MUD PLOT REPLACED 5/8 INCHJ CURB COCK BACKFILLED AREA JOB COMPLETED
201801606401 | 2018-09-06 | LEAD | 3204 | BOYD | IVORY | WILK | WM-LEAK BETWEEN SIDEWALK AND STREET EXMAINE INLET SERVICE FOR LEAK BETWEEN CURB AND STREET /** 1) MN: A121699 SN: 0148137, *TAP: SIZE: B LOC: 25 FEET FROM P LINE AT IVORY, *MB: CODE: AE LOC: ON BOYD 25' FROM PL IVORY 3' OUTSIDE PL IVORY ****/ | 2018-11-03 | EXAMINED AREA CLEANED OUT METER BOX EXAMINE INELT + OUTLT SERVICE NO LEAK OBSERVED
201801608701 | 2018-09-06 | LEAD | 4999 | BURGUNDY | REYNES | WILK | ML- METER LEAK ACCT# 303554-573524 METER# A409021 INLET SERVICE LEAK IN MUDPLOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-09-21 | EXCAVATED 3 X 3 MUD PLOT FOUND ABANDON METER BOX LEAKING REPLACED 5/8 INCH METER COCK AND CASING MARKED WITH BLUE PAINT BACKFILLED AND CLEANED THE AREA. JOB COMPLETE
201801613601 | 2018-09-07 | LEAD | 2339 | N MIRO | SPAIN | WILK | ML- METER LEAK ACCT#130095-483922 METER#A430145 CUSTOMER STATES, THERE IS NO CAR PARKED OVER THE METER 09/18 (CG) CUSTOMER INQUIRED ABOUT W/O INLET SERVICE LEAK /** 1) MN: A136971 SN: 0070540, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT MIRO N, *MB: CODE: CD LOC: ON SPAIN,100' FROM P.L. NO. MIRO ****/ | 2018-09-28 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801614601 | 2018-09-08 | LEAD | 1207-09 | ALVAR | MARAIS | WILK | ML-METER LEAK ACCT#111079-488014 METER#A364044 INLET SERVICE LEAK /** AT 1207: 1) MN: A136342 SN: 0059134, *TAP: SIZE: A LOC: 78 FEET FROM P LINE AT MARAIS, *MB: CODE: CDM1 LOC: ON ALVAR 78FT FROM MARAIS ****/ | 2018-10-03 | EXCAVATED IN MUD PLOT REPLACED 5/8 INCH CURB COCK BACKFILLED AREA JOB COMPLETE
201801619101 | 2018-09-10 | LEAD | 4824 | GALLIER DR | STEPHEN GIRARD AV | WILK | ML-METER LEAK ACCT#170484-469253 METER#A417739 EXAMINE INLET SERVICE FOR LEAK IN MUDPLOT /** 1) MN: A115456 SN: 0113009, *TAP: SIZE: A LOC: 341 FEET FROM P LINE AT MIRABEAU AVE, *MB: CODE: ADM5 LOC: MTR ON GALLIER DR 341FT FRM PL MIRABEAU 7FT OUTSD ****/ | 2018-10-08 | EXCAVATED IN MUDPLOT BY HAND TO REPAIR LEAK ON 5/8 LEAD LINE ON INLET SERVICE. ALSO REMOVED LEAD FROM OUTLET, RAISED METER BOX TO GRADE AND REPLACED COMPLETE 5/8 SETUP. BACKFILLED 3X3 MUD PLOT CUT. (D.N.R LEAD ON INLET NEED MACHINE.)
201801621501 | 2018-09-10 | LEAD | 2526 | CONGRESS | LAW | WILK | ML-METER LEAK METER#404485 ACCT#164951-434194 INLET SERVICE LEA K /** 1) MN: A136424 SN: 0104924, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT LAW, *MB: CODE: BDK1 LOC: ON CONGRESS, 95' FROMP.L. LAW, 7' OUTSIDE P.L. ****/ | 2018-09-21 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK +BROKEN 5/8INCH HANDWHEEL IN METER BOX BACKFILLED + DRESSED UP AREA
201801621601 | 2018-09-10 | LEAD | 3704 | N CLAIBORNE AV | INDEPENDENCE | WMTLK | ML: METER LEAK, MTR # A399724, ACCOUNT # 163653-430495 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A214161 SN: 0103173, *TAP: SIZE: B LOC: 48 FEET FROM P LINE AT INDEPENDENCE, *MB: CODE: ADKO LOC: 33'FROM P L INDEPENDENCE 8'FROM CLAIBORNE FRONT ****/ | 2018-09-21 | ARRIVED AT ABOVE LOCATION + FOUND COCK + WHEEL NOT LINEING UP REPLACED BROKEN 5/8 INCH HAND WHEEL THAT WAS CAUSING LEAK
201801623001 | 2018-09-10 | LEAD/PLASTIC | 1728 | WAGNER |  | WMTBG | LOCATION ID-227140 MTR-A374765 MTR BELOW GRADE AND MTR GLASS SCRATCH/PLEASE CHANGE MTR AND RAISE MTR TO GRADE ADJUST METER BOX TO PROPER GRADE/CHANGE METER /** 1) MN: A294344 SN: 0108542, *TAP: SIZE: A LOC: 717 FEET FROM P LINE AT BRINGIER, *MB: CODE: AFLM LOC: ON WAGNER 721' FROM PL BRINGIER 7' OUTSIDE PL 7' I ****/ | 2018-09-25 | RAISED BOX TO GRADE LEAD ON INLET NEED TO BE REMOVED BACKFILLED WITH SAND AND COLDMILL
201801624301 | 2018-09-11 | LEAD | 1411 | BENSON | N VILLERE | WILK | INET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-09-21 | EXCAVATED 5 X 12 MUD PLOT AND 3 X 3 DRIVEWAY TO LOCATE METER EXAMINED JOB + FOUND NO LEAK BACKFILLED AND CLEANED THE AREA
201801624601 | 2018-09-11 | LEAD | 2701 | DREUX AV |  | WMRE | LOCATION: 305797 PER INSP M FRAZIER - METER BOX BURIED. PLEASE LOCATE AND SET A 5/8 METER. LOCATE, RAISE TO GRADE AND SET 5/8 METER, NEW CONSTRUCTION 10/05/18 OWNER STATED REPAIRS ARE MADE .NEED METER SET SO THAT HE CAN HAVE TENANT TO MOVE IN. (KSW) /** 1) MN: A287444 SN: 0085873, *TAP: SIZE: A LOC: 24 FEET FROM P LINE AT LAFAYE, *MB: CODE: BFN LOC: ON DREUX AVE 24FT FROM PL OF LAFAYE ****/ | 2018-10-08 | EXCAVATED BY HAND LOCATD METER RAISE AND RENEWED 5/8 METER BOX COMPLETE UP TO GRADE ALSO RENEWED OUTLET SERVICE AND SET 5/8 METER.
201801625901 | 2018-09-11 | LEAD | 818 | THAYER |  | WILK | ML-- METER LEAK METER # A353146 ACCT # 231924-403972 INLET SERVICE LEAK IN THE MUD PLOT FLOODING SIDEWALK ***SPOKE WITH CUSTOMER*** /** 1) MN: A238144 SN: 0144040, *TAP: SIZE: B LOC: 179 FEET FROM P LINE AT SLIDELL, *MB: CODE: BD LOC: RES ON THAYER 179' FROM PL SLIDELL 7' OUTSIDE PL 3 ****/ | 2018-11-04 | ARRIVED ON JOB SITE EXAMINE LEAK IN MUD PLOT EXCAVATED BY HAND MADE REPAIRS ON INLET SERVICE BACKFILLED DRESSE UP WORK SITE
201801632001 | 2018-09-12 | LEAD/PLASTIC | 5524-26 | S GALVEZ | OCTAVIA | WILK | ML- METER LEAK ACCT# 152699-574720 METER# A413439 *************L.THOMPSON @ 12:52PM*************** INLET SERVICE LEAK IN GRASS, FLOODING AREA /** AT 5524: 1) MN: A228277 SN: 0088498, *TAP: SIZE: B LOC: 196 FEET FROM P LINE AT OCTAVIA, *MB: CODE: CE LOC: ON S GALVEZ 195' FROM PL OCTAVIA 8' OUTSIDE PL 2' ** AT 5526: 2) MN: A244684 SN: 0088498, *TAP: SIZE: A LOC: 196 FEET FROM P LINE AT OCTAVIA, *MB: CODE: CE LOC: ON S GALVEZ 195' FROM PL OCTAVIA 8' OUTSIDE PL 2' ****/ DOTTIE READY 9-19-18 EXP 10-9-18 | 2018-09-22 | EXCAVTED IN GUTRER BOTTOM OVER INLET SERVICE.MADE REPAIR AND TIED SERVICE BACK INTO LEAD.
201801632701 | 2018-09-12 | LEAD | 2404 | A P TUREAUD AV | DELERY | WILK | ML- METER LEAK ACCT# 139470-498478 METER# A 398712 EXAMINE INLET SERVICE FOR A LEAK NEAR CATCH BASIN /** 1) MN: A341834 SN: 0070578, *TAP: SIZE: B LOC: 133 FEET FROM P LINE AT DELERY, *MB: CODE: CD LOC: ON A P TUREAUD 133FT FROM DELERY ****/ | 2018-10-01 | EXCAVATED 3 X 3 MUD PLOT MADE REPAIR ON INELT SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801633801 | 2018-09-12 | LEAD | 1812 | COLUMBUS | N ROMAN | WILK | ML- METER LEAK METER# A429853 ACCT# 219449-593038 INLET SEVICE LEAK BEHIND CURB COCK FLOODING SIDEWALK & GUTTER BOTTOM /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-09-20 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801636201 | 2018-09-13 | LEAD | 7119 | PANOLA |  | WMTLK | LOCATIONID#135867-579898 METER#A303173 METERBOX OVERFLOWING /** 1) MN: A303173 SN: 0066410, *TAP: SIZE: B LOC: 139 FEET FROM P LINE AT AUDUBON, *MB: CODE: ADL LOC: ON PANOLA, 139' FROM P.L. AUDUBON ****/ DOTTIE READY 9-19-18 EXP 10-9-18 | 2018-09-22 | REPLACED 5/8 INCH CURB COCK TIED INTO LEAD
201801641501 | 2018-09-13 | LEAD | 3232 | JEFFERSON AV | S GALVEZ | WOLK | MI - LEAK ON SIDE WALK OUTLET SERVICE LEAK IN SIDEWALK NEAR GRASS FLOODING SIDEWALK /** 1) MN: 000000 SN: 0089175, *TAP: SIZE: A LOC: 33 FEET FROM P LINE AT JEFFERSON AVE, *MB: CODE: BDH LOC: SIDE ST 2ND METER - 34' P.L. JEFFERSON AVE ****/ | 2018-09-13 | LEAK ON 1' LEAD LINE WE REPAAIRED LINE AND FIX LEAK REFERRE BACK TO ZONE 3TO REMOVE LEAD
201801643901 | 2018-09-13 | LEAD | 2126 | MARIGNY |  | WMTLK | LOCATION ID-301537 MTR-A426148 CASING SHIFTED OVER CURB COCK(PENDING DELINQUENT TURN OFF) EXAMINE INLET AND OUTLET SERVICE FOR A LEAK METER BOX SHIFTED FLOODING AREA /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-10-08 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801644201 | 2018-09-13 | LEAD/PLASTIC | 43 | WARBLER | MARCONI DR | WMRE | MI CLOSE FOR REPAIRS BROKEN OUTSIDE ACCT# 163238-513169 METER# A399899 **********1ST AM********* LOCATE RAISE AND MARK METER, CLOSE SERVICE PIPE BROKEN OUTSIDE /** 1) MN: A122658 SN: 0102498, *TAP: SIZE: A LOC: 1042 FEET FROM P LINE AT MARCONI DR, *MB: CODE: AFT4 LOC: ON BREEZE PARK, 1042' FROM P.L. MARCONI DR.,8' OUT ****/ | 2018-09-14 | LOCATED AND EXCAVATED A 2 X 3 MUD CUT AND RAISE THE METER TO GRADE. PLASTIC ON OUTLET SERVICE AND LEAD ON INLET SERVICE. BACKFILL & CLEAN UP
201801647801 | 2018-09-14 | LEAD | 4003 | STATE STREET DR | FONTAINEBLEAU DR | WILK | ML: METER LEAK, MTR # A374224, ACCOUNT # 150240-722584 INLET SERVICE LEAK BEHIND CURB COCK, FLOODING GRASS AND GUTTER /** 1) MN: A312152 SN: 0083012, *TAP: SIZE: B LOC: 296 FEET FROM P LINE AT FONTAINBLEAU DR, *MB: CODE: ADK2 LOC: ON STATE STREET 298FT FROM FONTAINBLEAU ****/ | 2018-10-31 | EXCAVTED IN MUDPLOT OVER INLET SERVICE .CHANGED METER BOX COCK.
201801651201 | 2018-09-15 | LEAD | 1120 | JENA | CHESTNUT | WILK | ML-METER LEAK ACCT#115045-561103 METER#A278795 INLET SERVICE LEAK IN BOX /** 1) MN: A278795 SN: 0023489, *TAP: SIZE: A LOC: 104 FEET FROM P LINE AT COLISEUM, *MB: CODE: AFN LOC: METER ON JENA 103.5 FT FROM PL COLISEUM ****/ | 2018-10-26 | REPLACED 5/8 CURB COCK TIED INTO LEAD.(SOC 3 FT X 3 FT . MUD-PLOT)
201801658701 | 2018-09-17 | LEAD | 1146 | CONSTANTINOPLE | COLISEUM | WMTLK | ML- METER LEAK METER#A427885 ACCT#190741-557014 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: A181059 SN: 0023254, *TAP: SIZE: B LOC: 49 FEET FROM P LINE AT COLISEUM, *MB: CODE: AFKM LOC: 48FT FROM PL COLISEUM 3' OUTSIDE PL 7' INSIDE CURB ****/ | 2018-09-29 | REPLACED 5/8 CURB COCK TIED INTO LEAD.(SOC4FT X 4 FT D/W)
201801663001 | 2018-09-18 | LEAD | 816 | ORLEANS AV |  | WMTLK | LOCATIONID#147140-528036 METER#A268255 LEAK INSIDE METERBOX EXAMINE INLET AND OUTET SERVICE FOR LEAK /** 1) MN: A268255 SN: 0022210, *TAP: SIZE: A LOC: 129 FEET FROM P LINE AT BOURBON, *MB: CODE: AEN1 LOC: ON ORLEANS 129' FROM P LINE BOURBON ****/ | 2018-10-07 | REPLACED 5/8 INCH WASHERS TO STOP LEAK
201801663101 | 2018-09-18 | LEAD | 930 | ORLEANS AV |  | WMTLK | LOCATIONID#114251-527992 METER#A319250 LEAK INSIDE METERBOX EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A319250 SN: 0016893, *TAP: SIZE: A LOC: 88 FEET FROM P LINE AT BURGUNDY, *MB: CODE: AFN1 LOC: ON ORLEANS 88FT FROM BURGUNDY ****/ | 2018-10-05 | REPLACE 5/8 INCH METER WITH WASHER TO STOP LEAK *******************OLD METER INFO************** METER:A319250 FAC:53300194 MAKE:SENSUS READ:1448
201801663601 | 2018-09-18 | LEAD | 2634 | MEXICO |  | WILK | LOCATIONID#159098-473330 METER#A382573 METERBOX OVERFLOWING INLET SERVICE LEAK IN THE MUD PLOT ON EADS /** 1) MN: A300078 SN: 0097402, *TAP: SIZE: A LOC: 43 FEET FROM P LINE AT MEXICO, *MB: CODE: ADHK LOC: ON EADS 43FT FROM PL MEXICO ****/ | 2018-09-18 | MADE ALL REPAIRS ON INLET LEAK ALSO REFERRE TO ZONE 5 TO RMOVE LEAD
201801663901 | 2018-09-18 | LEAD | 3307 | PIEDMONT DR |  | WILK | LOCATIONID#155390-711222 METER#A422294 LEAK INSIDE METERBOX INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A252713 SN: 0092100, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT BAY, *MB: CODE: ADMK LOC: ON PIEDMONT DR.,53.5'FROM P.L. BAY,7.5' OUTSIDE ****/ | 2018-09-18 | MADE ALL REPAIR ON INLET LEAK ALSO REFERRE TO ZONE 5 RMOVE LEAD
201801665501 | 2018-09-18 | LEAD | 3333 | 2ND |  | WILK | MI LEAK IN THE STREET INLET SERVICE LEAK BEHIND CURB COCK FLOODING SIDEWALK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-18 | REPLACED 5/8 CURB COCK TIED INTO LEAD.
201801666101 | 2018-09-18 | LEAD | 1111 | LEONTINE |  | WILK | ML METER LEAK ACCOUNT #106331-559428 METER #A424767 CHANGED FROM 1109 LEONTINE INLET SERVICE LEAK BAD BLEEDER VALVE FLOODING SIDEWALK /** 1) MN: A320877 SN: 0032725, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT CHESTNUT, *MB: CODE: CF LOC: INSIDE ON LEONTINE 76FT FROM PL OF CHESTNUT ****/ | 2018-10-31 | REPLACED 5/8 CURB COCK TIED INTO LEAD
201801666801 | 2018-09-18 | LEAD/PLASTIC | 1448 | AVIATORS | DUPLESSIS | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK IN THE MUD PLOT ON ABANDON SERVICE ON VACANT LOT NEXT 2 ADDRESS. FLOODING SIDEWALK /** 1) MN: A133895 SN: 0130832, *TAP: SIZE: __ LOC: 7 FEET FROM P LINE AT DUPLESSIS, *MB: CODE: AD LOC: 7FT EXT PL DUPLESSIS ON AVIATORS 8' OUTSIDE ****/ | 2018-09-20 | EXCAVATED IN MUDPLOT THROUGH TREEROOTS TOO REPAIS. A 5/8 INLET SERVICE LEAK ADJUST METERBOX UP TO GRADE AND REPLACE 10FT OF 3/4 PVC PIPE FROM METBOX TO PROPERTY BACKFILLED AND DRESSUP WITH RIVERSAND PLASTIC INLET LEAD OUTLET
201801671701 | 2018-09-19 | LEAD | 1031 | ORLEANS AV | N RAMPART | WILK | LOCATIONID#106169-703376 METER#A430070 INLET CONNECTION LEAK /** 1) MN: A331973 SN: 0032200, *TAP: SIZE: A LOC: 97 FEET FROM P LINE AT RAMPART N, *MB: CODE: BEK1 LOC: 97' P.L. N RAMPART ****/ | 2018-10-05 | REMOVE DEBRIS OF METER BOX ALIGN METER IN METER BOTTOM AND REPLACED 5/8 WASHERS
201801672801 | 2018-09-19 | LEAD | 3114 | IBERVILLE | N SALCEDO | WILK | WM-LEAK IN SIDEWALK INLET ON ABANDON SERVICE INTERFERING WITH CONTRACTORS WORK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-10-04 | EXCAVATED IN MUD PLOT + MADE REPAIR ON ABANDONED 1 INCH INLET SERVICE LINE NO METER BOX NO METER BACKFILLED + DRESSED UP AREA (NO METER) (JOB COMPLETE)
201801673701 | 2018-09-19 | LEAD | 2308 | DRYADES | PHILIP | WILK | LEAK BETWEEN SIDEWALK & STREET CHANGED FROM 2312 DRYADES INLET SERVICE LEAK IN THE MUD PLOT IN FRONT AN ABANDON LOT FLOODING CURB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-09-29 | EXCAVTED IN MUDPLOT OVER ABANDON SERVICE MADE REPAIR IN MUDPLOT ON 1"SERVICE.
201801674101 | 2018-09-19 | LEAD | 4631 | CLARA | CADIZ | WILK | WM-LEAK ON THE SIDEWA;K INLET SERVICE LEAK IN MUDPLOT FLOODING CURB LEAK IS ON CLARA /** 1) MN: A258272 SN: 0065603, *TAP: SIZE: A LOC: 183 FEET FROM P LINE AT CADIZ, *MB: CODE: ADL LOC: 183' P.L. CADIZ ****/ | 2018-10-30 | LEAK WAS AT 4619 CLARA INSIDE THE METER BOX.BAD CURB COCK INSIDE THE BOX.NO METER IN BOX.(SOC 3FT. X 5 FT .S/W)
201801676601 | 2018-09-19 | LEAD | 2319 | LAFRENIERE |  | WMRE | INSP M FRAZIER SAYS SERVICE IS BURIED. PLEASE RAISE TO GRADE AND CHANGE METER A259457 LOC ID 159535 LOCATE/RAISE/CHANGE METER /** 1) MN: A259457 SN: 0097286, *TAP: SIZE: A LOC: 131 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: CDLN LOC: 131FT FROM PL MANDEVILLE 8.5' OUTSIDE PL 1.5'INSI ****/ | 2018-10-11 | LOCATED WATER MATER AND EXCAVATED DOWN ON INLET AND OUTLET SERVICES. FOUND LEAD SERVICES. REPLACED LEAD OUTLET WITH PLASTIC TUBING FROM METER TO PROPERTY ALSO RAISED METER TO GRADE. BACKFILLED
201801676801 | 2018-09-19 | LEAD/PLASTIC | 3826 | PALMYRA | S SCOTT | WILK | WM-LEAK IN THE STREET INLET SERVICE LEAK IN CONCRETE STREET NEXT TO ABOVE ADDRESS /** 1) MN: A225261 SN: 0049485, *TAP: SIZE: A LOC: 111 FEET FROM P LINE AT SCOTT S, *MB: CODE: ADL5 LOC: ON PALMYRA,112' FROM U.R.P.L. SO. SCOTT ****/ | 2018-11-08 | EXCVATED IN 8 X 8 CUT MADE WATER MAIN 3/4 INLET SERVICE WAS LEAKING.MADE REPAIR ON SERVICE TIED SERVICE BACK INTO THE WATER MAIN .BACKFILLED JOB AND WASHED STREET DOWN.
201801678401 | 2018-09-19 | LEAD/PLASTIC | 2061 | EASTER LN |  | WILK | UNDERGROUND LEAK IN SIDEWALK/AREA FLOODED INLET SERVICE @ METER /** 1) MN: A322988 SN: 0139525, *TAP: SIZE: B LOC: 431 FEET FROM P LINE AT VALENTINE CT.R, *MB: CODE: BDK2 LOC: ON EASTER LN., 9' FROM D.P.L. VALENTINE CT., 1' ****/ | 2018-11-01 | WE EXCAVATED TO MAKE REPAIRS TO A 1" CORP COCK ON A WATER MAIN IN THE SIDE WLAK BY HAND
201801683001 | 2018-09-20 | LEAD | 2309-11 | LAMANCHE |  | WMBK | *****************PICKUP***************** BROKEN METER BOX CASING ON SIDEWALK, 1 CONE LEFT FOR PROTECTION /** AT 2309: 1) MN: A331715 SN: 0140357, *TAP: SIZE: B LOC: 90 FEET FROM P LINE AT NO. TONTI, *MB: CODE: AE2 LOC: ON LAMANCHE, 90' FROM P.L. NO. TONTI, 7' OUTSIDE ****/ | 2018-10-19 | EXAMINED JOB AND FOUND BROKEN METER BOX CASING REPLACED METER BOX CASING IN SIDEWALK JOB COMPLETE
201801696401 | 2018-09-22 | LEAD | 201 | POLK | CATINA | WILK | **********************PICKUP************************ INLET SERVICE LEAK BETWEEN SIDEWAK AND CURB IN MUD /** 1) MN: A187799 SN: 0175672, *TAP: SIZE: B LOC: 27 FEET FROM P LINE AT CATINA, *MB: CODE: CDL LOC: ON POLK AVE 27' FROM PL OF CATINA ****/ | 2018-09-28 | EXCAVATED AND EXAMINED FOUND LEAK ON OUTLET REPAIRED LEAK CLEAN BACKFILLED AND DRESSED JOB ( FOUND LEAD ON OUTLET)
201801697401 | 2018-09-23 | LEAD | 2412-14 | DEERS | ALMONASTER AV | WMTLK | ML-METER LEAK ACCT#142392-479575 METER#A132202 EXAMINE INLET/OUTLET SERVICE FOR LEAK AREA SATURATED DUE TO RAINFALL IN AREA /** AT 2412: 1) MN: A132202 SN: 0077872, *TAP: SIZE: B LOC: 98 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: CDLN LOC: METER ON DEERS 98 FT FROM PL N ROCHEBLAVE ****/ | 2018-10-13 | EXCAVATED IN 4 X 4 SIDEWALK CUT FOUND 5/8 INCH CURB COCK LEAKING REPLACED CURB COCK BACKFILLED AREA
201801700001 | 2018-09-24 | LEAD | 2327 | JOSEPHINE | LASALLE | WILK | MI- LEAK ON SIDEWALK CURC COCK PASSING IN OFF POSITION, NO METER IN BOX, FLOODING SIDEWALK /** 1) MN: A249482 SN: 0061210, *TAP: SIZE: A LOC: 90 FEET FROM P LINE AT LASALLE, *MB: CODE: CFLN LOC: 73FT FROM PL LASALLE ****/ | 2018-10-30 | MADE 3X5 CUT IN SIDEWALK OVER 5/8 INLET SERVICE.CHANGED 5/8 METER BOX COK NO METER INSIDE.(SOC 3FT. X 5 FT. S/W) JOB COMPLETE
201801700601 | 2018-09-24 | LEAD | 5915 | TULLIS DR | WOODLAND PL | WOLK | MI- LEAK ON SIDEWALK ***CUST STATES IT IS NOT THE SAME AS 5910 TULLIS DR, STATES IT IS ACROSS THE STREET*** CHECK OUTLET SERVICE FOR A LEAK @ PROPERTY LINE FLOODING DRIVEWAY 11/12/18 LEAK BETWEEN SIDE WALK AND STREET FLOODING LAWN. * CALLER STATES FALL HAZARD* *****PER INSP L HEBERT UPGRD TO A ( B LEAVE IN SYSTEM ) (KSW) /** 1) MN: A301286 SN: 0162774, *TAP: SIZE: B LOC: 189 FEET FROM P LINE AT WOODLAND PL, *MB: CODE: OOOO LOC: ON TULLIS 199FT FROM PL WOODLAND ****/ | 2018-11-11 | ARRIVED ON JOB SITE EXAMINE LEAK IN MUD PLOT AND TREE ROOT EXCAVATED IN MUD PLOT BY HAND MADE REPAIR ON SERVICE RENEWED OUTLET BACKFILLED DRESS UP WORK SITE.
201801701201 | 2018-09-24 | LEAD | 829 | SISTER | BURGUNDY | WILK | ML- METER LEAK METER # A397917 ACCT# 163952-424574 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A290401 SN: 0103600, *TAP: SIZE: A LOC: 40 FEET FROM P LINE AT SISTER, *MB: CODE: CD LOC: ON BURGUNDY 40FT FROM PL SISTER 8FT OUTSIDE PL 2.5 ****/ | 2018-10-08 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA. JOB COMPLETE
201801701701 | 2018-09-24 | LEAD/PLASTIC | 2221 | CHIPPEWA | JACKSON AV | WILK | LOCATIONID#170183-542023 METER#D05121 INLET CONNECTION LEAK /** 1) MN: D005121 SN: 0009257, *TAP: SIZE: D LOC: 156 FEET FROM P LINE AT JACKSON AVE, *MB: CODE: CE LOC: 156FT PL JACKSON AV 5' OUTSIDE 3' INSIDE CURB ****/ | 2018-11-04 | WE ARRIVED AN EXAM AND FOUND A 2IN INLET LEAKING INSIDE A MAN HOLE
201801701901 | 2018-09-24 | LEAD | 2520 | D"ABADIE | N DORGENOIS | WILK | LOCATIONID#135480-489788 METER#A430952 INLET CONNECTION.LEAK /** 1) MN: SN: 0066183, *TAP: SIZE: A LOC: 169 FEET FROM P LINE AT DORGENOIS NO., *MB: CODE: CDLM LOC: ON D'ABADIE, 167' FROM P.L. NO. DORGENOIS ****/ | 2018-10-05 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201801703401 | 2018-09-24 | LEAD/PLASTIC | 1506 | ALVAR |  | WOLK | LOCATION: 211343 PER INSP L UDEBOR - PLEASE REPAIR BROKEN WHEEL AND SET A 5/8 METER. CUSTOMER HOME WAITING ON WATER BROKEN HANDWHEEL CUSTOMER WAITING ON WATER *****HOUSE UNDER RENOVATIONS***** /** 1) MN: A271204 SN: 0079426, *TAP: SIZE: B LOC: 55 FEET FROM P LINE AT ROBERTSON, *MB: CODE: BDL1 LOC: ON ALVAR ST. 56' FROM DIV. P.L. OF NO. ROBERTSON ****/ | 2018-10-01 | EXCV RAISE TO GRADE AND SET 5/8 METER LEAD ON INLET AND OUTLET.
201801703702 | 2018-09-24 | LEAD | 7736 | I-10 SERVICE RD | PARC BRITTANY BL | WMTBG | ACCT# 161186111 METER# A370184 METER CASING BELOW GRADE /** 1) MN: SN: 0159295, *TAP: SIZE: B LOC: 146 FEET FROM P LINE AT PARC BRITTANY BLVD, *MB: CODE: CK2 LOC: ON /** 1) MN: SN: 0159295, *TAP: SIZE: B LOC: 146 FEET FROM P LINE AT PARC BRITTANY BLVD, *MB: CODE: CK2 LOC: ON I-10 SERVICE RD., 146' FROM P.L. PARC BRITTANY ****/ | 2018-10-09 | EXCAVATED AROUND METER BOX FOUND LEAD ON INLET AND OUTLET METER AT GRADE. CLEAN BACKFILLED AND DRESSED JOB.
201801708401 | 2018-09-24 | LEAD | 4423 | VIXEN | CUPID | WILK | MI-LEAK IN STREET INLET SERVICE LEAK IN ASPHALT STREET FLOODING AREA /** 1) MN: A153924 SN: 0129364, *TAP: SIZE: C LOC: 302 FEET FROM P LINE AT CUPID, *MB: CODE: BDK LOC: ON VIXEN 294FT FROM P.L. CUPID ****/ | 2018-11-03 | EXAMINED AREA BROKE OUT CONCRETE IN STREET EXCAVATED IN STREET EXPOSED 1 INCH INLET SERVICE LEAK REPAIRED LEAK BACKFILLED CLEANED AREA COMPRESSED STREET
201801708601 | 2018-09-24 | LEAD | 1801 | ST CHARLES AV | FELICITY | WILK | WM-LEAK ON THE SIDEWALK EXAMINE INLET SERVICE FOR LEAK BETWEEN CURB/STREET IN FRONT OF WALGREEN /** 1) MN: C026694 SN: 0000000, *TAP: SIZE: C LOC: 62 FEET FROM P LINE AT ST CHARLES AVE, *MB: CODE: BE2 LOC: ON ST CHARLES 20 FT FR FELICITY BY DRIVEWAY ** 2) MN: C027158 SN: 0999999, *TAP: SIZE: C LOC: 30 FEET FROM P LINE AT FELICITY, *MB: CODE: CD LOC: METER IN MANHOLE ON FELICITY 206FT.FROM P.L.ST THERE IS 1 MORE NOT LISTED. ****/ DOTTIE READY 12-7-18 EXP 12-27-18 | 2018-12-29 | EXAMINED + FOUND NO LEAK
201801709801 | 2018-09-25 | LEAD | 2306 | ST BERNARD AV | N ROCHEBLAVE | UNKN | LOCATION: 218711 MTR# A 356570 PER INSP JD - NEED CONCRETE REMOVED, ALSO CHANGE METER. FOUND CEMENT IN METER BOX UNABLE TO REMOVE METER /** 1) MN: A334748 SN: 0049182, *TAP: SIZE: A LOC: 203 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BFN LOC: ON ST. BERNARD AVE.,203' FROM U.R.P.L. NO. ****/ | 2018-10-05 | RENEWED CONCRETE FROM METER BOX ALSO MADE A 1 X 1 CUT IN SIDEWALK TO SHIFT CASING FROM OVER CURB COCK TO CHANGE 5/8 INCH METER ****************OLD METER INFO**************** METER:A356570 FAC:69297441 MAKE:SENSUS READ:44962
201801710001 | 2018-09-25 | LEAD | 5006 | N ROBERTSON | REYNES | WMTLK | **********PICK UIP********** EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER. /** 1) MN: A245554 SN: 0108016, *TAP: SIZE: B LOC: 70 FEET FROM P LINE AT REYNES, *MB: CODE: BDK LOC: RES 64FT P.L. REYNES BY DRIVE 7' OUTSIDE ****/ | 2018-10-28 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO MAKE THE REPAIRS MADE A 3X3 MUD CUT BACKFILLED AND DRESS UP CUT
201801724501 | 2018-09-27 | LEAD | 3809 | WASHINGTON AV | ROCHEBLAVE | WILK | LOCATIONID#138206-551507 METER#A276268 LEAK INSIDE METERBOX CURB COCK PASSING IN OFF POSITION, NO METER IN BOX /** 1) MN: A276268 SN: 0068778, *TAP: SIZE: A LOC: 24 FEET FROM P LINE AT ROCHEBLAVE S, *MB: CODE: BDL1 LOC: ON WASHINGTON AVE., 55' FROM L.P.L. SO. ROCHEBLAVE ****/ | 2018-11-10 | EXCVATED IN MUDPLOT OVER 5/8 INLET SERVICE.REPLACED METER BOX COCK.BACKFILLED .REMOVE AND SET NEW METER.(OLD METER # A276268/SENSUS;NEW METER A418845/HERSEY.) OLD METER INFO: A276268 FACT: 45179638 MAKE: SENSUS READ: 9757
201801728401 | 2018-09-27 | LEAD | 1035 | LEBOUEF | DIANA | WMRE | *************PICKUP JOB**** LOCATE WATER METER, ADJUST TO GRADE & MARK /** 1) MN: A340544 SN: 0113308, *TAP: SIZE: A LOC: 79 FEET FROM P LINE AT NEWTON, *MB: CODE: BD LOC: ON LEBOUEF, 81' FROM P.L. NEWTON, 8' OUTSIDE P.L. ****/ | 2018-11-21 | EXAMINED PROPERTY TO LOCATE METER COUND NOT LOCATE METER IT APPEARS A GRAVEL/ASPHALT DRIVEWAY HAS BEEN LAID OVER MUD PLOT
201801729801 | 2018-09-28 | LEAD | 5754 | E LOUIS PRIMA DR | LAKE FOREST BL | WOLK | MI- LEAK ON SIDEWALK CHANGED FROM 5754 LOUIS PRIMA CT EXAMINE OUTLET SERVICE FOR A LEAK IN THE SIDEWALK /** 1) MN: A276248 SN: 0161412, *TAP: SIZE: A LOC: 605 FEET FROM P LINE AT LAKE FOREST BLVD, *MB: CODE: OOO LOC: ON LOUIS PRIMA 605FT FROM PL LAKE FOREST 3FT INSD ****/ | 2019-02-03 | ARRIVED ON JOB SITE EXAMINED LEAK IN AREA EXCAVATED IN MADE REPAIRS ON SERVICE BACKFILLED DRESS UP WORK SITE
201801733501 | 2018-09-29 | LEAD | 927 | BOURBON | ST PHILIP | WOLK | ACCT# 105646-402207 METER#A197251 INSPECTOR FOUND CONS REG ON METER /** 1) MN: A197251 SN: 0021380, *TAP: SIZE: B LOC: 133 FEET FROM P LINE AT ST PHILIP, *MB: CODE: AE6 LOC: 4APTS AND OFFICE 133.2 FT FROM P LINE ST PHILIP ****/ | 2018-10-07 | EXAMINED + FOUND 5/8 INCH WASHERS LEAKING QAQND FOUND SPLIT HANDWHEEL THAT WAS CAUSING CONSTANT REGISTRATION REPLACED BROKEN 5/8 INCH HANDWHEEL
201801733901 | 2018-09-29 | LEAD/PLASTIC | 4312 | STATE STREET DR | GRAPE | WILK | MI- LEAK IN STREET EXAMINE INLET IN ASPHALT STREET. FLOODING BOTH SIDES OF THE STREET, WATER GETTING OFF IN DCB. (C) /** 1) MN: A287130 SN: 0080569, *TAP: SIZE: Y LOC: 95 FEET FROM P LINE AT GRAPE, *MB: CODE: BDK4 LOC: 124' P.L. GRAPE ****/ DOTTIE READY 11-16-18 EXP 12-6-18 | 2018-11-28 | ARRIVED AT ABOVE LOCATION,EXAMINED ,EXCAVATED AND MADE REPAIRS TO STOP LEAK ON 6"WATER MAIN .BACKFILLED ,CLEANED UP AND WASHED DOWN WORK AREA TO COMPLETE JOB.(SOC 4FT X 4FT. D/W;12FT.X 8 FT .ASPHALT STREET F/D)
201801738001 | 2018-10-01 | LEAD | 1908 | LIZARDI | PRIEUR | WILK | WM-LEAK IN THE STREET CHAANGED FROM 1900BLK LIZARDI INLET ON ABANDON SERVICE INFRONT VACANT LOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-15 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 INCH INLET SERVICE FOR ABANDON 10 FT UNDERNEATH CURB BACKFILLED AREA
201801738101 | 2018-10-01 | LEAD | 5411 | N ROMAN | ANDRY | WILK | **********************PICKUP********************** INLET ON ABANDON SERVICE INFORNT VACANT LOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-10-22 | EXCAVATED AND MADE REPAIRS ON 3/4 INCH COOPER INLET SERVICE BACKFILLED JOB WITH RIVERSAND
201801741801 | 2018-10-01 | LEAD | 4024 | N ROBERTSON |  | WILK | MI LEAK ON SIDEWALK INLET SERVICE LEAK INSIDE BOX /** 1) MN: A309646 SN: 0075206, *TAP: SIZE: B LOC: 178 FEET FROM P LINE AT BARTHOLOMEW, *MB: CODE: CDL1 LOC: ON N ROBERTSON ST 184' FROM PL BARTHOLOMEW ****/ | 2018-11-07 | EXCAVATED IN PREVIOUS CUT + MADE REPAIR ON 3/4 INCH ABANDONED INLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201801741901 | 2018-10-01 | LEAD | 735 | MARIGNY | DAUPHINE | WILK | ML METER LEAK ACCT# 125300-480890 METER# INLET SERVICE LEAKING INSIDE BOX /** 1) MN: A248129 SN: 0047660, *TAP: SIZE: A LOC: 58 FEET FROM P LINE AT DAUPHINE, *MB: CODE: BDMN LOC: ON MARIGNY,60' FROM L.R.P.L. DAUPHINE ****/ | 2018-10-11 | REPLACED 5/8 INCH HANDWHEEL + GUTS INMETER BOX
201801742601 | 2018-10-01 | LEAD | 3042 | ST CLAUDE AV |  | WILK | LOCATION ID-139196 MTR-A397924 METER LEAK/AREA FLOODED INLET SERVICE LEAK IN BOX /** 1) MN: A311640 SN: 0069822, *TAP: SIZE: C LOC: 348 FEET FROM P LINE AT MONTEGUT, *MB: CODE: CDL5 LOC: 331FT FROM PL MONTEGUT ON ST CLAUDE ****/ | 2018-10-11 | EXAMINED JOB + FOUND JOB ALREADY COMPLETED
201801749501 | 2018-10-02 | LEAD | 338 | HILLARY | DOMINICAN | WILK | ML-METER LEAK ACCT# 118517-586399 METER# A415461 INLET SERVICE LEAK BAD BLEEDER VALVE FLOODING GRASSY AREA /** 1) MN: A286180 SN: 0042506, *TAP: SIZE: A LOC: 67 FEET FROM P LINE AT HILLARY, *MB: CODE: BFH LOC: 2ND METER SIDE ST ON DOMINICAN 67' P.L. HILLARY ****/ | 2018-10-02 | MADE ALL REPAIRS ON INLET LEAD LINE REFERRE TO ZONE 1 TO REMOVE LEAD
201801749801 | 2018-10-02 | LEAD | 1464 | N DORGENOIS | COLUMBUS | WILK | WM-LEAK IN SIDEWALK NEAR GRASSY AREA INLET SERVICE LEAK NO METER IN BOX /** 1) MN: B026044 SN: 0047397, *TAP: SIZE: B LOC: 48 FEET FROM P LINE AT COLUMBUS, *MB: CODE: CDL LOC: CURB 48' P.L. COLUMBUS ****/ | 2018-10-24 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH ABANDON INLET SERVICE BACKFILLED JOB WITH RIVERSAND JOB COMPLETE
201801750601 | 2018-10-02 | LEAD | 3430 | LOUISIANA AV PK | S GALVEZ | WILK | MI- LEAK ON SIDEWALK INLET SERVICE LEAK BEHIND CURB COCK FLOODING GRASSY AREA /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ DOTTIE READY 11/27/18 EXPIRATION 12/17/18 | 2018-11-19 | MADE REPAIRS ON 3/4 SERVICE REPLACED 5/8 CURB COCK ALSO REPLACED 5/8 WATER METER OLD METER INFO: M: A145929 F: 19210510 MAKE: ROCKWELL READ:3439
201801752801 | 2018-10-03 | LEAD | 1757 | N GAYOSO | AUBRY | WILK | ML- METER LEAK METER # A356971 ACCT # 128126-491715 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A125949 SN: 0059364, *TAP: SIZE: A LOC: 125 FEET FROM P LINE AT AUBRY, *MB: CODE: BDO2 LOC: 125FT FROM LSPL AUBRY BY TREE ****/ | 2018-10-16 | EXCAVATED IN CONCRETE DRIVEWAY AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AND CLEANED AREA
201801753401 | 2018-10-03 | LEAD | 2013 | MANDEVILLE | N JOHNSON | WILK | ML-METER LEAK ACCT#144425-483527 METER#A406127 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A259363 SN: 0075915, *TAP: SIZE: B LOC: 105 FEET FROM P LINE AT JOHNSON N, *MB: CODE: BD LOC: 104FT FROM PL JOHNSON 9FT ON MANDEVILLE ****/ | 2018-10-24 | MADE ADDITIONAL 2 X 2 SIDEWALK CUT AND MADE REPAIRS ON 3/4 INCH TEE AND INLET SERVICE BACKFILLED AREA
201801753501 | 2018-10-03 | LEAD | 2314 | PAULINE |  | WILK | ML-- METER LEAK METER# A150272 ACCT# 156502-483066 EXAMINE INLET SERVICE FOR LEAK METER UNDER WATER HOUSE UNDER RENOVATION /** 1) MN: A150272 SN: 0093546, *TAP: SIZE: A LOC: 91 FEET FROM P LINE AT TONTI, *MB: CODE: AD LOC: ON PAULINE 90' FROM PL N TONTI 7' OUTSIDE PL 3' IN ****/ | 2018-10-17 | EXCAVATED IN MUD PLOT AND REPLACED CLARK BOTTOM AND CURB COCK BACKFILLED AREA. JOB COMPLETE
201801754401 | 2018-10-03 | LEAD | 1813 | TOURO | N ROMAN | WMTLK | MI- UNDERGROUND LEAK PER METER MTR.# A-388528 ACCT # 129351-494646 /** 1) MN: A264897 SN: 0067911, *TAP: SIZE: A LOC: 109 FEET FROM P LINE AT ROMAN N, *MB: CODE: ADL LOC: ON TOURO 117FT FROM PL OF N ROMAN ****/ | 2018-10-26 | EXAMINE JOB AT ABOVE LOCATION FOUND NO LEAK ON INLET OR OUTLET
201801754701 | 2018-10-03 | LEAD | 905 | NASHVILLE AV | CAMP | WMTLK | ML- METER LEAK MN:B029477 ACCT#101792-563900 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: B029477 SN: 0011956, *TAP: SIZE: B LOC: 73 FEET FROM P LINE AT NASHVILLE AVE, *MB: CODE: CDHK LOC: 73FT FROM LSPL NASHVILLE ****/ | 2018-10-31 | ARRIVED AT ABOVE LOCATION ,EXAMINED ,EXCAVTED BY HAND AND MADE REPAIR TO STOP LEAK ON 3/4 INLET SERVICE LINE.BACKFILLED ,CLEANED UP,AND WASHED DOWN AREA TO COMPLETE JOB." LEAD INLET" (SOC 3FT. X 3 FT .CONCRETE D/W)
201801756601 | 2018-10-03 | LEAD | 1911 | N JOHNSON | ANNETTE | WOLK | ML MTR# A375440 LOC & CUST# 159625-494744 INSPECTOR: F/ON- OCC. OUTSIDE INSPECTION ONLY. CONS FOUND ON MTR, NO S&W VALUE VISIBLE AND NO REPAIRS /** 1) MN: A115612 SN: 0070143, *TAP: SIZE: A LOC: 186 FEET FROM P LINE AT ANNETTE, *MB: CODE: CEK LOC: ON N JOHNSON 86.5FT FROM PL OF ANNETTE 7.5FT OUT- ****/ | 2018-10-23 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201801759201 | 2018-10-04 | LEAD | 425 | BURGUNDY | CONTI | WILK | ML-LEAK IN THE STREET ACCT#117149-527663 METER#A195329 INLET SERVICE LEK IN SIDE BOX /** 1) MN: A195329 SN: 0023977, *TAP: SIZE: A LOC: 114 FEET FROM P LINE AT ST LOUIS, *MB: CODE: BEN7 LOC: 118' P.L. ST LOUIS ****/ | 2018-10-12 | EXAMINED AND FOUND BA D 5/8 INCH METER REPLACED METER 5/8 INCH AND REPLACED WASHERS ON ILET AND OUTLET. CHANGED 5/8 METER
201801760501 | 2018-10-04 | LEAD | 2506 | ANDRY | LAW | WMLK | **********************PICKUP*********************** LEAK ON THE WATER MAIN /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-10-29 | EXAMINED JOB AT ABOVE LOCATION AND FOUND NO LEAK
201801762801 | 2018-10-04 | LEAD | 2627 | IBERVILLE | N BROAD | WMBK | ********************PICK UP************** UPPER METER BOX CASING/BOTTOM BROKEN CASING HOLE ON SIDEWALK LEFT ONE BARREL/LIGHT /** 1) MN: A333255 SN: 0034136, *TAP: SIZE: A LOC: 285 FEET FROM P LINE AT BROAD N, *MB: CODE: CFLM LOC: 286' P.L. N BROAD ****/ | 2018-10-12 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED BROKEN 5/8 INCH METER BOX BOTTOM + UPPER CASING BACKFILLED + DRESSED UP AREA
201801763201 | 2018-10-04 | LEAD | 911 | DAUPHINE |  | WMTLK | LOCATION ID-103994 MTR-A197999 METER LEAK EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A197999 SN: 0031403, *TAP: SIZE: A LOC: 68 FEET FROM P LINE AT DUMAINE, *MB: CODE: CE LOC: ****/ | 2018-10-12 | EXCAVATED IN 2 X 4 SIDEWALK CUT REPLACED 5/8 CURB COCK CLEAN UP AREA BACKFILLED AREA. JOB COMPLETE
201801764201 | 2018-10-04 | LEAD | 1721 | GALLIER | N ROMAN | WOLK | ML-METER LEAK METER#A312848 ACCT#142218-431953 WATER PASSING IN OFF POSITION UNABLE TO MAKE REPAIRS /** 1) MN: A312848 SN: 0084647, *TAP: SIZE: A LOC: 167 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: AD4 LOC: 162FT FROM N.DERBIGNY ON GALLIER ****/ | 2018-10-30 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801764301 | 2018-10-04 | LEAD | 2429 | TOURO |  | WMTLK | METER LEAK EXAMINE INLET/OUTLET SERVCE FOR LEAK METER UNDER WATER /** 1) MN: A214003 SN: 0083103, *TAP: SIZE: B LOC: 214 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: ADLN LOC: 214' P.L. N ROCHEBLAVE ****/ | 2018-10-23 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INELT SERVICE BACKFILL JOB WITH RIVERSAND
201801764401 | 2018-10-04 | LEAD | 1936 | LAPEYROUSE | N JOHNSON | WILK | MI- LEAK IN SIDEWALK INLET SERVICE IN SIDEWALK FLOODING AREA ON ABANDON LOT NEXT TO ADDRESS /** 1) MN: 000000 SN: 0045388, *TAP: SIZE: B LOC: 51 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: BE LOC: 1ST METER SIDE ST ON N JOHNSON 50' P.L. LAPEYROUSE ****/ | 2018-10-15 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CORB COCK BACKFILLED + DRESSED UP AREA
201801764901 | 2018-10-05 | LEAD | 622 | PIRATES AL | ROYAL | WOLK | ML METERLEAK MTR#A286088 LOC/CUST#118882-528001 CONS REG ON METER. 10/21/18 CONSTANT REG ON METER. PER BILLING S/R # 12855202 (PET) /** 1) MN: C008080 SN: 0029522, *TAP: SIZE: C LOC: 150 FEET FROM P LINE AT ROYAL, *MB: CODE: EL1 LOC: ON PIRATES ALLEY 150' FROM PL ROYAL 2' OUTSIDE PL ** 2) MN: SN: 0029522, *TAP: SIZE: A LOC: 153 FEET FROM P LINE AT ROYAL, *MB: CODE: OOOO LOC: 153' P.L. ROYAL ****/ | 2019-02-14 | EXMINED + FOUND NO LEAK
201801765001 | 2018-10-05 | LEAD | 1714 | BAYOU RD | N CLAIBORNE AV | WOLK | ML METERLEAK MTR#A390975 LOC/CUST#153070-525798 CONS REG ON METER. /** 1) MN: SN: 0031868, *TAP: SIZE: B LOC: 111 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: ADKL LOC: ON BAYOU RD., 112.8' FROM P.L. NO. CLAIBORNE AVE., ****/ | 2018-10-12 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801768501 | 2018-10-05 | LEAD/PLASTIC | 4035 | WASHINGTON AV | S WHITE | WOLK | MI- LEAK ON SIDEWALK OUTLET SERVICE LEAK IN GRASS FLOODING GRASS & SIDEWALK. ALGAE HAS FORM ON SIDEWALK FROM LEAK (NEED MACHINE) /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ DOTTIE READY 10-18-18 EXP 11-7-18 | 2018-10-26 | EXAMINED AREA AROUND METER AND SIDEWALK FOUND LEAK IN SIDEWALK .USED AIRGUN TO CUT SIDEWALK OUT TO EXPOSE CONTROL LINE .REPAIRED LEAK BACKFILLED AND CLEANED AREA.(SOC 2FT. X 3 FT .S/W)
201801770102 | 2018-10-20 | LEAD | 4305 | WERNER DR | CHEF MENTEUR HW | WILK | /** 1) MN: C021786 SN: 0138135, *TAP: SIZE: C LOC: 140 FEET FROM P LINE AT CHEF MENTEUR HWY, *MB: CODE: CDL LOC: BEAUTY & BARBER SHOPS 140FT FROM PL CHEF HWY 8' O ****/ | 2018-10-27 | EXCCAVATED IN A 4X6 SIDEWALK WITH JACKHAMMMER AND BUY HAD FOUND A BANDIT LEAD LINE LEAKING. REPLACING ABANDED LINE WITH A 5/8 PACK JOINT. BACKFILL AND DRESS WITH RIVER SAND AND COLD MILL. (JOB COMPLETE)
201801771701 | 2018-10-06 | LEAD | 1125 | ROYAL | GOV NICHOLLS | WILK | ACCT# 114493-529170 MTR# A293396 INSPECTOR FOUND LEAK AT CURB COCK /** 1) MN: A293396 SN: 0017613, *TAP: SIZE: A LOC: 121 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: BFR4 LOC: 10 APTS 126' P.L. GOV NICHOLLS ****/ | 2018-10-30 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLEDAND CLEANED THE AREA
201801772502 | 2018-10-07 | LEAD | 9022 | EDINBURGH |  | PASI | NEED TO REPLACE A 4X18 ASPHALT STREET CUT /** 1) MN: A232164 SN: 0080716, *TAP: SIZE: A LOC: 197 FEET FROM P LINE AT HOLLYGROVE, *MB: CODE: ADL LOC: ON EDINBURG 206' FROM PL OF HOLLYGROVE ****/ | 2019-03-28 | JOB COMPLETED -PER ROYAL.
201801774201 | 2018-10-08 | LEAD | 3932 | PRYTANIA | CONSTANTINOPLE | WLPR | PP-POOR PRESSURE ACCT#108559-556777 METER#A326707 EXAMINE INLET SERVICE FOR POOR PRESURE FOUND 25PSI /** 1) MN: A283912 SN: 0005605, *TAP: SIZE: B LOC: 80 FEET FROM P LINE AT CONSTANTINOPLE, *MB: CODE: CD LOC: ON PRYTANIA 106FT FROM CONSTANTINOPLE ****/ | 2018-10-09 | REPLACED 3/4 SERVICE FROM 6" WATER MAIN TO METER BOX(5FT .X 5 FT .S/W; 10FT. X 42 FT. ST).
201801775001 | 2018-10-08 | LEAD | 1614 | INDEPENDENCE | N CLAIBORNE AV | WMLK | MI- LEAK ON BETWEEN CURB AND SIDEWALK LEAK ON WATER MAIN NEAR ADDRESS BY WOODEN FENCE. LEFT MARKING ON GROUND NEAR LEAK /** 1) MN: A183328 SN: 0096485, *TAP: SIZE: B LOC: 110 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: ADK2 LOC: ON INDEPENDENCE 110' FROM PL N CLAIBORNE AVE 8' ****/ | 2018-10-14 | MADE 8 X 32 CUT IN BLACK TOP STREET TRACEDTHE LEAK AND FOUND SERVICE LEAKING FOR ABANDON LOT MADE REPAIRS ON 3/4 INCH TAILPIECE BACKFILLED BACKFILLED AREA. JOB COMPLETE
201801779501 | 2018-10-08 | LEAD | 2107 | MARENGO | S SARATOGA | WMTLK | MI- LEAK ON THE SIDEWALK EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: A297146 SN: 0059695, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT SARATOGA S, *MB: CODE: AD LOC: ON MARENGO 51.7' FROM SPL SARATOGA S ****/ | 2018-10-17 | ARRIVED AT ABOVE LOCATION, EXAMINED, EXCAVATED BY HAND AND MADE REPAIRS TO STOP LEAK ON 5/8 INLET SERVICE LINE. BACKFILLED, CLEANED UP AND WASHED DOWN WORK AREA TO COMPLETE JOB. ALSO RENEWED OUTLET FROM METERBOX TO PROPERTY LINE BY REMOVING LEAD LINE AND REPLACED WITH PLASTIC TUBING. LEAD INLET
201801780301 | 2018-10-09 | LEAD | 5523 | S ROCHEBLAVE | OCTAVIA | WILK | LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET /** 1) MN: A141335 SN: 0091176, *TAP: SIZE: A LOC: 179 FEET FROM P LINE AT OCTAVIA, *MB: CODE: CD2 LOC: ON S ROCHEBLAVE 179' FROM PL OCTAVIA 8' OUTSIDE PL ****/ | 2018-10-14 | EXCAVATED 6 X 4 MUD PLIOT MADE REPAIR ON ABANDON INLET SERVICE AT METER BOX BACKFILLED AND CLEANED THE AREA MARKED WITH BLUE PAINT IN THE STREET ABD METER BOX TAP
201801789301 | 2018-10-10 | LEAD/PLASTIC | 2734 | CALHOUN | BARRETT | WILK | MI - LEAK IN STREET *************L.THOMPSON @ 12:41PM************* INLET SERVICE LEAK IN CONCRETE STREET FLOODING AREA GETTING OFF IN DCB /** 1) MN: A231482 SN: 0074767, *TAP: SIZE: B LOC: 239 FEET FROM P LINE AT STORY, *MB: CODE: BFK2 LOC: ON CALHOUN 239' FROM PL OF STORY ****/ | 2018-11-04 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 1"CONTROLLING LINE LEAKING.REPLACED 8FT. OF 1"TUBING TIED INTO LEAD.(SOC 8FT. X 8 FT. COCNRETE STREET)
201801790101 | 2018-10-10 | LEAD | 600-02 | N ST PATRICK |  | WILK | LOCATION ID-131593 MTR-A385222 MTR ON/CUST NOT GETTING WATER/CUST WAITING ON WATER *******D RANDOLPH @ 14:08PM****** INLET SERVICE LEAK IN TREE ROOTS BETWEEN MUDPLOT AND STREET *****CUSTOMER OUT OF WATER***** /** AT 600: 1) MN: A284183 SN: 0062239, *TAP: SIZE: B LOC: 49 FEET FROM P LINE AT ST PATRICK N, *MB: CODE: CDH5 LOC: ON TOULOUSE,50' FROM L.P.L. NO. ST. PATRICK ** AT 602: 2) MN: A157190 SN: 0062339, *TAP: SIZE: A LOC: 49 FEET FROM P LINE AT ST PATRICK N, *MB: CODE: CDH5 LOC: ON TOULOUSE,48.5' FROM L.P.L. NO. ST. PATRICK ****/ | 2018-10-10 | EXCAVATED CIN NUDPLOT AN TREE ROOTS REPAIR 5\8 STOP AN WAST LEAD LINE DRESS UP WITH RIVERSAND JOB REF TO ZONE1 TO TAKE LEAD LINE OUT FROM WATERMAIN TO METERBOX
201801790901 | 2018-10-10 | LEAD | 1524 | CRETE | LEPAGE | WMTLK | ML-METER LEAK ACCT#139158-490906 MTR#A123840 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: A123840 SN: 0036924, *TAP: SIZE: __ LOC: 168 FEET FROM P LINE AT LAPAGE, *MB: CODE: OOO LOC: ON CRETE 170' PL OF LAPAGE ****/ | 2018-10-24 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN MTER BOX ALSO EXCAVATED + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSSED UP AREA
201801791301 | 2018-10-10 | LEAD | 1821 | URSULINES AV | N TONTI | WMTLK | ML: METER LEAK, METER# A425454, ACCT # 111940-525153 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK METER BOX UNDER WATER SIDEWALK FLOODED /** 1) MN: A289019 SN: 0039905, *TAP: SIZE: A LOC: 153 FEET FROM P LINE AT ROMAN, *MB: CODE: CD LOC: ON URSULINES 151FT FROM ROMAN ****/ | 2018-10-24 | EXCAVATED IN CONCRETE DRIVEWAY + REPLACED TWO 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801792601 | 2018-10-11 | LEAD | 2323 | N VILLERE |  | WMRE | LOCATION: 303625 MTR# A 427165 PER INSP UDEBOR - METER BOX BURIED, CONCRETE AND ROCKS OVER METER BOX, ALSO CHANGE THE METER. LOCATE, RAISE TO GRADE AND CHANGE METER, HOUSE UNDER RENOVATION /** 1) MN: 000000 SN: 0061507, *TAP: SIZE: A LOC: 180 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: BE1 LOC: CURB AT #25 - ****/ | 2018-10-22 | EXCAVATED IN LIMESTONE DRIVEWAY + LOCATED METER BOX ALSO REPLACED 5/8 INCH WATER METER BACKFILLED + DRESSED UP AREA ALSO REPLACED 5/8 INCH CURB COCK ***************OLD METER INFO************ METER:A427165 FAC:16312177 MAKE:HERSEY READ:25
201801792901 | 2018-10-11 | LEAD/PLASTIC | 9109 | PRITCHARD PL | HAMILTON | WOLK | LOCATION ID-219434 MTR-A420684 LEAK BETWEEN STOP & WASTE AND MTR/CONS REG ON MTR /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-10-19 | EXCAVATED IN MUDPLOT TO REPAIR A 5/8" OUTLET SERVICE ADJUST METER BOX UP TO GRADE AND REPLACED 8FT OF PVC PIPE FROM HAND WHEEL TO PROPRETY BACKFILLED AND DRESS UP PLASTIC INLET AND LEAD OUTLET JOB COMPLETE
201801793501 | 2018-10-11 | LEAD | 2024 | N MIRO | PAUGER | WOLK | MI- CONS ON METER PER INSPECTOR MTR: A-412162 ACCT# 210005- 495324 /** 1) MN: A223077 SN: 0073324, *TAP: SIZE: B LOC: 216 FEET FROM P LINE AT ST ANTHONY AV, *MB: CODE: AD LOC: 215' P.L. ST ANTHONY AVE ** 2) MN: A342390 SN: 0073324, *TAP: SIZE: D LOC: 103 FEET FROM P LINE AT PAUGER, *MB: CODE: CD LOC: ON N MIRO 107' FROM P.L. PAUGER 3'OUTSIDE 9'INSIDE THERE ARE 2 MORE NOT LISTED. ****/ | 2018-10-23 | EXAMINE AND FOUND NO LEAK ON OUTLET SERVICE
201801794301 | 2018-10-11 | LEAD | 1936 | N TONTI | ALLEN | WILK | ML- METER LEAK ACCT# 155880-494215 METER#A403241 EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A311753 SN: 0087267, *TAP: SIZE: A LOC: 36 FEET FROM P LINE AT ALLEN, *MB: CODE: CDK LOC: ON NO. TONTI, 35.5' FROM P.L. ALLEN,8.5' OUTSIDE ****/ | 2018-10-23 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH OUTLET SERVICE IN SIDEWALK BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201801795601 | 2018-10-11 | LEAD | 2121 | FORSTALL | N GALVEZ | WILK | ML- METER LEAK MTR# A427262 ACCT# 304096-405870 INELT SERVICE LEAK INSIDE METER BOX /** 1) MN: A251102 SN: 0117289, *TAP: SIZE: A LOC: 191 FEET FROM P LINE AT NO. GALVEZ, *MB: CODE: AEK LOC: ON FORSTALL, 185' FROM P.L. NO. GALVEZ, 5' OUTSIDE ****/ | 2018-10-22 | REPLACE BOTH INLET AND OUTLET WASHRS AT ABOVE LOCATION
201801802001 | 2018-10-12 | LEAD | 1844 | THALIA | DRYADES | WILK | ML- METER LEAK METER# A428343 ACCT# 134402-479671 BAD BLEEVER VALVE IN BOX, FLOODING SIDEWALK 12/04/18 CUST STATED LEAK HAS GOTTEN WORSE PER SR#12859581 (AJR) /** 1) MN: A327891 SN: 0000000, *TAP: SIZE: B LOC: 62 FEET FROM P LINE AT DRYADES, *MB: CODE: BELN LOC: ON THALIA,62' FROM R.P.L. DRYADES ****/ DOTTIE READY 12-11-18 EXP 12-31-18 | 2018-12-29 | EXCAVATED AND REPAIRED INLET SERVICE LEAK TREE ROOTS SLOWED PROGRESS 3 X5 SIDEWALK CUT BACKFILLED NEED PAVING
201801804101 | 2018-10-12 | LEAD | 1615 | GOV NICHOLLS | N ROBERTSON | WILK | ML- METER LEAK MTR# A380345 ACCT # 212427-722759 INLET SERVICE LEAKING BEHIND CURB COCK /** 1) MN: A133387 SN: 0018354, *TAP: SIZE: E LOC: 110 FEET FROM P LINE AT N ROBERTSON, *MB: CODE: CD LOC: ON GOV NICHOLLS 99FT FROM PL OF N CLAIBORNE AVE ** 2) MN: A300669 SN: 0018354, *TAP: SIZE: E LOC: 110 FEET FROM P LINE AT N ROBERTSON, *MB: CODE: CD LOC: ON GOV NICHOLLS 98FT FROM PL OF N CLAIBORNE AVE THERE ARE 23 MORE NOT LISTED. ****/ | 2018-10-24 | EXAMINE JOB AT ABOVE LOCATION LEAK IS ON PROPERTY REFER TO P.O.P FOR REPAIRS TO BE MADE
201801804301 | 2018-10-12 | LEAD | 2227 | D"ABADIE |  | WILK | METER LEAK MTR# A 380438 ACCT# 122929-488653 INLET SERVICE LEAKING BEHIND CURB COCK /** 1) MN: SN: 0055341, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT TONTI, *MB: CODE: CDM2 LOC: ON D'ABADIE 76FT FROM PL OF N TONTI ****/ | 2018-10-24 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLT SERVICE BACKFILLED JOB WITH RIVERSAND COLDMILL
201801805301 | 2018-10-12 | LEAD | 3436 | S ROBERTSON | DELACHAISE | WMTLK | ML METER LEAK ACCT# 155737-703412 METER# A422087 EXAMINE INLET/OUTLET SERVICE FOR LEAK INSIDE METER BOX /** 1) MN: A252119 SN: 0092601, *TAP: SIZE: A LOC: 38 FEET FROM P LINE AT DELACHAISE, *MB: CODE: BDLN LOC: ON SO. ROBERTSON,38' FROM .L. DELACHAISE,9.5' OUT- ****/ | 2018-10-18 | ARRIVED AT LOCATION, EXAMINED JOB FOUND BAD BLEEDER ON METER BOX COCK. HAND DUG THE JOB PUT A NEW NEW METER BOX COCK WITH OUT FITTING AND 2 NEW WASHERS. BACKFILLED WITH 3 BUCKETS OF RIVERSAND CLEANED JOB AFTER WE FINISHED
201801808201 | 2018-10-14 | LEAD | 1623 | FORSTALL | N CLAIBORNE AV | WILK | MI LEAK ON SIDEWALK INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A272448 SN: 0114629, *TAP: SIZE: A LOC: 164 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: D LOC: RES ON FORSTALL 169FT PL N CLAIBORNE AV 6' OUTSIDE ****/ | 2018-10-26 | MADE 2 X 4 SIDEWALK CUT AND MADE REPAIRS ON 3/4 INCH OUTLET SERVICE BACKFILLED AREA
201801808701 | 2018-10-15 | LEAD | 701 | N SALCEDO |  | WMRE | LOCATION: 178896 PER INSP UDEBOR - METER BOX BURIED, PLEAE LOCATE AND CHANGE MTR# A 372031 LOC ATE, RAISE TO GRADE AND CHANGE METER /** 1) MN: A320439 SN: 0039759, *TAP: SIZE: A LOC: 44 FEET FROM P LINE AT SALCEDO N, *MB: CODE: AELO LOC: ST PETER 1ST METR INSIDE 43' P/L N SALCEDO 2' ****/ | 2018-11-02 | EXCAVATED AND RAISE METER BOX UP TO GRADE IN GARDEN BACKFILL JOB WITH RIVERSAND
201801809901 | 2018-10-15 | LEAD | 1014 | CHARTRES |  | WMTLK | LOCATIONID#106116-528856 METER#B023633 LEAK INSIDE METERBOX /** 1) MN: A292581 SN: 0135784, *TAP: SIZE: A LOC: 114 FEET FROM P LINE AT ST PHILIP, *MB: CODE: CF LOC: 115FT FROM PL ST PHILIP ****/ | 2018-10-24 | EXCAVATED AND MADE REPAIRS ON 3/4 INCH INLET SERVICE IN SIDEWALK BCKFILLED JOB WITH RIVERSAND AND COLDMILL
201801810001 | 2018-10-15 | LEAD | 710 | URSULINES AV |  | WMTLK | LOCATIONID#112369-529002 METER#A363154 LEAK INSIDE METERBOX /** 1) MN: A277396 SN: 0053290, *TAP: SIZE: B LOC: 105 FEET FROM P LINE AT ROYAL, *MB: CODE: BE LOC: ON URSULINES 105FT FROM ROYAL ****/ | 2018-10-24 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201801810401 | 2018-10-15 | LEAD | 185 | WALNUT |  | WMTLK | LOCATIONID#152250-585479 METER#A429930 LEAK INSIDE METERBOX /** 1) MN: A224162 SN: 0061083, *TAP: SIZE: A LOC: 131 FEET FROM P LINE AT MAGAZINE, *MB: CODE: ADN1 LOC: 3RD METER FROM MAGAZINE,IN FRONT OF 185 WALNUT ** 2) MN: SN: 0061083, *TAP: SIZE: A LOC: 131 FEET FROM P LINE AT MAGAZINE, *MB: CODE: ADN1 LOC: 3RD METER FROM MAGAZINE,IN FRONT OF 185 WAKNUT THERE ARE 2 MORE NOT LISTED. ****/ | 2018-10-31 | ARRIVED AT ABOVE LOCATIO ,EXAMINED ,EXCAVATWED BY HAND AND MADE REPAIRS TO STOP LEAK ON 5/8 OUTLET SERVICE LINE ALSO RENEWED OUTLET BY REMOVING LEAD LINE FROM METER BOX TO PROPERTY LINE.BACKFILLED CLEANED UP AND WASHED DOWN AREA TO COMPLETE JOB."LEAD INLET" (SOC 10FT. X 4 FT .S/W) OLD METER INFO: A429930 FACTORY: 16355519 MAKE: HERSEY READ; 3828
201801811501 | 2018-10-15 | LEAD/PLASTIC | 2716 | 2ND | CLARA | WMTLK | ML METER LEAK METER# A416772 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER GRASS & GUTTER BOTTOM FLOODED ***HOUSE UNDER RENOVATIONS*** /** 1) MN: A212583 SN: 0054902, *TAP: SIZE: A LOC: 107 FEET FROM P LINE AT CLARA, *MB: CODE: CDLM LOC: ON SECOND ST 106' FROM RPL CLARA ****/ | 2018-10-23 | ARRIVED AT ABOVE LOCATION,EXAMINED EXCAVATED BY HAND AND MADE REPAIRS TO STOP LEAK ON 5/8 INLET SERVCIE LINE.BACKFILLED CLEANED UP AND WASHED DOWN AREA TO COMPLETE JOB. (LEAD INLET)
201801811601 | 2018-10-15 | LEAD | 1335 | BARTHOLOMEW |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 207673-725894 METER NUMBER - A311064 EXAMIN INLET SERVICE FOR LEAK CARS PARKING ON METER /** 1) MN: A304030 SN: 0062041, *TAP: SIZE: C LOC: 68 FEET FROM P LINE AT VILLERE N, *MB: CODE: AK1 LOC: ON BARTHOLOMEW 66FT FROM P.L. N VILLERE 8FT OUT- ****/ | 2018-10-25 | EXCAVATED AND MADE REPAIRS ON INLET SERVICE BAKFILLED JOB WITH RIVERSAND
201801814101 | 2018-10-15 | LEAD | 5320 | DAUPHINE | EGANIA | WILK | ML- METER LEAK ACCT# 165954-424851 MTR# A416878 INLET SERVICE LEDAK IN BOX /** 1) MN: A245775 SN: 0106300, *TAP: SIZE: A LOC: 201 FEET FROM P LINE AT EGANIA, *MB: CODE: ADL3 LOC: ON DAUPHINE, 201' FROM P.L. EGANIA, 7' OUTSIDE ****/ | 2018-10-26 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201801816501 | 2018-10-15 | LEAD | 2373 | N VILLERE |  | WMTLK | LOCATIONID#121735-481747 METER#A209341 LEAK INSIDE METERBOX EXAMNE INLET/OUTLET SERVICE FOR LEAK MERER BOX LOCATED ON SIDEWALK /** 1) MN: A209341 SN: 0039468, *TAP: SIZE: A LOC: 34 FEET FROM P LINE AT ST ROCH AVE, *MB: CODE: BEFK LOC: INSIDE BY STEPS 35' P.L. ST ROCH AVE ****/ | 2018-10-25 | EXCAVATED IN BRICK SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801816801 | 2018-10-15 | LEAD | 819 | S CARROLLTON AV | MAPLE | WILK | ML- METER LEAK METER# A215576 ACCT# 200763-584157 INLET SERVICE LEAK IN MUDPLOT LEAKING FROM BLEEDER VALVE /** 1) MN: A215576 SN: 0049468, *TAP: SIZE: A LOC: 133 FEET FROM P LINE AT MAPLE, *MB: CODE: AD LOC: ON S CARROLLTON 133FT FROM PL MAPLE 9FT OUTSIDE PL ****/ | 2019-06-10 | EXCV 4 X 4 CUT EXAMINE INLET/ OUTLET SERVICE LINE FOUND NO LEAK NO LEAK INSIDE METER BOX FOUND LEAD ON INLET /OUTLET SERVICE LINE BACKFILLED AND DRESS CUT WITH SAND. JOB COMPLETE
201801817301 | 2018-10-15 | LEAD | 2453 | N ROMAN |  | WILK | LOCATIONID#304058-422312 METER#A427394 BLEEDER LEAK INLET SERVICE LEAK IN MUDPLOT FLOODING CURB CAUSING POOR PRESSURE /** 1) MN: A124533 SN: 0067919, *TAP: SIZE: B LOC: 144 FEET FROM P LINE AT MUSIC, *MB: CODE: BDN1 LOC: 144FT FROM PL MUSIC ****/ | 2018-10-24 | EXCAVATED IN MUD PLOT UNDERNEATH CURB NEAR DRAIN BASE AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201801817401 | 2018-10-15 | LEAD/PLASTIC | 6457 | GEN DIAZ | BRAGG | WILK | WM-LEAK BETWEEN THE STREET AND SIDEWALK EXAMINE INLET SERVICE FOR LEAK IN GRASS FLOODING GRASS NEAR STREET /** 1) MN: A320430 SN: 0103703, *TAP: SIZE: A LOC: 357 FEET FROM P LINE AT BRAGG, *MB: CODE: BDLN LOC: ON GEN. DIAZ, 357' FROM P.L. BRAGG, 8' OUTSIDE ****/ | 2018-10-24 | EXCAVATED IN MUD PLOT TO REPAIR A LEAK ON A 5/8 INLET SERVICE AND REPLACED 8 FT OF PVC PIPE FROM THE CURB TO METER BOX BACKFILLED AND DRESS UP WITH RIVERSAND
201801818201 | 2018-10-16 | LEAD | 1828 | ARTS |  | WILK | LOCATIONID#132687-482889 METER#A412207 BLEEDER LEAK /** 1) MN: A289524 SN: 0048073, *TAP: SIZE: A LOC: 238 FEET FROM P LINE AT ROMAN N, *MB: CODE: BDN1 LOC: ON ARTS ST 238' FROM PL N ROMAN ****/ | 2018-10-25 | EXCAVATED IN MUD PLOT +REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA ALSO REPLACED 5/8 INCH HANDWHEEL
201801819101 | 2018-10-16 | LEAD/PLASTIC | 2045 | MANDOLIN |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 165453-501926 METER NUMBER - A285172 INLET SERVICE LEAK IN MUD PLOT /** 1) MN: A285172 SN: 0105430, *TAP: SIZE: A LOC: 72 FEET FROM P LINE AT PAUGER, *MB: CODE: CDK LOC: 72FT FROM PL PAUGER MTR ON MANDOLIN 7FT OUTSIDE ****/ | 2018-10-31 | EXCAVATED IN MUD PLOT TO REPAIR A LEAK ON A 5/8" INLET ADJUST METER BOX UP TO GRADE AND REPLACED 9FT OF 3/4" PIPE FROM CURB TO PROPERTY BACKFILLED AND DRESS UP
201801819801 | 2018-10-16 | LEAD | 1405 | EGANIA | N VILLERE | HGRD | WM-LEAK IN SIDEWALK EXAMINE HOLE IN GROUND ON FRONT ABOVE ADDRESS, MARKED WITH GREEN PAINT ****NO LEAK FOUND ****** /** 1) MN: A283021 SN: 0100778, *TAP: SIZE: B LOC: 64 FEET FROM P LINE AT EGANIA, *MB: CODE: BDHK LOC: RES ON N.VILLERE 64FT P.L. EGANIA 7' OUTSIDE ****/ | 2018-10-29 | EXCAVATED IN MUD PLOT + SIDEWALK NEAR SMALL HOLE IN GRASS AT ABOVE LOCATION FOUND NO LEAK + NO SEWER CONNECTION IN CUT BACKFILLED + DRESSED UP AREA
201801820401 | 2018-10-16 | LEAD | 2057 | N PRIEUR |  | WMRE | SERVICE IS BURIED. PLEASE RAISE TO GRADE AND CHANGE METER A383155 LOC ID 125025 LOCATE, RAISE TO GRADE AND CHANGE METER /** 1) MN: A263022 SN: 0054686, *TAP: SIZE: A LOC: 97 FEET FROM P LINE AT TOURO, *MB: CODE: ADKO LOC: OPP GATE 98' P.L. TOURO ****/ | 2018-10-30 | FOUND METER BOX IN SIDEWALK WITH NEW HARSEY METER ALREADY SET MARKED METER BOX WITH BLUE PAINT
201801822001 | 2018-10-16 | LEAD | 6010 | CHARTRES | GORDON | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A287104 SN: 0161396, *TAP: SIZE: B LOC: 59 FEET FROM P LINE AT ALABO, *MB: CODE: OOO LOC: ON CHARTRES 99FT FROM PL ALABO 5FT OUTSD PL 3FT IN ****/ | 2018-10-30 | ARRIVED AT ABOVE LOCATION + FOUND KOCK ON CURB COCK IN METER BOX + COCK LEAKING EXCVAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801822101 | 2018-10-16 | LEAD | 417 | TUPELO | DOUGLAS | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A325487 SN: 0125215, *TAP: SIZE: B LOC: 151 FEET FROM P LINE AT BIENVENUE, *MB: CODE: ADK7 LOC: ON TUPELO 152FT PL BIENVENUE 7' OUTSIDE ****/ | 2018-10-29 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA. (NO METER) JOB COMPLETE
201801822201 | 2018-10-16 | LEAD | 514 | TUPELO | DOUGLAS | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A129541 SN: 0135281, *TAP: SIZE: B LOC: 100 FEET FROM P LINE AT CHARTRES, *MB: CODE: AD2 LOC: 101FT FROM PL CHARTRES 8' OUTSIDE ****/ | 2018-10-29 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801822301 | 2018-10-16 | LEAD | 1237 | GORDON | URQUHART | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A283628 SN: 0092918, *TAP: SIZE: B LOC: 290 FEET FROM P LINE AT MARAIS, *MB: CODE: CDL LOC: RES ON GORDON 290FT FROM PL MARAIS ****/ | 2018-10-30 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA. JOB COMPLETE
201801823001 | 2018-10-16 | LEAD | 511 | ALABO | CHARTRES | WMLK | WATER LEAK -MAIN. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A251825 SN: 0081292, *TAP: SIZE: A LOC: 108 FEET FROM P LINE AT DOUGLASS, *MB: CODE: BL7 LOC: ON ALABO 108FT FROM PL DOUGLAS ****/ | 2018-11-07 | MADE 8 X 8 CUT IN DOUBLE LAYER OF BLACK TOP STREET AND MADE REPAIRS ON 3/4 INCH TAILPIECE ON 6 INCH WATER MAIN BACKFILLED AREA
201801826001 | 2018-10-17 | LEAD | 1016 | KERLEREC | N RAMPART | WILK | ML-METER LEAK ACCT#112015-485827 METER#A281686 BAD BLEEDER VALVE PASSING IN ON POSITION /** 1) MN: A281686 SN: 0015293, *TAP: SIZE: A LOC: 115 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CFL LOC: ON KERLEREC 115FT FROM BURGUNDY ****/ | 2018-10-29 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER COCK TO STOPLEAK BACKFILLED AND CLEANED THE AREA
201801826101 | 2018-10-17 | LEAD | 1029 | BARRACKS |  | WILK | ML- METER LEAK METER #A277407 ACCT # 104922-529372 ***FLOODING AREA*** INLET SERVICE LEAK IN BOX /** 1) MN: A277407 SN: 0074053, *TAP: SIZE: A LOC: 101 FEET FROM P LINE AT RAMPART N, *MB: CODE: AEK4 LOC: ON BARRACKS 99 FT FROM N RAMPART ST PL. ****/ | 2018-10-25 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801826301 | 2018-10-17 | LEAD | 5765 | DAUPHINE | ALABO | WOLK | WATER LEAK -OUTLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. **LEAK IS ON ALABO*** /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-10-30 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA NO METER JOB COMPLETE
201801826901 | 2018-10-17 | LEAD | 919 | LAMANCHE | BURGUNDY | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-10-29 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK FOR ABANDON LOTBACKFILLED AREA. JOB COMPLETE
201801827101 | 2018-10-17 | LEAD | 1035 | LAMANCHE | ST CLAUDE AV | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A253580 SN: 0079937, *TAP: SIZE: A LOC: 274 FEET FROM P LINE AT RAMPART N, *MB: CODE: AD LOC: CURB LS 274FT FROM PL N RAMPART ****/ | 2018-11-01 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK FOR ABANDON LOT BACKFILLED AREA
201801827801 | 2018-10-17 | LEAD | 5700 | N CLAIBORNE AV | LAMANCHE | WMLK | WATER LEAK -MAIN. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A125468 SN: 0115843, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT NO. CLAIBORNE AVE., *MB: CODE: CEH LOC: ON LAMANCHE, 48' FROM P.L. NO. CLAIBORNE AVE.,2.5' ****/ | 2018-11-01 | MADE 2 X 6 CUT IN OLD SIDEWALK WITH LIMESTONE AND MADE REPAIRS ON 3/4 INCH TAILPIECE FOR ABANDON LOT BACKFILLED AREA
201801831701 | 2018-10-17 | LEAD | 2126-28 | PIETY | N MIRO | WMTLK | ML-METER LEAK METER#A419148 ACCT#305988 VACANT EXAMINE INLET/OUTLET SERVICE FOR LEAK ON SIDEWALK METER BOX UNDER WATER FLOODING SIDEWALK /** AT 2126: 1) MN: A219840 SN: 0168752, *TAP: SIZE: B LOC: 78 FEET FROM P LINE AT NO. MIRO, *MB: CODE: OOO LOC: ON PIETY, 113' FROM P.L. NO. MIRO, 1' OUTSIDE, 11' ** AT 2128: 2) MN: A305622 SN: 0168752, *TAP: SIZE: B LOC: 113 FEET FROM P LINE AT NO. MIRO, *MB: CODE: __ LOC: ON PIETY, 112' FROM P.L. NO. MIRO, 1' OUTSIDE, 11' ****/ | 2018-10-31 | REPLACED 5/8 INCH HANDWHEEL + GUTS AT ABOVE LOCATION ACTUAL LEAK IS AT 2127 PIETY ST
201801834502 | 2018-10-18 | LEAD | 3707 | DELGADO DR | WILSON DR | WILK | REROUTE INLET SERVICE /** 1) MN: A323708 SN: 0070055, *TAP: SIZE: B LOC: 62 FEET FROM P LINE AT ST MARKS CT, *MB: CODE: BDM2 LOC: ON DELGADO DR 62' FROM PL ST MARKS CT ****/ | 2018-10-29 | EXCAVATED 3 X 3 MUD PLOT MADE REPAIR ON 3/4 INCH LEAD LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801835101 | 2018-10-18 | LEAD/PLASTIC | 4004 | VIRGIL BL | PARIS AV | WILK | ML METER LEAK ACCT# 165639-496993 METER# B035935 INLET SERVICE LEAK IN DRIVEWAY CUSTOMER STATES THAT ALGAE IS STARTING TO DEVELOP IN DRIVEWAY , ITS BECOME A SLIP-HAZARD TO AREA. (CG) 11/07 11/16/18 LEAK CAUSING POOR PRESSURE PER SERVICE REQUEST #12857961 (FCP) /** 1) MN: B013770 SN: 0106419, *TAP: SIZE: B LOC: 400 FEET FROM P LINE AT PARIS AVE, *MB: CODE: ADM2 LOC: ON VIRGIL BLVD 400' FROM PL PARIS AVE 11' OUTSIDE ****/ | 2018-11-15 | EXCAVATED 4 X 4 MUDPLOT IN SIDWALK . LOCATED LEAK ON INLET SERVICE. REPLACED 3/4 STOP COCK ON INLET. METER WAS RAISED TO GRADE. ALSO LEAD LOCATED ON INLET SERVICE.
201801835701 | 2018-10-18 | LEAD | 6433 | N MIRO | DELERY | WILK | MI- LEAK IN THE STREET EXAMINE INLET ON ABANDON SERVICE INFRONT VACNT LOT FOR LEAK /** 1) MN: A133269 SN: 0152342, *TAP: SIZE: B LOC: 258 FEET FROM P LINE AT DELERY, *MB: CODE: CDM1 LOC: RES ON N MIRO 258' P/L DELERY 8' OUTSIDE 2' INSIDE ****/ | 2018-11-09 | MADE 8 X 8 CUT IN BLACK TOP STREET AND FOUND LEAK WAS IN ANOTHER LOCATION MADE 8 X 8 CUT FATHER BACK IN BLACK TOP STREET AND MADE REPAIRS ON 3/4 INCH TAILPIECE FOR ABANDON LOT BACKFILLED AREA
201801835901 | 2018-10-18 | LEAD | 2301 | ST CLAUDE AV |  | WMBK | LOCATION: 108699 PER INSP DJ - UNABLE TO SET METER, VALVE NOT LINING UP. PLEASE REPAIR AND SET A 5/8 METER. UNDER CONSTRUCTION INLET AND OUTLET NOT LINING UP, ALSO SET 5/8 METER HOUSE UNDER CONSTRUCTION 10/26/18 PER S/R 12855827 LEAK IN THE SIDEWALK, PER INSP K GRIFFIN FOUND METER IN BOX, REPAIRS HAS NOT BEEN MADE YET /** 1) MN: B024179 SN: 0054450, *TAP: SIZE: B LOC: 62 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: CDLM LOC: SIDE ST LS DR C 62' P.L. ST CLAUDE AV ****/ | 2018-10-30 | EXCAVATED 4 X 3 SIDEWALK CUT REPLACE 3/4 INCH METER BOTTOM SET METER WITH WASHERS BACKFILLED AND CLEANED THE AREA
201801836401 | 2018-10-18 | LEAD | 1476-78 | N GALVEZ | COLUMBUS | WMRE | ML- METER LEAK METER# B042761 ACCT# 130360-524161 LOCATE/RAISE METER TO PROPER GRADE /** AT 1476: 1) MN: B033214 SN: 0060053, *TAP: SIZE: B LOC: 86 FEET FROM P LINE AT GALVEZ N, *MB: CODE: BDH LOC: RES FRONT OF 2024 COLUMBUS 84FT FROM PL GALVEZ ****/ | 2018-11-01 | EXAMINED AND FOUND NO LEAK ALSO METER BOX MARKED WITH BLUE PAINT
201801836501 | 2018-10-18 | LEAD | 501 | N SALCEDO | LAFITTE | WILK | ML- METER LEAK ACCT# 306017-428447 MTR# A417551 INLET SERVICE LEAK CUSTOMMER ROLLING OVER METER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-02 | EXCAVATED AND RELOCATED METER BOX INTO SIDEWALK BACKFILL JOB WITH RIVERSAND AND COLDMILL RENEW OUTLET SERVICE FROM METER BOX TO PROPERTY
201801837301 | 2018-10-18 | LEAD/PLASTIC | 73 | ALLARD BL | DUMAINE | WILK | ML-METER LEAK METER#A415947 ACCT#103317-514583 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A267357 SN: 0012696, *TAP: SIZE: B LOC: 260 FEET FROM P LINE AT DUMAINE, *MB: CODE: __ LOC: ON ALLARD BL 260FT FROM USPL OF DUMAINE ****/ | 2018-11-02 | EXCAVATED A 3 X 4 MUD CUT AND MADE REPAIRS ON THE INLET SERVICE. LEAD ON THE INLET SEVICE AND PLASTIC ON THE OLTLET SERVICE. BACKFILL AND CLEAN UP
201801839001 | 2018-10-19 | LEAD | 2411 | MEMORIAL PARK DR | ARIZONA | WMTLK | ML : METER LEAK ACCT#235463-411295 METER# A420752 EXAMINE INLET AND OUTLET SERVICE FOR LEAK INSIDE BOX IN MUDPLOT /** 1) MN: A322989 SN: 0162191, *TAP: SIZE: B LOC: 357 FEET FROM P LINE AT ARIZONA, *MB: CODE: AFK2 LOC: ON MEMORIAL 358FT FROM PL ARIZONA ****/ | 2018-11-03 | ARRIVED ON JOB SITE EXAMINED LEAK EXCAVATED IN MUD PLOT BY HAND MADE REPAIR SERVICE BACKFILLED DRESS UP WORK SITE. JOB COMPLETE
201801840701 | 2018-10-19 | LEAD | 3416 | N VILLERE |  | WMRE | LOCATION: 306178 PER INSP UDEBOR - METER BOX BURIED. PLEASE LOCATE AND SET A 5/8 METER. HOUSE UNDER CONST & VACANT LOCATE, RAISE TO GRADE AND SET 5/8 METER /** 1) MN: SN: 0066972, *TAP: SIZE: A LOC: 106 FEET FROM P LINE AT DESIRE, *MB: CODE: CEK2 LOC: ****/ | 2018-10-31 | EXCAVATED IN MUD PLOT + LOCATED 5/8 INCH METER BOX RAISED TO GRADE + SET 5/8 INCH WATER METER BACKFILLED +DRESSED UP AREA
201801841301 | 2018-10-19 | LEAD | 3337 | ST ANN | HAGAN AV | WMTLK | ML-METER LEAK ACCT#143346-520484 METER#A425923 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: A268798 SN: 0026730, *TAP: SIZE: B LOC: 284 FEET FROM P LINE AT HAGAN AVE, *MB: CODE: CDLM LOC: HAGAN/MOSS METER ON ST ANN 284 FT FROM PL N HAGAN ****/ | 2018-11-02 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201801842401 | 2018-10-19 | LEAD | 2507 | PRYTANIA | 2ND | WILK | WM- LEAK IN STREET INLET SERVICE LEAK ON ABANDON SERVICE NO METER IN BOX /** 1) MN: B025834 SN: 0014190, *TAP: SIZE: B LOC: 119 FEET FROM P LINE AT PRYTANIA, *MB: CODE: BDHK LOC: ON 2ND 119FT FROM PRYTANIA ****/ | 2018-11-04 | MADE 3X5 CUTIN SIDEWALK OVER INLET SERVICE ,CHANGED 5/8 METER BOX COCK.
201801843601 | 2018-10-19 | LEAD | 515 | N RENDON | TOULOUSE | WILK | ML-METER LEAK ACCT#113924-520119 METER#A284946 INLET SERVICE LEAK NSIDE METER BOX /** 1) MN: A277116 SN: 0051197, *TAP: SIZE: B LOC: 115 FEET FROM P LINE AT TOULOUSE, *MB: CODE: CDLN LOC: USPL TOULOUSE ****/ | 2018-11-02 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE IN MUD PLOT BACKFILLED JOB WITH RIVERSAND
201801845301 | 2018-10-20 | LEAD | 1955 | N TONTI | ALLEN | WMTLK | ML- METER LEAK ACCT# 165336-494241 MTR# A328937 EXAMINE INLET/OUTLET SERVICE FOR LEAK IN MUDPLOT ALSO REPLACE METER BOX CASING /** 1) MN: A119483 SN: 0105530, *TAP: SIZE: A LOC: 145 FEET FROM P LINE AT ALLEN, *MB: CODE: BDK LOC: 145FT FROM PL ALLEN 7.5' OUTSIDE PL ****/ | 2018-10-28 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO MAKE THE REPAIR
201801846501 | 2018-10-21 | LEAD | 1510 | N DORGENOIS | COLUMBUS | WMTLK | LOCATIONID#118243-489237 METER#A389575 LEAK INSIDE METERBOX /** 1) MN: A297473 SN: 0043917, *TAP: SIZE: A LOC: 84 FEET FROM P LINE AT COLUMBUS, *MB: CODE: BFM LOC: INSIDE 84' P.L. COLUMBUS ****/ | 2018-11-01 | REMOVE DEBRIS OUT OF METER BOX AND FOUND NO LEAK
201801847301 | 2018-10-21 | LEAD | 2801 | MANSFIELD AV |  | WMTLK | LOCATIONID#233526-418999 METER#A415373 LEAK INSIDE METERBOX /** 1) MN: A253453 SN: 0150725, *TAP: SIZE: B LOC: 17 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: CDN2 LOC: ON MANSFIELD 200FT FROM GEN MEYER 10FT OUTSIDE ****/ | 2018-11-04 | ARRIVED ON JOB SITE EXAMINE LEAK IN MUD PLOT EXCAVATED IN MUD PLOT BY HAND MADE REPAIRS ON INLET SERVICE BACKFILLED DRESSED UP WORK SITE
201801847901 | 2018-10-21 | LEAD | 2439 | COLUMBUS |  | WMTLK | LOCATIONID#127159-489325 METER#A400264 LEAK INSIDE METERBOX /** 1) MN: A299051 SN: 0051663, *TAP: SIZE: A LOC: 108 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: ADK2 LOC: ON COLUMBUS,109' FROM L.R.P.L. NO. DORGENOIS ****/ | 2018-11-09 | REPLACE INLET AND OUTLET WASHERS AT ABOVE LOCATION
201801848401 | 2018-10-22 | LEAD | 705 | AURORA DR | NEIL AV | WMTLK | LOCATIONID#226540-419555 METER#A420681 LEAK INSIDE METERBOX /** 1) MN: A193464 SN: 0146324, *TAP: SIZE: C LOC: 98 FEET FROM P LINE AT NEIL AVE, *MB: CODE: BFM LOC: ON AURORA 98FT FROM NEIL 4FT OUTSIDE ****/ | 2018-11-10 | WE EXCAVATED TO MAKE REPAIRS TO A 5/8 INCH BOX COCK WE BACKFILLED PLUS CLEAN UP BY HAND IN TREE ROOTS AN A 5/8 INCH METER BOX COMPLETE
201801848701 | 2018-10-22 | LEAD | 1835 | ALLEN | N PRIEUR | WILK | LOCATIONID#114185-547404 METER#A378707 BLEEDER LEAK /** 1) MN: A299308 SN: 0071910, *TAP: SIZE: A LOC: 87 FEET FROM P LINE AT PRIEUR N, *MB: CODE: CFK LOC: ON ALLEN 87' FROM LRPL N PRIEUR ****/ | 2018-11-05 | EXCAVATED IN SIDEWALK + MADE REPAIRS ON 5/8 INLET SERVICE BACKFILLED JOB WITH RIVERSAND COLDMILL RAISE METER BOX TO GRADE
201801849301 | 2018-10-22 | LEAD/PLASTIC | 4326 | CLEVELAND AV | S ALEXANDER | WILK | WM-LEAK IN CURB INLET SERVICE LEAK IN THE STREET FLOODING THE CURB /** 1) MN: A253927 SN: 0082544, *TAP: SIZE: Y LOC: 193 FEET FROM P LINE AT HENNESSEY S, *MB: CODE: CDV LOC: 193FT FROM HENNESSEY 10FT OUTSD PL 3.5' INSIDE CUR ****/ | 2018-10-26 | MADE A 2 X 2 ASPHALT STREET CUT & A 4 X 8 MUD CUT EXCAVATED AND MADE REPAIRS ON A 1 1/2 X 3/4 CONTROLING MAIN SERVICE IN LET. LEAD TO PLASTIC
201801850301 | 2018-10-22 | LEAD | 4254 | DALE | CHEF MENTEUR HW | WILK | MI- LEAK IN THE STREET INLET SERVICE LEAK IN MUDPLOT FLOODING SIDEWALK /** 1) MN: A317716 SN: 0130272, *TAP: SIZE: A LOC: 85 FEET FROM P LINE AT WARFIELD, *MB: CODE: BDKO LOC: RES ON DALE 85FT PL WARFIELD 7' OUTSIDE ****/ | 2018-11-26 | MADE A 4X3 CUT IN SIDEWALK. EXCAVATED DOWN ON INLET AND OUTLET SERVICES. FOUND LEAD AND METER COCK WAS LEAKING ALSO SERVICE WAS FOR ABANDON LOT NEXT DOOR. MADE REPAIRS. BY REPLACING 2FT OF INLET AND METER COCK. NO METER ABANDON LOT BACKFILLED.
201801851101 | 2018-10-22 | LEAD | 1929 | FORSTALL |  | WILK | LEAK BETWEEN SIDEWALK AND STREET **********J GILLIAM 11:21 INLET SERVICE LEAK ON ABANDON SERVICE WATER SHOOTING IN THE AIR /** 1) MN: A265523 SN: 0151287, *TAP: SIZE: B LOC: 155 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CEK LOC: ON FORSTALL 149FT FROM PL N JOHNSON 10FT OUTSIDE ****/ | 2018-10-22 | EXCAVATED AND MADE REPAIR ON 3/4 INCHABANDON INLET SERVICE BACKFILLED JOB WITH RIVERSAND. JOB COMPLETE
201801853601 | 2018-10-22 | LEAD | 3146 | N CLAIBORNE AV | CLOUET | WMTLK | WM LEAK IN SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** 1) MN: A266250 SN: 0097081, *TAP: SIZE: B LOC: 330 FEET FROM P LINE AT CLOUET, *MB: CODE: BD LOC: 367' FROM PL CLOUET 9' OUTSIDE PL 1' INSIDE CURB ****/ | 2018-11-12 | PUMPED DOWN METER BOX + REMOVED JUMPER FROM METER BOX THAT WAS CAUSING LEAK. NO METER (JOB COMPLETE)
201801853801 | 2018-10-22 | LEAD | 2344 | MAZANT | N ROCHEBLAVE | WILK | MI - LEAK AT THE CURB INLET SERVICE LEAK ON ABANDON SERVICE INFRONT VACANT LOT /** 1) MN: SN: 0099675, *TAP: SIZE: B LOC: 36 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: ADM LOC: ON MAZANT, 30' FROM P.L. NO. ROCHEBLAVE,7.5' OUT- ****/ | 2018-11-05 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA. JOB COMPLETE
201801854701 | 2018-10-22 | LEAD | 4114-16 | GEN PERSHING | S BERNADOTTE | WMTLK | MI -LEAK IN STREET EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER, FLOODING AREA INFRONT VACANT LOT ***NOT THE SAME AS 4118 GEN PERSHING*** /** AT 4116: 1) MN: A113523 SN: 0064115, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT DUPRE N, *MB: CODE: AFM LOC: ON GENL PERSHING 113' FROM USPL DUPRE 1' OUTSIDE ****/ | 2018-10-29 | EXCAVTED IN MUDPLOT OVER INLET SERVICE.REPLACED 5/8 METER BOX COCK.NO METER INSIDE BOX.
201801854901 | 2018-10-22 | LEAD | 2126 | PIETY | N MIRO | WMTLK | MI- LEAK BETWEEN THE STREET AND THE SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK BOTH METERS UNDER WATER /** 1) MN: A219840 SN: 0168752, *TAP: SIZE: B LOC: 78 FEET FROM P LINE AT NO. MIRO, *MB: CODE: OOO LOC: ON PIETY, 113' FROM P.L. NO. MIRO, 1' OUTSIDE, 11' ****/ | 2018-10-31 | STOPPED LEAK ON METER BY TIGHTENING METER AFTER CHANGING WASHERS
201801855001 | 2018-10-22 | LEAD | 3319 | BELL | HAGAN AV | WILK | WM-LEAK IN THE STREET BETWEEN METER AND STREET INLET SERVICE LEAK INSIDE METER BOX IN THE MUD PLOT /** 1) MN: A236132 SN: 0059699, *TAP: SIZE: A LOC: 119 FEET FROM P LINE AT HAGAN AVE, *MB: CODE: BD LOC: ON BELL 120.5FT FROM PL OF HAGAN AVE ****/ | 2018-11-01 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801857101 | 2018-10-22 | LEAD | 1416 | FRANKLIN AV | N VILLERE | WILK | ML-METER LEAK ACCT# 116708-481692 METER# A336588 BAD BLEEDER VALVE CAUSING METER BOX TO OVERFLOW /** 1) MN: A302461 SN: 0022626, *TAP: SIZE: A LOC: 92 FEET FROM P LINE AT VILLERE N, *MB: CODE: CEM1 LOC: 145FT FROM USPL N VILLERE ****/ | 2018-11-06 | EXCAVATED + MADE REPAIRS ON 5/8 INCH INLET SERVICE IN SIDEWALK BACKFILLED JOB WITH RIVERSAND + COLDMILL
201801858901 | 2018-10-22 | LEAD | 622 | BARRACKS |  | WILK | WM- LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET IN FRONT OF ABOVE ADDRESS 10/26/18 CALLER STATED PROBLEM HAS GOTTEN WORSE (KSW) /** 1) MN: A221533 SN: 0030239, *TAP: SIZE: A LOC: 153 FEET FROM P LINE AT CHARTRES, *MB: CODE: CFL LOC: RES 154' P.L. CHARTRES ****/ | 2019-08-15 | EXCAVATED IN CONCRETE STREET + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE ALSO MADE REPAIR ON 10 DRAIN LINE COMPACTED BACKFILL + DRESSED UP AREA
201801859301 | 2018-10-22 | LEAD/PLASTIC | 2807 | CALHOUN | BARRETT | WILK | WM LEAK IN THE STREET INLET SERVICE LEAK IN CONCRETE STREET FLOODING STREET **CHANGED FROM 2808 CALHOUN** 10/31/18 CUSTOMER STATES LEAK HAS GOTTEN WORSE FLOODING HER LAWN (NLD) /** 1) MN: A267090 SN: 0063342, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT BARRETT, *MB: CODE: ADN2 LOC: ON CALHOUN ST 72.3' FROM LSPL BARRETT ST ****/ | 2018-11-04 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 3/4 SERVICE LEAKING,REPLACED 21 FT. OF 3/4 TUBING TIED INTO LEAD. OLD METER INFO: A386864 FACT: 74972482 MAKE: SENSUS READ: UNABLE TO READ
201801861001 | 2018-10-23 | LEAD | 3042 | ST ANN |  | WMRE | INSP L UDUEBOR STATES SERVICE IS BURIED. PLEASE RAISE TO GRADE ANDCHANGE METER A380349. LOC ID 203379 LOCATE MARK AND BRING METER TO GRADE /** 1) MN: A121313 SN: 0022007, *TAP: SIZE: A LOC: 42 FEET FROM P LINE AT SALCEDO N, *MB: CODE: CFLM LOC: ON ST ANN 41.7' FROM USPL SALCEDO ****/ | 2018-11-28 | EXCVATED 2 X 2 SIDEWALK CUT RAISED METER BOX TO GRADE BACKFILLED AND CLEANED THE AREA
201801862901 | 2018-10-23 | LEAD | 2627 | S ROBERTSON | THIRD | WMTLK | ML- METER LEAK METER#A392144 ACCT# 173249-590115 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER, GRASSY AREA FLOODED /** 1) MN: 000000 SN: 0156574, *TAP: SIZE: A LOC: 213 FEET FROM P LINE AT THIRD, *MB: CODE: CDLM LOC: ON S ROBERTSON 213' P/L 3RD ST 6' OUTSIDE ****/ | 2018-10-30 | CHANGED 5/8 METER BOX COCK .REPLACED METER OLD METER WAS CHOKED. **************OLD METER INFO********** METER:A392144 FAC:74979162 MAKE:SENSUS READ:39810
201801863801 | 2018-10-23 | LEAD | 1433 | TENNESSEE | N ROBERTSON | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A126332 SN: 0107284, *TAP: SIZE: A LOC: 132 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: ADL LOC: ON TENNESSEE, 132' FROM P.L. NO. ROBERTSON, 9' OUT ****/ | 2018-11-07 | EXAMINED JOB AT ABOVE LOCATION FOUND NO LEAK ON INLET OR OUTLET
201801864001 | 2018-10-23 | LEAD | 1201 | TUPELO | MARAIS | WMLK | WATER LEAK -MAIN. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A345164 SN: 0090839, *TAP: SIZE: A LOC: 20 FEET FROM P LINE AT MARAIS, *MB: CODE: CD LOC: ON TUPELO 20FT FROM MARAIS 8FT OUTSIDE ****/ | 2018-11-13 | MADE 2 X 2 CUT IN SIDEWALK AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201801864401 | 2018-10-23 | LEAD | 5436 | MARAIS | FLOOD | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A255143 SN: 0075416, *TAP: SIZE: A LOC: 183 FEET FROM P LINE AT FLOOD, *MB: CODE: DK LOC: ON MARAIS, 183' FROM U.R.P.L. FLOOD,3' FROM CURB ****/ | 2018-11-01 | MADE 4 X 6 CUT IN BLACK TOP STREET AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED AREA. JOB COMPLETE
201801864501 | 2018-10-23 | LEAD | 4803 | DIXON | S GENOIS | WMTLK | ML-METER LEAK EXAMINE INLET AND OUTLET SERVICE INSIDE METER BOX IN MUDPLOT FOR A LEAK /** 1) MN: A256171 SN: 0091180, *TAP: SIZE: A LOC: 43 FEET FROM P LINE AT DIXON, *MB: CODE: BDHM LOC: ON S. GENOIS,43' FROM P.L. DIXON,8' OUTSIDE P.L., ****/ | 2018-11-01 | EXCVATED IN MUDPLOT OVER 5/8 INLET SERVICE .CHANGED 5/8 METER BOX CURB COCK.
201801864701 | 2018-10-23 | LEAD | 841 | WILSON DR | DUMAINE | WILK | ML- METER LEAK METER # A421636 ACCT # 141262-514237 ***FLOODING AREA**** INLET SERVICE LEAK IN MUDPLOT HOLE IS EXPOSE ALSO LEAKING ON WHITE JOINT OF LEAD /** 1) MN: A193170 SN: 0072469, *TAP: SIZE: B LOC: 288 FEET FROM P LINE AT DUMAINE, *MB: CODE: ADL2 LOC: ON WILSON DR., 288' FROM P.L. DUMAINE ****/ | 2018-11-08 | EXCAVATED IN TREE ROOTS AND MADE REPAIR ON 5/8 INCH OUTLET SERVICE BACKFILLED JOB WITH RIVERSAND RAISE TO GRADE
201801865001 | 2018-10-23 | LEAD | 3330 | LOYOLA AV | LOUISIANA AV | WILK | WM-LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-04 | MADEE 3 X 5 CUT IN SIDEWALK OVER 5/8 INLET SERVICE CHNAGED METER BOX CURB COCK .BACKFILLED LEFT ACONE ON CUT COCDMILL IS SOFT.
201801866001 | 2018-10-24 | LEAD | 928 | JACKSON AV |  | WMTLK | LOCATIONID#301163-700066 METER#A425112 LEAK INSIDE METERBOX /** 1) MN: A317635 SN: 0078444, *TAP: SIZE: A LOC: 208 FEET FROM P LINE AT LAUREL, *MB: CODE: BG LOC: IN LINE WITH S AND W ON JACKSON AVE 209.5 FT FROM ****/ | 2018-11-03 | WE ARRIVED AND FOUND A 5/8 INCH WASHERS WAS LEAKING WE REPLACE IT WITH A NEW ONE
201801866101 | 2018-10-24 | LEAD | 2417 | TUPELO |  | WMTLK | LOCATIONID#173317-426119 METER#A424812 LEAK INSIDE METERBOX /** 1) MN: SN: 0135229, *TAP: SIZE: A LOC: 142 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: ADL2 LOC: ON TUPELO 143FT FROM PL ROCHEBLAVE N 8FT OUTSIDE ****/ | 2018-11-07 | REPLACE BOTH INLT + OUTLET WASHERS AT ABOVE LOCATION
201801866601 | 2018-10-24 | LEAD/PLASTIC | 5202 | COLISEUM |  | WMTLK | LOCATIONID#101275-585911 METER#A380550 METER LEAK,AREA FLOODED /** 1) MN: A250547 SN: 0006305, *TAP: SIZE: A LOC: 89 FEET FROM P LINE AT COLISEUM, *MB: CODE: AD LOC: ON DUFOSSAT 90' FROM U.R.P.L. COLISEUM ****/ | 2018-11-03 | EXCAVATED IN GUTTER BOTTOM OVER INLET SERVICE.CHANGED METER BOX COCKS AND RAISED METER TO GRADE.BACKFILLED AND CLEANED JOB SITE.
201801866701 | 2018-10-24 | LEAD/PLASTIC | 1631 | ORETHA CASTLE HALEY BL | EUTERPE | WOLK | WOLK WATER LEAK- OUTLET SERVICE /** 1) MN: A307568 SN: 0039548, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT DRYADES, *MB: CODE: AEHK LOC: METER ON SIDE ST ON EUTERPE 82' P.L. DRYADES ****/ | 2018-10-23 | EXAMINE JOB FOUND METER BOX COCK LEAKING MADE REPAIRS AND BACKFILL.
201801869101 | 2018-10-24 | LEAD | 342 | S CORTEZ | BANKS | WMTLK | MI- LEAK ON THE SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK INSIDE METER BOX FLOODING SIDEWALK & STREET /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-01 | EXCAVTED IN MUDPLOT OVER 5/8 INLET SERVICE.REPLACED 5/8 METER BOX COCK,ALSO CHANGED OLD METER WAS CHOKED.
201801869401 | 2018-10-24 | LEAD | 2265 | N GALVEZ | MANDEVILLE | WILK | MI-LEAK IN THE STREET EXAMINE INLET SERVICE FOR LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-20 | REPLACED 5/8 INCH WASHERS TO STOP LEAK
201801869501 | 2018-10-24 | LEAD | 1422 | MARIGNY | N ROBERTSON | WOLK | ML METERLEAK MTR#A276464 LOC/CUST#112354-487105 CONS REG ON METER. /** 1) MN: A236520 SN: 0014187, *TAP: SIZE: A LOC: 141 FEET FROM P LINE AT ROBERTSON S, *MB: CODE: CDEM LOC: 141FT FROM URPL ROBERTSON ON MARIGNY ****/ | 2018-11-08 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201801870501 | 2018-10-24 | LEAD | 1422 | N PRIEUR |  | WOLK | LOCATION ID-114519 MTR-A358169 UNDERGROUND LEAK BETWEEN MTR AND STOP & WASTE/MTR OFF/CONS REG ON MTR EXAMINE OUTLET SERVICE FOR A LEAK @ PROPERTY LINE FOUND METER OFF LEFT METER OFF ***HOUSE VACANT*** /** 1) MN: A248634 SN: 0017034, *TAP: SIZE: A LOC: 132 FEET FROM P LINE AT KERLEREC, *MB: CODE: CDM LOC: ON PRIEUR 131.5FT FROM KERLEREC ****/ | 2018-11-01 | EXCAVATED 3 X 2 MUD PLOT REPLACED 5/9 ICH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801871401 | 2018-10-24 | LEAD | 5232 | ANNUNCIATION |  | WMRE | INSP L UDUEBOR STATES SERVICE IS BURIED AND LOCATION IS COVERED WITH ROCKS. PLEASE RAISE TO GRADE AND CHANGE METER A268899. LOC ID 197477 LOCATE/RAISE/CHANGE 5/8 METER /** 1) MN: A268899 SN: 0054634, *TAP: SIZE: B LOC: 77 FEET FROM P LINE AT BELLECASTLE, *MB: CODE: CF LOC: ON ANNUNCIATION 47FT PL BELLECASTLE 2' OUTSIDE ****/ DOTTIE READT 12-5-18 EXP 12-25-18 | 2019-01-06 | EXCAVATED AND REMOVED METER BOX FROM FLOWER GARDEN PLACED WATER METER BOX IN SIDEWALK METER WAS COVER BY FLOWERS AND BUSHES ALSO REPLACED WATER METER OLD METER INFO: A268899 FACT: 39732867 MAKE: ROCKWELL READ: 9080
201801873301 | 2018-10-25 | LEAD | 1130 | REYNES |  | WMTLK | LOCATIONID#301233-704256 METER#A425493 LEAK INSIDE METERBOX /** 1) MN: A261309 SN: 0103801, *TAP: SIZE: A LOC: 23 FEET FROM P LINE AT MARAIS, *MB: CODE: ADK LOC: ON REYNES, 121' FROM P.L. MARAIS ****/ | 2018-11-05 | EXCAVATED IN MUD PLOT MADE REPAIRS ON 3/4 INCH SERVICE BACKFILLED AREA
201801873501 | 2018-10-25 | LEAD | 405 | ESPLANADE AV |  | WOLK | ML METERLEAK MTR#E004108 LOC/CUST#204992-600801 CONS REG ON MTER. /** 1) MN: H001359 SN: 0000000, *TAP: SIZE: H LOC: 52 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: OOO LOC: ON N. PETERS 45FT FROM PL ESPLANADE AVE 19FT OUT- ** 2) MN: E004108 SN: 0165660, *TAP: SIZE: E LOC: 52 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: __ LOC: IN MH ON N. PETERS 34FT. FROM PL ESPLANADE AVE 4FT ****/ | 2018-11-05 | EXAMINED + FOUND NO LEAK OR CONSTANT REQISTRATION
201801874501 | 2018-10-25 | LEAD | 1037 | KERLEREC | N RAMPART | WILK | ***********PICKUP JOB************ ********CUSTOMER OUT OF WATER********* J GILLIAM @ 11:45AM INLET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-10-26 | MADE A 6 X 22 CUT AT ABOVE LOCATION + REPLACED 25 FT OF 3/4 INCH INLET SERVIC LINE RESTORING WATER TO ABOVE LOCATION COMPACTED BACKFILLED + DRESSED UP AREA ALSO REPLACED DAMAGED 5/8 INCH WATER METER
201801875201 | 2018-10-25 | LEAD | 2218 | JACKSON AV |  | WMTLK | LOCATIONID#124944-714969 METER#A395533 LEAK INSIDE METERBOX /** 1) MN: A245352 SN: 0046943, *TAP: SIZE: A LOC: 119 FEET FROM P LINE AT LASALLE, *MB: CODE: ADKW LOC: ON JACKSON AVE.,120.5' FROM R.P.L. LASALLE ****/ | 2018-11-01 | EXCAVATED OVER OUTLET SERVICE,CHANGED 5/8 HANDWHEEL SET UPPER CASING THE RIGHT WAY AND RAISED TO GRADE.
201801875301 | 2018-10-25 | LEAD | 5310 | DAUPHINE |  | WMTLK | LOCATIONID#209529-425145 METER#A416825 LEAK INSIDE METERBOX /** 1) MN: A303272 SN: 0170254, *TAP: SIZE: B LOC: 32 FEET FROM P LINE AT EGANIA, *MB: CODE: CD LOC: ON DAUPHINE 33' FROM DIV. P.L. EGANIA 2'OUTSIDE ****/ | 2018-11-07 | EXCAVATED AND MADE REPAIR ON INLET SERVICE IN MUD PLOT BACKFILLED JOB WITH RIVERSAND
201801875401 | 2018-10-25 | LEAD | 3400 | ST CLAUDE AV |  | WILK | LOCATIONID#197712-428043 METER#E008338 BLEEDER LEAK /** 1) MN: E003759 SN: 0017248, *TAP: SIZE: E LOC: 69 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: CDHN LOC: ON DESIRE 53' PL ST CLAUDE AV 3' OUTSIDE 3' INSIDE ** 2) MN: SN: 0017248, *TAP: SIZE: A LOC: 18 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: __ LOC: SIDE ST /DESIRE 18 FT FROM PL ST CLAUDE AVE ****/ | 2018-11-07 | PUMPED DOWN MANHOLE + REPLACED 2 INCH UNION ON INLET SIDE IN MANHOLE AT ABOVE LOCATION
201801875901 | 2018-10-25 | LEAD/PLASTIC | 2730 | PRANCER | VIXEN | WOLK | METER # A289799 LOCATION # 229832-409686 CONS REGISTRATION /** 1) MN: A289799 SN: 0132635, *TAP: SIZE: B LOC: 94 FEET FROM P LINE AT VIXEN, *MB: CODE: __ LOC: ON PRANCER 94' FROM PL VIXEN 7' OUTSIDE PL 4' INSI ****/ | 2018-11-27 | EXAMINED AREA EXCAVATED ON INLET AND OUTLET SERVICE TRACED LINE TO PROPERTY OBSERVED NO LEAK RENEWED OUTLET SERVICE LEAD LINE ON INLET OBSERVED RAISE TO GRADE BACKFILLED AND CLEANED AREA
201801876001 | 2018-10-25 | LEAD | 1937 | LIZARDI | PRIEUR | WOLK | ML- METER LEAK METER #A288129 ACCT #181766-424177 OUTLET SERVICE LEAK WITH CONSTAT REG /** 1) MN: B033100 SN: 0130226, *TAP: SIZE: B LOC: 260 FEET FROM P LINE AT NO. PRIEUR, *MB: CODE: BEK LOC: ON LIZARDI, 261' FROM P.L. NO. PRIEUR, 7' OUTSIDE ****/ | 2018-11-07 | EXCAVATED AND MADE REPAIRS ON 3/4 INCH OUTLET SERVICE BACKFILL JOB WITH RIVERSAND CODLMILL IN SIDEWALK
201801876401 | 2018-10-25 | LEAD | 2095 | LAW |  | WMRE | INSP D JOHNSON STATES HE IS UNABLE TO LOCATE SERVICE TO SET METER. PLEASE LOCATE AND SET 5/8 METER. LOC ID 306268. LOCATE AND RAISE AND BRING TO GRADE AND SET 5/8 METER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-05 | EXCAVATED IN MUD PLOT + LOCATED 5/8 INCH METER BOX RAISED METER BOX TO GRADE + SET 5/8 INCH METER BACKFILLED + DRESSED UP AREA
201801876901 | 2018-10-25 | LEAD | 3020 | BIENVILLE | N GAYOSO | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: SN: 0046352, *TAP: SIZE: A LOC: 176 FEET FROM P LINE AT GAYOSO N, *MB: CODE: AFL LOC: ON BIENVILLE 174FT FROM PL GAYOSO N 2' OUTSIDE PL ****/ | 2018-11-01 | REPLACED 5/8 INCH WASHERS TO STOP LEAK
201801877701 | 2018-10-25 | LEAD | 4753 | HICKERSON |  | WILK | /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-10-25 | EXCAVATED IN MUDPLOT IN FLOODED AREA BY HAND TO REPAIR LEAK ON 3/4 LEAD SERVICE ON INLET IN FRONT OF AABANDONED LOT. BACKFILLED MUDPLOT
201801878101 | 2018-10-26 | LEAD | 825 | STATE | CAMP | WILK | MI- LEAK AT THE STREET INLET SERVICE LEAK BEHIND CURB COCK, FLOODING SIDEWALK AND GUTTER /** 1) MN: A279542 SN: 0018271, *TAP: SIZE: A LOC: 103 FEET FROM P LINE AT CAMP, *MB: CODE: CD LOC: ON STATE 103FT FROM CAMP ****/ | 2018-11-06 | MADE 3 X 5 CUT IN SIDEWALK OVER 5/8 INLET .REPLACE 5/8 CURB COCK.BACKFILLED WITH SAND AND COLDMILL .LEFT BARRELL COLDMILL WAS SOFT.
201801879001 | 2018-10-26 | LEAD/PLASTIC | 2503 | PINE | NELSON | WILK | WM- LEAK IN THE SIDEWALK ***********L.THOMPSON @ 10:18AM********** INLET SERVICE LEAK IN ASPHLT STREET AND SIDEWALK, FLOODING AREA /** 1) MN: A140570 SN: 0062222, *TAP: SIZE: A LOC: 44 FEET FROM P LINE AT NELSON, *MB: CODE: ADM1 LOC: ON PINE,43' FROM L.S.P.L. NELSON ****/ | 2018-11-17 | MADE 4 X 2 CUT ON SIDEWALKEXCAVTED IN MUDPLOT MADE REPAIRS ON 3/4 "INLET AND BACKFILLED. (SOC 4FT .X 2 FT . S/W)
201801879901 | 2018-10-26 | LEAD | 1404 | DELERY | N VILLERE | WILK | ML- METER LEAK METER# A418992 ACCT# 305632-705859 INLET SERVICE LEAK INTERFERING WITH CUSTOMERS GETTING INTO HOME /** 1) MN: A244696 SN: 0103236, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT VILLERE N, *MB: CODE: AEN2 LOC: RES ON DELERY 47FT FROM PL VILLERE ****/ | 2018-11-07 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED AND DRESSED UP AREA
201801880701 | 2018-10-26 | LEAD | 1335 | BARTHOLOMEW | N VILLERE | WILK | ***********PICK UP********** INLET SERVICE LEAK 11/6/18 OUTLET LEAK FROM THE BOTTOM CAUSING POOR PRESSURE. PER S/R# 12856902 (PET) /** 1) MN: A304030 SN: 0062041, *TAP: SIZE: C LOC: 68 FEET FROM P LINE AT VILLERE N, *MB: CODE: AK1 LOC: ON BARTHOLOMEW 66FT FROM P.L. N VILLERE 8FT OUT- ****/ | 2018-11-06 | EXCAVATED + MADE REPAIR ON 1 INCH INLET SERVICE IN GUTTER BOTTOM BACKFILLED JOB WITH RIVERSAND CODLMILL FLUSH OUT LINE DIDN'T HAVR OUTSIDE FAUCET TO FLUSH LLITTLE MUD GOT INSIDE PIPE
201801881701 | 2018-10-26 | LEAD/PLASTIC | 41 | KINGSMILLS LN | ROSEDOWN CT | WINE | INSTALL ONE 5/8 INCH WATER METER AND SERVICE ON KINGSMILLS LN 1,016 FEET FROM P.L. OF OAK ALLEY CIRCLE 3 FEET BACK OF CURB. FOR #41 KINGSMILLS LANE GOOD JOB APP.: 123306 KEITH'S PLUMBING SERVICE (504) 392-3004 /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-21 | EXCAVATED HOLE NEAR CURB TO LOCATE INLET UNABLE TO LOCATE METER DUE TO BUILDING MATERIALS OBSTNCTING DIGGING AREA HOLE WAS BACKFILLED
201801882501 | 2018-10-26 | LEAD | 2226 | PAULINE | N TONTI | WILK | ML-METER LEAK ACCT# 154822-432575 METER# A325456 INLET SERVICE LEAK IN MUDPLOT SPOKE TO CUSTOMER 11/08/18 CUST STATED LEAK HAS GOTTEN WORSE AND WATER IS ATTRACTING ANIMALS TO HIS HOUSE (KSW) /** 1) MN: A325456 SN: 0091355, *TAP: SIZE: A LOC: 193 FEET FROM P LINE AT MIRO N, *MB: CODE: CDL LOC: 196.5 FROM P.L. N. MIRO 8' OUTSIDE PL ****/ | 2018-11-13 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK ALSO RAISED 5/8 INCH METER BOX COMPLETE TO GRADE BACKFILLED + DRESSED UP AREA
201801882601 | 2018-10-26 | LEAD | 1501 | FRANCE | N ROBERTSON | WMTLK | ML-METER LEAK ACCT#137725-707043 METER#A340210 EXAMINE INLET AND OUTLET SERVICE INSIDE METER BOX FOR A LEAK FLOODING SIDEWALK /** 1) MN: A327070 SN: 0068624, *TAP: SIZE: __ LOC: 21 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: OOO LOC: ON FRANCE 22FT FROM P.L. N ROBERTSON 8FT OUTSIDE ****/ | 2018-11-13 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 3/4 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801882701 | 2018-10-26 | LEAD | 5301 | ST CHARLES AV | VALMONT | WILK | ML-METERLEAK ACCT# 125402-571122 METER# C025803 BAD BLEEDER VALVE FLOODING GUTTER BOTTOM/DRIVEWAY /** 1) MN: C025803 SN: 0047455, *TAP: SIZE: Y LOC: 41 FEET FROM P LINE AT ST CHARLES AVE, *MB: CODE: BEH2 LOC: SIDE ST 2ND METER ON VALMONT 41' P.L. ST CHARLES ****/ DOTTIE READY 12/21/18 EXPIRATION 1/10/19 | 2018-12-26 | ARRIVED ON THE JOB SITE EXAMINE THE PROBLEM ,THE CURB COCK WAS BAD .BROKE UP DRIVEWAY WITH THEE MAUL.THE LINE WAS LEAD,CHANGED THE CURB COCK AND BACKFILLED THE CUT WITH SAND AND COLDMILL.(DONALD JOHNSON WAS THE FORMAN)
201801882901 | 2018-10-26 | LEAD | 1641 | BARTHOLOMEW | N DERBIGNY | WMTLK | MI--LEAK IN THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE INSIDE METER BOX FOR A LEAK FLOODING SIDEWALK /** 1) MN: A305213 SN: 0084033, *TAP: SIZE: A LOC: 11 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: __ LOC: ON BARTHOLOMEW 14FT FROM DERBIGNY ****/ | 2018-11-06 | EXCAVATED + MADE REPAIRS ON 5/8 INCH INLET SERVICE IN MUD PLOT BACKFILLED JOB WITH RIVERSAND
201801883503 | 2018-12-16 | LEAD/PLASTIC | 3866 | VIRGIL BL | PARIS AV | WILK | JOB CONTINUED TO REPAIR LEAK IN STREET /** 1) MN: A199293 SN: 0142716, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT HYDT, *MB: CODE: BDK2 LOC: ON VIRGIL BL 54FT FROM LSPL OF 3RD HYDT FROM PARIS ****/ | 2018-12-17 | EXAMINED LEAK ON LEAD CUT OUT STREET DUG DOWN TO MAIN AND REMOVED LEAD FROM AMIN TO METER AND REMOVED LEAD ON OUTLET TO PROPERTY. BACKFILLED AND CLEANED UP JOB.
201801884201 | 2018-10-26 | LEAD | 2322 | LAHARPE | N ROCHEBLAVE | WILK | ML-METER LEAK METER#A406863 ACCT#113980-709687 /** 1) MN: A244454 SN: 0044191, *TAP: SIZE: A LOC: 129 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BE LOC: 128' P.L. N ROCHEBLAVE ****/ | 2018-12-04 | REPLACED BOTH INLET AND OUTLET WASHERS
201801884701 | 2018-10-27 | LEAD/PLASTIC | 3942 | PIN OAK AV |  | WOLK | ML- METER LEAK MTR# A217447 ACCT# 232450-413213 OUTLET SERVICE LEAK @ PROPERTY LINE IN THE SIDEWALK /** 1) MN: A217447 SN: 0146147, *TAP: SIZE: B LOC: 400 FEET FROM P LINE AT TALL TIMBERS DR, *MB: CODE: ADKL LOC: ON S PIN OAK 10FT FROM DIV P/L TALL TIMBERS 2FT ****/ | 2018-11-15 | EXAMINED AREA EXCAVATED ON OUTLET SERVICE TRACED TO PROPERTY NO LEAK OBSERVED EXCAVATED ON INLET SERVICE TO MAIN OBSERVED LEAK ON TAIL PEICE REPAIRED LEAK RENEWED INLET SERVICE BACKFILLED CLEANED AREA
201801885001 | 2018-10-27 | LEAD | 2917 | URSULINES AV | N DUPRE | WILK | ML-METER LEAK ACCT#119009-520926 METER#A394018 INLET SERVICE LEAK IN THE DRIVEWAY BEHIND GATE /** 1) MN: A316217 SN: 0029920, *TAP: SIZE: A LOC: 2 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: OOO LOC: LAWN PL 7' DPL N DUPRE 159' P.L. N GAYOSO ****/ | 2018-11-15 | EXCAVATED IN CONCRETE DRIVEWAY + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801885101 | 2018-10-27 | LEAD | 2533 | COLUMBUS | N DORGENOIS | WMTLK | WM-LEAK IN SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR ALEAK /** 1) MN: C018004 SN: 0044035, *TAP: SIZE: C LOC: 138 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CDM LOC: ON COLUMBUS,138' FROM P.L. NO. DORGEOIS,8' OUTSIDE ****/ | 2018-11-08 | REPLACE BOTH INELT AND OUTLET WASHERS AT ABOVE LOCATION
201801889001 | 2018-10-28 | LEAD | 1 | MARLBOROUGH GATE PL | FRERET | WILK | ML: METER LEAK, MTR # A153497, ACCT 3 141328-570191 INLET SERVICE LEAKING BEHIND CURB COCK /** 1) MN: A153497 SN: 0072190, *TAP: SIZE: B LOC: 59 FEET FROM P LINE AT FRERET, *MB: CODE: BFHM LOC: ON MARLBOROUGH GATE PL 57.4' FROM PL FRERET ST ****/ | 2018-11-14 | EXCAVATED JOB DOWN BY HAND IN MUDPLOT FOUND LEAK ON INLET SERVICES COMING OFF TEE MADE REPAIRS TO LEAK BACKFILLED AND CLEANED JOB AREA .( NEED LEAD REMOVED) SHORT - SIDE
201801890501 | 2018-10-29 | LEAD | 1438 | N CLAIBORNE AV | KERLEREC | WILK | MI-CLOSED FOR INSIDE REPAIRS ACCT#107342-726448 METER#A336228 ****CONTACT UPON ARRIVAL***** BAD BLEEDER VALVE PASSING IN OFF POSITION /** 1) MN: A336228 SN: 0034850, *TAP: SIZE: A LOC: 40 FEET FROM P LINE AT KERLEREC, *MB: CODE: BELM LOC: ON NO. CLAIBORNE AVE.,40' FROM P.L. KERLEREC ****/ | 2018-11-09 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INELT SERVICE IN SIDEWALK BAKFILLED JOB WITH RIVERSAND COLDMILL
201801891401 | 2018-10-29 | LEAD | 2335 | CAFFIN AV | N TONTI | WILK | ML-METER LEAK ACCT#180724-421601 METER#B037336 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: B031880 SN: 0127925, *TAP: SIZE: B LOC: 281 FEET FROM P LINE AT NO. TONTI, *MB: CODE: AFN LOC: ON CAFFIN AVE., 275' FROM P.L. NO. TONTI ****/ | 2018-11-09 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201801892401 | 2018-10-29 | LEAD | 1636 | N TONTI | ONZAGA | WILK | ML- METER LEAK METER # A417868 ACCT# 128690-487544 INLET SERVICE LEAK, SIGNS OF PREVIOUS REPAIRS /** 1) MN: A295381 SN: 0066821, *TAP: SIZE: B LOC: 51 FEET FROM P LINE AT TONTI N, *MB: CODE: DHL LOC: ON ONZAGA 51FT PL N TONTI 10' OUTSIDE 2' INSIDE ****/ | 2018-11-09 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND AND COLDMILL IN GUTTER BOTTOM
201801893401 | 2018-10-29 | LEAD | 2 | SHEPARD CT |  | WMTLK | ML - METER LEAK ACCOUNT NUMBER - 235385-703316 METER NUMBER - A423263 EXAMINE INLET & OUTLET SERVICE FOR A LEAK INSIDE METER BOX IN THE MUD PLOT /** 1) MN: A328119 SN: 0161599, *TAP: SIZE: B LOC: 29 FEET FROM P LINE AT MAGELLAN, *MB: CODE: OO LOC: ON SHEPARD CT., 29' FROM P.L. MAGELLAN ** 2) MN: A155989 SN: 0161599, *TAP: SIZE: B LOC: 30 FEET FROM P LINE AT MAGELLAN, *MB: CODE: OOO LOC: ON SHEPARD CT., 30' FROM P.L. MAGELLAN, 9' OUTSIDE ****/ | 2018-11-11 | ARRIVED ON JOB SITE EXAMINE LEAK IN MUD PLOT EXCAVATED IN MUD PLOT MADE REPAIRS ON INLET SERVICE BACKFILLED DRESSED UP AREA WORK SITE
201801893501 | 2018-10-29 | LEAD | 1317 | ATLANTIC AV |  | WMTLK | MI--LEAK IN SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK INSIDE METER BOX IN THE MUD PLOT /** 1) MN: A243547 SN: 0134058, *TAP: SIZE: B LOC: 175 FEET FROM P LINE AT LAMARQUE, *MB: CODE: CD LOC: ON ATLANTIC AVE., 171' FROM P.L. LAMARQUE, 7' OUT- ****/ | 2018-11-10 | ARRIVED ON JOB SITE EXAMINE LEAK IN MUD PLOT EXCAVATED IN MUD PLOT BY HAND MADE REPAIRS ON SERVICE BACKFILLED DRESSED UP WORKSITE
201801893901 | 2018-10-29 | LEAD | 1431 | BOURBON |  | WILK | LOCATION ID-104865 MTR-A386002 BAD MTR LEAK/CUST HAS VERY LOW PRESSURE INLET SERVICE LEAK UNDERGROUND GETTING OFF IN DCB NEXT TO LARGE TREE ROOTS /** 1) MN: A295829 SN: 0015690, *TAP: SIZE: B LOC: 214 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: CDKM LOC: ON BOURBON 33FT FROM UPL OF KERLEREC ****/ | 2019-06-13 | EXCAVATED 2 X 4 CONCRETE SIDEWALK IN TREE ROOTS BY HAND FOUND LEAK ON 5/8 INCH SERVICE MADE REPAIR ON INLET SERVICE BACKFILL JOB WITH RIVERSAND AND COLDMILL
201801894101 | 2018-10-29 | LEAD/PLASTIC | 6410 | MILNE BL | BRAGG | WILK | MI- LEAK IN STREET CHANGED FROM 6400 MILNE BL INLET SERVICE LEAK IN ASPHALT STREET FLOODING AREA GETTING OFF IN DCB /** 1) MN: B014332 SN: 0118701, *TAP: SIZE: C LOC: 54 FEET FROM P LINE AT BRAGG, *MB: CODE: ADL1 LOC: 56FT FROM PL BRAGG MTR ON MILNE 6FT OUTSD PL ****/ | 2018-11-17 | EXCV 10 X 6 CUT IN STREET 3 X 3 CUT IN MUDPLOT, REPLACED 15 FT OF INLET LEAD LINE TO METER BOX RAISE TO GRADE BACKFILL DRESS CUT WITH SAND AND COLDMILL.
201801894701 | 2018-10-29 | LEAD | 1608 | ST CHARLES AV | EUTERPE | WILK | ML- METER LEAK MTR # A190030 ACCT # 102345-550007 INLET SERVICE LEAK NO METER IN BOX CURB COCK OFF WATER PASSING THROUGH 11/05/18 CUSTOMER STATED LEAK HAS GOTTEN WORSE, FLOODING AREA. PER SR@12856807 (AJR) /** 1) MN: A196355 SN: 0001164, *TAP: SIZE: B LOC: 75 FEET FROM P LINE AT EUTERPE, *MB: CODE: CEL LOC: 75FT FROM URPL EUTERPE ** 2) MN: A190030 SN: 0001164, *TAP: SIZE: B LOC: 75 FEET FROM P LINE AT EUTERPE, *MB: CODE: CEL LOC: ON ST CHARLES AVE 75FT FROM URPL OF EUTERPE ****/ | 2018-11-13 | MADE 3 X 3 CUT ON SIDEWALK EXCVATED ON INLET 3/4"WATER SERVICES.MADE REPAIRS AND BACKFILL LEAD LINE NO METER.
201801894901 | 2018-10-29 | LEAD/PLASTIC | 2522 | ST THOMAS |  | WILK | ML-METER LEAK ACCT#119159-541387 MTR#A323331 INLET SERVICE LEAK BEHIND CURB COCK 11/09/18 LEAK HAS GOTTEN WORSE CAUSING POOR PRESSURE PER SERVICE REQUEST #12857329 (FCP) /** 1) MN: A323331 SN: 0030611, *TAP: SIZE: A LOC: 72 FEET FROM P LINE AT THIRD, *MB: CODE: CEM LOC: 71FT FROM PL THIRD ON ST THOMAS ST ****/ | 2018-12-11 | EXAMINED AREA BROKE OUT BRICKS EXCAVATED ON INLET AND OUTLET SERVICE OBSERVED LEAK ON INLET SERVICE RENEWED OUTLET SERVICE RENEWED LEAD ON OUTLET TO PROPERTY LEAD FOUND ON INLET BACKFILLED NEED SAND AND COAL MILL FOR BACKFILL AND LEFT CONE ON SITE CLEANED AREA
201801895001 | 2018-10-29 | LEAD | 5631 | DEBORE DR | MENDEZ | WILK | MI LEAK AT EMPTY METER BOX INLET SERVICE LEAK @ THE CURB FLOODING CURB IN FRONT VACANT LOT /** 1) MN: A310542 SN: 0120550, *TAP: SIZE: B LOC: 240 FEET FROM P LINE AT MENDEZ, *MB: CODE: CDMN LOC: 240FT PL MENDEZ OPP WINDOW 7' OUTSIDE 4' INSIDE ****/ | 2018-11-12 | EXCAVATED IN A 5X5 MUDPLOT BY HAND FOUD LEAD LINE LEAKING ON INLET. REPAIRED LEAD LINE WITH 1 INCH STOP COCK AND RUN 4FT OF 1 INCH WATER TUBING. RAISE METER TO GRADE AND BACKFILLED AND DRESS
201801895301 | 2018-10-29 | LEAD | 4631 | ANNUNCIATION | CADIZ | WILK | ML; METER LEAK METER# A430814 ACCT# 139580-562339 LEAK IS STREAMING DOWN STREET PLEASE REVIEW INLET SERVICE LEAK IN AN ASPHALT STREET FLOODING SIDEWALK & DRIVEWAY. COMING FROM AN OLD PATCH /** 1) MN: A192445 SN: 0042527, *TAP: SIZE: A LOC: 227 FEET FROM P LINE AT CADIZ, *MB: CODE: BDKL LOC: ON ANNUNCIATION 227FT FROM PL CADIZ ****/ | 2018-11-06 | EXCAVTED OVER 6"WATER MAIN CHANGED 3/4 TAILPEICE TIED SERVICE BACK ITO WATER MAIN .BACKFILLED WITH RIVERSAND AND COLDMILL .MADE 6FT. X 6FT. CIT STREET IN FRONT OFF DRIVEWAY.
201801895701 | 2018-10-29 | LEAD/PLASTIC | 2409 | AMELIA | LASALLE | WOLK | LOCATION ID-124432 MTR-A431143 METER LEAK/CONS REG ON MTR OUTLET SERVICE LEAK CONSTANT REG /** 1) MN: A335246 SN: 0050734, *TAP: SIZE: A LOC: 90 FEET FROM P LINE AT LA SALLE, *MB: CODE: CDM1 LOC: 88FT FROM SPL LASALLE AMELIA ****/ DOTTIE READY 11-6-18 EXP 11-26-18 | 2018-11-12 | EXCAVTED JOB BY HAND OVER 4 X 4 CUT IN CONCRETE DRIVEWAY FOUND LEAK ON OUTLET SERVICE MADE REPAIRS TO LEAK BACKFILLED AND CLEANED JOB AREA.
201801896801 | 2018-10-29 | LEAD | 1405 | MUSIC | VILLERE | WOLK | ML- METER LEAK MTR# A408741 ACCT #126788-481834 OUTLET SERVICE LEAK /** 1) MN: 000000 SN: 0059107, *TAP: SIZE: A LOC: 51 FEET FROM P LINE AT VILLERE N, *MB: CODE: CDLM LOC: ON MUSIC,50' FROM L.S.P.L. NO. VILLERE ****/ | 2018-11-20 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH HANDWHEEL TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801897101 | 2018-10-29 | LEAD | 1405 | SONIAT | PRYTANIA | WMTLK | MI-LEAK AT THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: A228280 SN: 0013361, *TAP: SIZE: A LOC: 69 FEET FROM P LINE AT PRYTANIA, *MB: CODE: AELK LOC: ON SONIAT 67' P.L. PRYTANIA ****/ DOTTIE READY 11-7-18 EXP 11-27-18 | 2018-11-07 | EXCAVTED JOB DOWN BY HAND OVER 2X 2 CUT IN SIDEWALK FOUND LEAK INSIDE METER BOX (BAD COCK) MADE REPAIRS ON LEAK ,BACKFILLED AND CLEANED JOB AREA.
201801897501 | 2018-10-29 | LEAD | 1723 | N BROAD | AUBRY | WILK | WM-LEAK ON THE SIDEWALK INLET SERVICE LEAK FLOODING SIDEWALK/DRIVEWAY BAD BLEEDER VALVE /** 1) MN: A283967 SN: 0057181, *TAP: SIZE: A LOC: 129 FEET FROM P LINE AT AUBRY, *MB: CODE: BDM2 LOC: 128FT FROM USPL AUBRY ****/ | 2018-11-09 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801898201 | 2018-10-30 | LEAD | 2855 | ALLEN | AGRICULTURE | WILK | WM-LEAK ON THE SIDEWALK /** 1) MN: A244891 SN: 0104999, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT INDUSTRY, *MB: CODE: CDN1 LOC: ON ALLEN 130FT PL INDUSTRY 7' OUTSIDE ****/ INLET LEAK AT THE CURB ACROSS FROM ABOVE ADDRESS | 2018-11-14 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH OUTLET SERVICE UP TO GATE BACKFILLED JOB WITH RIVERSAND CODLMILL CUSTOMER HAS LEAK ON PROPERTY REFER TO P.O.P
201801898901 | 2018-10-30 | LEAD | 6331 | N DORGENOIS | DELERY | WILK | INLET SERVICE LEAK /** 1) MN: B030269 SN: 0128754, *TAP: SIZE: B LOC: 35 FEET FROM P LINE AT NO. DORGENOIS, *MB: CODE: ADHL LOC: ON DELERY, 35' FROM P.L. NO. DORGENOIS, 7' OUTSIDE ****/ | 2018-10-29 | EXCAVATED IN MUD PLOT AND REPLACED BAD CURB COCK BACKFILLED AREA. JOB COMPLETE
201801900201 | 2018-10-30 | LEAD | 908 | LIZARDI | BURGUNDY | WMTLK | ML- METER LEAK ACCT#130232-424863 METER# A374659 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: A327206 SN: 0059833, *TAP: SIZE: A LOC: 74 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CDL LOC: ON LIZARDI 73FT FROM USPL BURGUNDY ****/ | 2018-11-13 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201801900301 | 2018-10-30 | LEAD | 720 | BIENVILLE |  | WMTLK | LOCATION# 125778 CUSTOMER# 600147 METER# G002275 INSPECTOR DID AN OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION ON METER, CAN'T DETERMINE WHERE LEAK IS COMING FROM.........PLEASE REPAIR /** 1) MN: G002275 SN: 0048109, *TAP: SIZE: G LOC: 116 FEET FROM P LINE AT BOURBON, *MB: CODE: BE2 LOC: 131' FRM PL BOURBON IN DRIVEWAY IN SW/ON BIENVILLE ****/ | 2018-11-12 | EXAMINED JOB AND WAS UNABLE DETERMINE WHERE LEAK IS REFER TO METER SHOP
201801902001 | 2018-10-30 | LEAD | 2512 | N ROMAN |  | WILK | ML-METER LEAK ACCT#143006-482978 MTR#A270835 INLET SERVICE LEAK /** 1) MN: A270835 SN: 0074303, *TAP: SIZE: B LOC: 101 FEET FROM P LINE AT ARTS, *MB: CODE: CDL1 LOC: 101' P.L. ARTS ****/ | 2018-11-12 | EXCAVATED 3 X 3 MUD PLOT MADE REPAIR ON INLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801902801 | 2018-10-30 | LEAD | 1313 | CAFFIN AV | URQUHART | WILK | ML METER LEAK METER# A264875 INLET SERVICE LEAK CARS PARKING ON METER /** 1) MN: A264875 SN: 0095052, *TAP: SIZE: A LOC: 109 FEET FROM P LINE AT URQUHART, *MB: CODE: DL7 LOC: 112'FROM URQUHART RES ****/ | 2018-11-13 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201801903701 | 2018-10-30 | LEAD | 2411 | DELACHAISE | LASALLE | WMBK | LOCATION: 306290 PER INSP BIBBINS - PLEASE REPAIR OUTLET BEHIND CASING, ALSO SET A 5/8 METER. CUSTOMER WAITING ON WATER METER BOX CASING SHIFTED OVER HANDWHEEL HOUSE UNDER RENOVATIONS SET 5/8 METER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-06 | EXCVATED JOB DONE BY HAND OVER MUDPLOT FOUND LEAK ON OUTLET SERVICE MADE REPAIRS ALSO FIXED CASING BACKFILLED AND CLEANED JOB AREA.
201801903901 | 2018-10-30 | LEAD | 735 | MARIGNY | DAUPHINE | WILK | ML- METER LEAK MTR# A248129 ACCT # 125300-480890. INLET SERVICE LEAK IN TREE ROOTS /** 1) MN: A248129 SN: 0047660, *TAP: SIZE: A LOC: 58 FEET FROM P LINE AT DAUPHINE, *MB: CODE: BDMN LOC: ON MARIGNY,60' FROM L.R.P.L. DAUPHINE ****/ | 2018-11-15 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801904101 | 2018-10-30 | LEAD | 3009 | ST CLAUDE AV |  | WILK | MI-LEAK BETWEEN SIDEWALK AND CURB INLET SERVICE LEAK UNDERGROUND /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-13 | EXCVATED IN CONCRETE SIDEWALK + MADE REPAIR ON 3/4 INCH SERVICE LINE BACKFILLED + DRESSED UP AREA
201801904301 | 2018-10-30 | LEAD | 1933 | LOUISA |  | WILK | INSP D JOHNSON SAYS SERVICE IS LEAKING FROM BLEEDER VALVE. PLEASE REPAIR METER A417053 LOC ID 144182-+ /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ INLET SERVICE LEAK INSIDE METER BOX | 2018-11-12 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801904401 | 2018-10-30 | LEAD | 1917 | GOV NICHOLLS |  | WOLK | INSP L UDUEBOR STATES SERVICE IS LEAKING BEHIND CURB COCK. PLEASE REPAIR METER A417127 LOC ID306263 EXAMINE OUTLET SERVICE FOR LEAK /** 1) MN: SN: 0045849, *TAP: SIZE: A LOC: 137 FEET FROM P LINE AT ROMAN N, *MB: CODE: AFM4 LOC: 136' P.L. N ROMAN ****/ | 2018-11-14 | EXCAVATED IN MUD PLOT AND MADE METER REPAIRS ON 3/4 INCH INLET SERVICE REPLACED 5/8 INCH METER BOTTOM AND 5/8 INCH CURB COCK BACKFILLED AREA
201801905701 | 2018-10-30 | LEAD | 2525 | N TONTI | MUSIC | WMLK | MI- LEAK IN STREET LEAK ON WATER MAIN IN MIDDLE OF STREET /** 1) MN: A273724 SN: 0077114, *TAP: SIZE: A LOC: 212 FEET FROM P LINE AT MUSIC, *MB: CODE: BDOK LOC: ON NO. TONTI, 212' FROM P.L. MUSIC ****/ | 2018-11-09 | EXCAVATED IN ASPHALT STREET + REPLACED 3/4 INCH BEND ADAPTER ON WATER MAIN COMPACTED BACKFILLED + DRESSED UP AREA
201801905801 | 2018-10-30 | LEAD | 1332 | ANDRY | URQUHART | WILK | ML- METER LEAK METER# A227869 ACCT# 174289-423530 INLET SERVICE LEA IN MUDPLOT /** 1) MN: A227869 SN: 0117795, *TAP: SIZE: A LOC: 257 FEET FROM P LINE AT URQUHART, *MB: CODE: DN6 LOC: ON AUDRY 257' FROM PL URQUHART RES ****/ | 2018-11-13 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201801906501 | 2018-10-30 | LEAD | 920 | 7TH | CONSTANCE | WILK | ML-METER LEAK METER#A412361 ACCT#115397-538909 INLET SERVICE LEAK IN SIDEWALK /** 1) MN: A267872 SN: 0018501, *TAP: SIZE: A LOC: 146 FEET FROM P LINE AT CONSTANCE, *MB: CODE: CFM1 LOC: ON 7TH 145FT. FRM PL CONSTANCE ****/ DOTTIE READY 12-27-18 EXP 1-16-19 | 2018-12-26 | REPLACED 5/8 CURB COCK TIED INTO LEAD.(SOC 3FT. X 3 FT. S/W)
201801907001 | 2018-10-31 | LEAD | 3144 | N DERBIGNY |  | WMTLK | LOCATION ID-180814 MTR-B028301 CURB COCK UNDER CASING UNABLE TO TURN MTR OFF FOR DELIQUENT BALANCE CONTACT MROC AFTER COMPLETION /** 1) MN: B028301 SN: 0128109, *TAP: SIZE: C LOC: 377 FEET FROM P LINE AT CLOUET, *MB: CODE: ADM7 LOC: ON NO. DERBIGNY, 377' FROM P.L. CLOUET, 7' OUTSIDE ****/ | 2018-11-12 | EXCAVATED IN MUD PLOT + RE-SET 5/8 INCH METER BOX CASING PROPERTY BACKFILLED + DRESSED UP AREA
201801909601 | 2018-10-31 | LEAD | 1801 | MANDEVILLE | N ROMAN | WILK | MI-- LEAK IN SIDEWALK CHANGED FROM 2321 N ROMAN INLET SERVICE LEAK ON N ROMAN /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-14 | EXCAVATED IN MUD PLOT + MADE REPIR ON 3/4 INCH INLET SERVICE LINE UNDER CURB BACKFILLED + DRESSED UP AREA
201801909801 | 2018-10-31 | LEAD | 2649 | LOUISA | FLORIDA AV | WMTLK | ML - METER LEAK ACCT#220631-725643 METER#A417636 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-12 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX AT ABOVE LOCATION
201801910501 | 2018-10-31 | LEAD | 2643-45 | DUMAINE | N DORGENOIS | WILK | MI-LEAK IN SIDEWALK CHANGED FROM 2641 DUMAINE INLET ON ABANDON SERVICE /** AT 2643: 1) MN: A124493 SN: 0048197, *TAP: SIZE: B LOC: 144 FEET FROM P LINE AT BROAD N, *MB: CODE: AEL4 LOC: ON DUMAINE 145' FROM PL N BROAD 10' OUTSIDE PL 2' ****/ | 2018-11-19 | MADE 2 X 4 CUT IN SIDEWALK AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA
201801910601 | 2018-10-31 | LEAD | 1219 | KENTUCKY | MARAIS | WILK | ML- METER LEAK ACCT# 162122-431425 METER# A311297 EXAMINE INLET AND OUTLET SERVICE FOR LEAK CARS DRIVING OVER METER /** 1) MN: A311297 SN: 0101087, *TAP: SIZE: A LOC: 138 FEET FROM P LINE AT MARAIS, *MB: CODE: BDL2 LOC: 138'P L MARAIS 8' OUTSIDE ****/ | 2018-11-12 | EXCVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801911701 | 2018-10-31 | LEAD | 1300 | MANDEVILLE | URQUHART | WLPR | PP-POOR PRESSURE ACCT#112147-715714 METER#A242561 ***CONTACT UPON ARRIVAL**** EXAMINE INLET SERVICE FOR LEAK, UPSTAIRS NOT GETTING NO WATER /** 1) MN: A242561 SN: 0016488, *TAP: SIZE: A LOC: 52 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: AHOF LOC: SIDE ST ON URQUHART 53' P.L. MANDEVILLE ****/ | 2018-11-08 | EXAMINED METER AT ABOVE LOCATION + FOUND EXCELLENT PRESSURE AT METER WITH NO LEAK OR CONSTANT REGISTRATION
201801913401 | 2018-10-31 | LEAD | 2119 | SIMON BOLIVAR AV | JOSEPHINE | WILK | MI - LEAK ON SIDEWALK INLET SERVICE LEAK IN THE SIDEWALK GETTING OFF IN THE DCB /** 1) MN: A187033 SN: 0012368, *TAP: SIZE: A LOC: 157 FEET FROM P LINE AT JOSEPHINE, *MB: CODE: CEN1 LOC: 158FT FROM PL JOSEPHINE 2' OUTSIDE PL 8' INSIDE CU ****/ DOTTIE READY 12/13/18/EXP 01/02/19 | 2019-01-01 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801919501 | 2018-11-01 | LEAD | 910 | N BROAD | DUMAINE | WILK | METER LEAK INLET SERVICE LEAK /** 1) MN: C028613 SN: 0047161, *TAP: SIZE: C LOC: 94 FEET FROM P LINE AT DUMAINE, *MB: CODE: BE LOC: ON BROAD 94FT FROM DUMAINE 8FT OUTSIDE ****/ | 2018-11-15 | REPLACED 1 INCH WASHERS IN METER BOX
201801921502 | 2019-01-28 | LEAD/PLASTIC | 939 | THALIA | CONSTANCE | WILK | WE EXCAVATED IN STREET AND SIDE WALK TO MAKE REPAIRS BUT COULD NOT COMPLETE THE JOB DOE TO TIME SIT WAS LEFT SAFE FLAGS AND BARRORS /** 1) MN: A284846 SN: 0146243, *TAP: SIZE: B LOC: 88 FEET FROM P LINE AT CONSTANCE, *MB: CODE: CDV LOC: ON THALIA 88FT FROM PL CONSTANCE 6FT OUTSIDE PL ****/ | 2019-01-28 | ARRIVED ON JOB SITE EXAMINED LEAK IN SIDEWALK AND STREET MADE CUT IN STREET EXCAVATED IN MUD PLOT MADE REPAIRS ON INLET SERVICE BACKFILLED DRESS UP WORK SITE ALSO WASH DOWN SIDEWALK AND STREET
201801921901 | 2018-11-01 | LEAD/PLASTIC | 5019 | S JOHNSON | JEFFERSON AV | WOLK | WM-LEAK IN THE STREET CHANGED FROM 5100 BLK S JOHNSON OUTLET SERVICE LEAK IN SIDEWALK FLOODING CURB CONSTANCE REG ON METER /** 1) MN: A332109 SN: 0102793, *TAP: SIZE: A LOC: 158 FEET FROM P LINE AT ROBERT, *MB: CODE: A LOC: ON S JOHNSON 158' FROM PL ROBERT 7' OUTSIDE PL 3' ****/ DOTTIE READY 11-7-18 EXP11-27-18 | 2018-11-07 | MADE 3 X 6 CUT IN SIDEWALK .REMOVE LEAD OUTLET SERVICE TO PROPERTY,REPLACED LEAD WITH 3/4 PLASTIC.MOVE METER BOX INTO SIDEWALK AND RAISED TO GRADE .REMOVE OLD METER SET NEW *************OLD METER INFO************ METER.A308035 FAC:52086893 MAKE:SENSUS READ:8576
201801922901 | 2018-11-02 | LEAD | 1307 | BOURBON |  | WILK | PP- POOR PRESSURE METER NUMBER - A191638 INLET SERVICE LEAK CAUSING POOR PRESSURE /** 1) MN: A191638 SN: 0022484, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT BARRACKS, *MB: CODE: BEN7 LOC: RES 2ND METER 62.7' FROM P LINE BARRACKS ****/ | 2018-11-16 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO MAKE THE REPAIRS MADE A 3X3 CON SIDEWALK CUT BACKFILLED AND DRESS UP CUT
201801924201 | 2018-11-02 | LEAD | 5942 | CHESTNUT | STATE | WILK | ML- METER LEAK ACCT# 121390-564612 METER# A270065 INLET SERVICE LEAKING UNDERGRD IN CONCRETE STREET /** 1) MN: A125642 SN: 0059492, *TAP: SIZE: A LOC: 105 FEET FROM P LINE AT STATE, *MB: CODE: OOO LOC: ON CHESTNUT,104' FROM L.P.L. STATE STREET ****/ | 2018-11-12 | EXCVATED JOB DOWN,BY HAND OVER 2X 2 CUT IN SIDEWALK FOUND LEAK ON INLET SERVICES MADE REPAIRS TO LEAK BACKFILLED AND CLEANED JOB AREA.
201801926301 | 2018-11-02 | LEAD/PLASTIC | 927 | 3RD | CONSTANCE | WILK | MI- LEAK ON THE SIDWALK INLET SERVICE LEAK IN BRICK WALKWAY, ALSO TREE ROOTS IN WALKWAY /** 1) MN: A346301 SN: 0027416, *TAP: SIZE: A LOC: 111 FEET FROM P LINE AT CONSTANCE, *MB: CODE: CEL LOC: 112FT FROM PL CONSTANCE ****/ | 2018-12-17 | ARRIVED ON JOB SITE EXAMINE LEAK IN AREA BROKE CONCRETE AND BRICK BY HAND MADE REPAIRS ON SERVICE RENEWED OUTLET BACKFILLED DRESS UP WORK SITE BY HAND
201801928501 | 2018-11-02 | LEAD | 400 | ESPLANADE AV | DECATUR | WILK | WM- LEAK IN STREET BY THE NEW ORLEANS JAZZ MUSEUM INLET SERVICE LEAK IN NEUTRAL GROUND FLOODING CURB/STREET /** 1) MN: G001149 SN: 0005198, *TAP: SIZE: G LOC: 137 FEET FROM P LINE AT PETERS N, *MB: CODE: __ LOC: IN ST. ON BARRACKS 120FT. FROM N. PETERS ** 2) MN: H001266 SN: 0000000, *TAP: SIZE: H LOC: 118 FEET FROM P LINE AT PETERS N, *MB: CODE: __ LOC: ON BARRACKS BET DECATUR & N. PETERS 112FT. PL N. P ****/ | 2019-04-09 | EXCAVATED 4 X 10 MUD PLOT FOUND LEAK ON 2 INCH INLET SERVICE MADE REPAIR ON 2 INCH INLET BACKFILL JOB WITH RIVERSAND
201801928701 | 2018-11-02 | LEAD | 1632 | N TONTI | ONZAGA | WMTLK | PP-POOR PRESSURE METER#A181524 ACCT3137370-488826 EXAMINE INLET/OUTLET SERVICE LEAKING INSIDE METER BOX CAUSING POOR PRESSURE /** 1) MN: A181524 SN: 0067944, *TAP: SIZE: A LOC: 253 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: BDKN LOC: 57' P.L. ONZAGA ****/ | 2018-11-13 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH CUEB COCK LEAKING ON LEAD LINE + REPAIRS + BACKFILLED
201801931001 | 2018-11-03 | LEAD | 1548 | LEDA CT | PRIVATE | WILK | ML- METER LEAK METER# A370869 ACCT# 118756-490762 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A307978 SN: 0029147, *TAP: SIZE: A LOC: 11 FEET FROM P LINE AT PRIVATE ST, *MB: CODE: AFK7 LOC: 11FT FROM UR CURB OF PRIVATE ST METER ON LEDA ****/ | 2018-12-06 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILED JOB WITH RIVERSAND
201801933101 | 2018-11-04 | LEAD | 2613 | DEERS | LAW | WILK | WM-LEAK IN STREET INLET SERVICE LEAK AT CURB /** 1) MN: A280440 SN: 0097161, *TAP: SIZE: B LOC: 142 FEET FROM P LINE AT LAW, *MB: CODE: CDLM LOC: ON DEERS 141.5FT FROM PL OF LAW 8FT OUTSIDE PL 3FT ****/ | 2018-11-15 | EXCAVATED IN GUTTER BOTTOM AND MADE REPAIRS ON 2 INCH CONTROLLING LINE DONE BY CONTRACTOR IN FRONT OF ABANDON LOT BACKFILLED AREA
201801933701 | 2018-11-04 | LEAD | 920 | TAFT PL | DUMAINE | WMTLK | ML- METER LEAK METER# A296963 ACCT#141336-704160 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A254803 SN: 0072634, *TAP: SIZE: B LOC: 177 FEET FROM P LINE AT DUMAINE, *MB: CODE: BD LOC: ON TAFT PL 177' FROM PL DUMAINE ****/ | 2018-11-16 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND
201801935401 | 2018-11-05 | LEAD | 4724 | SHALIMAR DR | DREUX AV | WMTLK | MI- LEAK IN THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: SN: 0124772, *TAP: SIZE: B LOC: 311 FEET FROM P LINE AT PRENTISS AVE, *MB: CODE: AD LOC: RES ON SHALIMAR 310' PL PRENTISS AV 8' OUTSIDE ****/ | 2018-11-21 | EXCAVATED DOWN ON INLET SERVICE. FOUND LEAD AND METER COCK WAS LEAKING. MADE REPAIRS BY REPLACING COCK AND WASHERS. BACKFILLED
201801935801 | 2018-11-05 | LEAD | 2013-15 | TOURO | N GALVEZ | WILK | MI- LEAK IN THE STREET CHANGED FROM 2017 TOURO **********CUSTOMER OUT OF WATER********** M DAIGLE 10:49 INLET SERVICE LEAK /** AT 2013: 1) MN: A316894 SN: 0061927, *TAP: SIZE: A LOC: 98 FEET FROM P LINE AT JOHNSON N, *MB: CODE: BD LOC: ON TOURO,99.4' FROM L.S.P.L. NO. JOHNSON ****/ | 2018-11-05 | FOUND BROKEN 6 INCH WATER MAIN AT ABOVE LOCATION EXCAVATED IN ASPHALT STREET (15 X 40 ) REPLACED 13 FT OF BROKEN 6 INCH WATER MAIN USING TWO 6 X 12 REPAIR CLAMP COMPACTED BACKFILLED + DRESSED UP AREA. JOB COMPLETE
201801936301 | 2018-11-05 | LEAD | 3805 | ROYAL | PAULINE | WILK | ML-METER LEAK METER #A408605 ACCT # 144262-711649 CHANGED ROM 3805 ROYAL INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A216096 SN: 0075699, *TAP: SIZE: B LOC: 47 FEET FROM P LINE AT PAULINE, *MB: CODE: CELM LOC: 46FT FROM PL PAULINE ON ROYAL ST ****/ | 2018-11-20 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK LEFT SAFETY CONE ON CUT (NEED SODEWALK REPAIR ASAP DUE TO HANDICAP CUSTOMER LIVING THERE)
201801938001 | 2018-11-05 | LEAD | 1224 | N GALVEZ | GOV NICHOLLS | WMTLK | ML- METER LEAK METER# B026349 ACCT# 100481-524663 EXMAINE INLET & OULET SERVICE FOR A LEAK /** 1) MN: B026349 SN: 0007802, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT NO. GALVEZ, *MB: CODE: CEL1 LOC: ON NO. GALVEZ,161' FROM L.R.P.L. GOV. NICHOLLS,1' ****/ | 2018-11-15 | REPLACED 3/4 INCH HANDWHEEL + GUTS IN METER BOX
201801938101 | 2018-11-05 | LEAD | 3223 | 3RD | S ROMAN | WILK | ML- METER LEAK ACCT#210094-551367 METER#A378129 CUSTOMER STATED HER AREA IS FLOODING *********************1ST AM****************** INLET SERVICE LEAK IN GRASS FLOODING AREA /** 1) MN: A341198 SN: 0073678, *TAP: SIZE: C LOC: 190 FEET FROM P LINE AT S PRIEURN, *MB: CODE: AD1 LOC: ON 3RD ST. 53' DIV. PL OF S.PRIEUR 4 FT ** 2) MN: A257913 SN: 0073678, *TAP: SIZE: B LOC: 50 FEET FROM P LINE AT S PRIEUR, *MB: CODE: AD1 LOC: ON 3RD ST. 48' FROM DPL S. PRIEUR,4' OUTSIDE PL 6' THERE ARE 23 MORE NOT LISTED. ****/ | 2018-11-11 | REPLACED 5/8 CURB COCK IN ABANDON METER BOX.(SOC 3FT. X 3 FT .S/W)
201801939101 | 2018-11-05 | LEAD | 1506-08 | SPAIN | N ROBERTSON | WOLK | WM - LEAK IN THE SIDEWALK EXAMINE OUTLET SERVICE @ PROPERTY LINE /** AT 1506: 1) MN: A332845 SN: 0062167, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: AFL LOC: INSIDE BY S&W ****/ | 2018-11-14 | EXCAVATED 4 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIRS ON OUTLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201801939901 | 2018-11-05 | LEAD | 2115 | MUSIC | N GALVEZ | WMBK | ML- METER LEAK METER# A365202 ACCT# 146983-484158 METER BOX CASING SHIFTED OVER CURB COCK, ALSO CHANGE METER /** 1) MN: A260166 SN: 0079073, *TAP: SIZE: B LOC: 140 FEET FROM P LINE AT GALVEZ N, *MB: CODE: DMN LOC: 140FT FROM PL GALVEZ N ON MUSIC ST ****/ | 2018-11-14 | REPLACE UPPER METER BOX CASING AND A 5/8INCH WATER METER ***************OLD METER INFO************ METER:A365202 FAC:70694417 MAKE:SENSUS READ:0
201801940101 | 2018-11-05 | LEAD | 3113 | BANKS | S LOPEZ | WMTLK | ML - METER LEAK MTR# A364758 ACCT # 114176-532224 EXAMINE INLET/OUTLET SERVICE FOR LEAK FLOODING SIDEWALK /** 1) MN: A273574 SN: 0015852, *TAP: SIZE: A LOC: 85 FEET FROM P LINE AT LOPEZ S, *MB: CODE: CFML LOC: ON BANKS 86' FROM LRPL S LOPEZ ****/ | 2018-11-16 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERCVICE IN SIDEWALK BACKFILL JOB WITH RIVERSAND COLDMILL
201801941201 | 2018-11-06 | LEAD | 2346 | N MIRO | SPAIN | WOLK | LOCATION ID-168294 MTR-A427025 LEAK AT AND AROUND MTR CONS REG ON MTR /** 1) MN: A328286 SN: 0110052, *TAP: SIZE: B LOC: 107 FEET FROM P LINE AT SPAIN, *MB: CODE: CDK6 LOC: ON NO. MIRO, 107' FROM P.L. SPAIN, 10' OUTSIDE ****/ | 2018-11-14 | EXCAVATED AND MADE REPAIR 5/8 INCH OUTLET SERVICE IN MUD PLOT BACKFILLED JOB WITH RIVERSAND
201801941401 | 2018-11-06 | LEAD/PLASTIC | 4301 | VIXEN |  | WILK | WM-- LEAK IN STREET INLET SERVICE LEAK IN A CONCRETE STREET FLOODING AREA, GETTING OFF IN THE DCB 11/26/18 LEAK CAUSING POOR PRESSURE PER SR#12858645 (AJR) /** 1) MN: A230967 SN: 0130685, *TAP: SIZE: B LOC: 555 FEET FROM P LINE AT HOLIDAY DR, *MB: CODE: B LOC: ON VIXEN, 555' FROM P.L. HOLIDAY DR., 10' OUTSIDE, ****/ | 2019-01-17 | EXAMINED AREA EXCAVATED ON INLET AND OUTLET SERVICE BROKE OUT STREET EXCAVATED IN STREET EXPOSED LEAK ON LEAD LINE REPAIRED LEAK BACKFILLED CLEANED AREA
201801942301 | 2018-11-06 | LEAD | 1814 | INDEPENDENCE |  | WMBK | LOCATION: 302538 MTR# A 425840 PER INSP D. JOHNSON - INLET/OULET NOT LINING UP, ALSO WASHER LEAKING ON OUTLET SIDE. PER L UDEBOR, TRANSFER TO CENTRAL YARD. INLET & OUTLET NOT LINING UP CORRECTLY **CUSTOMER HAS WATER*** /** 1) MN: A296780 SN: 0100923, *TAP: SIZE: A LOC: 99 FEET FROM P LINE AT ROMAN N, *MB: CODE: AD LOC: 99'FROM PL N ROMAN 7' OUTSIDE PL ****/ | 2018-11-19 | EXCAVATED TO FIND A 5/8 INCH METER BOTTOM BROKEN REMOVED AND REPLACED WITH A 5/8 INCH BOTTOM TO MAKE THE REPAIRS MADE A 3X3 MUD CUT BACKFILLED AND DRESS UP CUT
201801942701 | 2018-11-06 | LEAD/PLASTIC | 1802 | 2ND | BARONNE | WOLK | ML- METER LEAK MTR# A406234 ACCT# 100503-548463 OUTLET SERVIE LEAK IN SIDEWALK FLOODING SIDEWALK AND GUTTER BOTTOM /** 1) MN: SN: 0056562, *TAP: SIZE: B LOC: 77 FEET FROM P LINE AT SECOND, *MB: CODE: __ LOC: ON BARONNE,79' FROM U.S.P.L. SECOND. ****/ | 2018-11-09 | MADE CUT ON SIDEWALK EXCVATED IN MUDPLOT ON INLET AND MADE REPAIRS ON 3/4 WATER SERVICE AND BACKFILL.(SOC 2FT .X 2 FT . S/W)
201801943201 | 2018-11-06 | LEAD | 1221 | REYNES | URQUHART | WOLK | MI- CHANGE LEAD WHIP ACCT# 305635-705859 METER# A419589 CUSTOMER WAITING ON TIE IN **HOUSE UNDER RENOVATIONS** /** 1) MN: A341008 SN: 0093253, *TAP: SIZE: B LOC: 198 FEET FROM P LINE AT URQUHART, *MB: CODE: ADK LOC: RES ON REYNES 202FT FROM PL URQUHART L/S CURB ****/ | 2018-11-15 | EXCAVATED NAD MADE OUTLET TIE-IN ,IN MUD PLOT AT ABOVE LOCATION BACKFILLED JOB WITH RIVERSAND
201801943301 | 2018-11-06 | LEAD | 1318 | FLOOD | N VILLERE | WOLK | MI- CHANGE LEAD WHIP ACCT# 305637-705859 METER# A418421 CUSTOMER WAITING ON TIE IN **HOUSE UNDER RENOVATIONS** /** 1) MN: 000000 SN: 0099292, *TAP: SIZE: A LOC: 142 FEET FROM P LINE AT URQUHART, *MB: CODE: DM6 LOC: 142'FROM P L URQUHART 8' OUTSIDE RES ****/ | 2018-11-15 | EXCAVATED AND MADE OUTLET TIE - IN AT ABOVE LOCATION BACKFILLED JOB WITJ RIVERSAND COLDMILL IN ISDEWALK ALSO REPLACE 5/8 INCH WTER METER THERE A LEAK ON WATER LINE AT WATERMAIN CUSTOMER HAS LOW PRESSURE REFER TO ZONE FOR REPAIRS *****************OLD METER INFO************** METER:A418421 FAC:1544667 MAKE:HERSEY READ:0
201801943303 | 2018-11-19 | LEAD | 1318 | FLOOD | N VILLERE | WILK | EXCAVATED AND MADE OUTLET TIE-IN AT ABOVE LOCATION BACKFILLED JOB WITH RIVERSAND COLDMILL IN SIDEWALK ALSO REPLACE 5/8 INCH WATER METER THERE A LEAK ON WATER LINE AT WATER MAIN CUSTOMER HAS LOW PRESSURE REFER TO ZONE4 FOR REPAIRS /** 1) MN: 000000 SN: 0099292, *TAP: SIZE: A LOC: 142 FEET FROM P LINE AT URQUHART, *MB: CODE: DM6 LOC: 142'FROM P L URQUHART 8' OUTSIDE RES ****/ | 2018-11-21 | MADE 8 X 12 CUT IN BLACK TOP STREET AND RENEWED 3/4 INCH INLET FROM WATER MAI TO METER BOX BACKFILLED AREA
201801944101 | 2018-11-06 | LEAD | 2505 | PALMYRA |  | WMRE | LOCATION: 306333 PER INSP L UDEBOR - METER BOX IS BURIED. PLEASE LOCATE AND RAISE TO GRADE, ALSO SET A 5/8 METER. NEED WATER ASAP SOMEONE WILL BE MOVING IN SOON LOCATE, RAIS TO GRADE AND SET 5/8 METGER NEW CONSTUCTION /** 1) MN: A228946 SN: 0027860, *TAP: SIZE: A LOC: 42 FEET FROM P LINE AT ROCHEBLAVE S, *MB: CODE: FL LOC: BY S & W 42' P.L. S ROCHEBLAVE ****/ | 2018-11-15 | EXCAVATED IN MUD PLOT + CONCRETE SIDEWALK + LOCATED 5/8 INCH METER BOX RAISED METER BOX TO GRADE + ALSO SET 5/8 INCH METER BACKFILLED + DRESSED UP AREA
201801944301 | 2018-11-06 | LEAD | 2738 | ST PHILIP | N BROAD | WILK | MI - LEAK IN STREET CHANGED FROM 2740 ST PHILIP INLET SERVICE LEAK IN THE STREET /** 1) MN: SN: 0052128, *TAP: SIZE: B LOC: 279 FEET FROM P LINE AT BROAD N, *MB: CODE: ADK1 LOC: ON ST PHILIP 278FT FROM PL N BROAD ** 2) MN: SN: 0052128, *TAP: SIZE: B LOC: 279 FEET FROM P LINE AT BROAD N, *MB: CODE: ADK1 LOC: ON ST PHILIP BET N WHITE AND N BROAD THERE IS 1 MORE NOT LISTED. ****/ | 2018-11-14 | MADE 8 X 12 CUT IN CONCRETE BASE STREET AND REPLACED 5/8 INCH CARBARATION COCK ON 12 INCH WATER MAIN OPEN AND CLOSED 7 VALVES NOTIFIED AREA OF WATER CLOSURE BACKFILELD AREA
201801944701 | 2018-11-06 | LEAD | 1709 | N MIRO | ST BERNARD AV | WILK | ML- METER LEAK METER #A416127 ACCT #134845-488796 EXAMINE INLET SERVICE FOR A LEAK IN THE MUD PLOT NEAR METER /** 1) MN: A330777 SN: 0056567, *TAP: SIZE: A LOC: 84 FEET FROM P LINE AT ST BERNARD AVE, *MB: CODE: CDLM LOC: ON N MIRO ST 84' FROM PL D'ABADIE ST ****/ | 2018-11-19 | EXCAVATED 3 X 3 MUD PLOT REPLACED 5/8INCH HANDWHEEL TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801945101 | 2018-11-06 | LEAD | 5036 | N RAMPART | FORSTALL | WILK | ML- METER LEAK METER # A425503 ACCT# 130837 - 727399 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: 000000 SN: 0060875, *TAP: SIZE: A LOC: 37 FEET FROM P LINE AT RAMPART N, *MB: CODE: ADHT LOC: ON FORSTALL,37.4' FROM R.P.L. NO. RAMPART ****/ | 2018-11-15 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE IN SIDEWALK
201801947001 | 2018-11-07 | LEAD | 1520 | N ROCHEBLAVE | COLUMBUS | WMTLK | LOCATIONID#153178-489451 METER#A414281 AREA FLOODED,METER LEAK /** 1) MN: A345346 SN: 0089005, *TAP: SIZE: B LOC: 175 FEET FROM P LINE AT COLUMBUS, *MB: CODE: C LOC: ON NO. ROCHEBLAVE,174.3' FROM P.L. COLUMBUS,9'OUT- ****/ | 2018-11-19 | EXCAVATED 3 X 3 GUTTER BOTTOM REPLACED 5/8 INCH METER BOX COCK ALSO METER BOX CASING BACKFILLED AND CLEANED THE AREA
201801947401 | 2018-11-07 | LEAD | 2415 | OAK PL | N TONTI | WMTLK | LOCATIONID#211169-523110 METER#A401214 LEAK INSID METERBOX /** 1) MN: A317494 SN: 0171627, *TAP: SIZE: B LOC: 20 FEET FROM P LINE AT NO. TONTI, *MB: CODE: ALFD LOC: ON OAK PL., 18' FROM D.P.L. NO. TONTI, 2' OUTSIDE, ****/ | 2018-11-16 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH WASHERS LEAKING + REPLACED THEM ALSO ADDED METER CASING
201801947701 | 2018-11-07 | LEAD | 1400 | DELERY |  | WILK | WATER INLET SERVICE /** 1) MN: A289118 SN: 0165958, *TAP: SIZE: B LOC: 23 FEET FROM P LINE AT DELERY, *MB: CODE: OOO LOC: ON DELERY 23FT FROM PL N VILLERE 4' OUTSIDE PL 3' ****/ | 2018-11-06 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA. JOB COMPLETE
201801948601 | 2018-11-07 | LEAD | 3324 | ST PHILIP |  | WMTLK | LOCATIONID#124955-521619 METER#A300591 LEAK INSIDE METERBOX /** 1) MN: A300591 SN: 0048591, *TAP: SIZE: A LOC: 197 FEET FROM P LINE AT HAGAN AVE, *MB: CODE: CD LOC: ON ST. PHILIP,197.1' FROM U.S.P.L. HAGAN AVE. ****/ | 2018-11-20 | MADE 4 X 4 CUT IN DOUBLE LAYER CONCRETE DRIVEWAY AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA
201801948901 | 2018-11-07 | LEAD | 2910 | N RAMPART |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 105222-426632 METER NUMBER - A198793 INLET SERVICE LEAKING INSIDE BOX /** 1) MN: A198793 SN: 0082400, *TAP: SIZE: A LOC: 117 FEET FROM P LINE AT MONTEGUT, *MB: CODE: ADK LOC: 117FT FROM URPL MONTEGUT ON N RAMPART ****/ | 2018-11-14 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801950001 | 2018-11-07 | LEAD | 1954 | LAW | LONDON AV | WILK | ML- METER LEAK METER# A417525 ACCT# 147612-488376 INLET SERVICE LEAK INSIDE METER BOX CARS ROLLING OVER METER /** 1) MN: A124317 SN: 0079871, *TAP: SIZE: A LOC: 213 FEET FROM P LINE AT LONDON AVE, *MB: CODE: CDLE LOC: ON LAW 213FT FROM LONDON ****/ | 2018-11-14 | EXCAVATED IN GUTTER BOTTOM + REPLACED 5/8 INCH CURB COCK + ALSO REPLACED 5/8 INCH METER BOX BOTTOM BACKFILLED + DRESSED UP AREA
201801950401 | 2018-11-07 | LEAD | 1330 | ALABO | N VILLERE | WILK | ML- METER LEAK MTR# A395762 ACCT# 144723-426035 EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A141378 SN: 0152308, *TAP: SIZE: A LOC: 240 FEET FROM P LINE AT URQUHART, *MB: CODE: BDKO LOC: RES ON ALABO 240FT FROM PL URQUHART ****/ | 2018-11-16 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA
201801952901 | 2018-11-07 | LEAD | 1920 | ST BERNARD AV | N PRIEUR | WILK | WM-LEAK ON THE SIDEWALK INLET SERVICE LEAK IN MUDPLOT FLOODING CURB AND STREET GETTING OFF IN DCB IN FRONT OF ABANDON LOT NEXT TO LIBRARY /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-20 | EXCAVATED TO FIND A 3/4 INCH ABANDON INLET SERVICE LEAKING REPAIRED WHERE THE LEAK WAS FOUND MADE A 4X4 MUD CUT BACKFILLED AND DRESS UP CUT
201801954001 | 2018-11-08 | LEAD/PLASTIC | 388 | BROADWAY | GARFIELD | WILK | WM-LEAK IN STREET INLET SERVICE LEAK IN ASPHALT STREET NEAR CURB, FLOODING GUTTER BOTTOM /** 1) MN: A135195 SN: 0009818, *TAP: SIZE: B LOC: 119 FEET FROM P LINE AT GARFIELD, *MB: CODE: AD LOC: 119' P.L. GARFIELD ****/ | 2019-03-09 | EXCVATED OVER 6"WATER MAIN .MADE REPAIR ON 1"TAIL PEICE AND TIED ISERVICE BACK IN BACKFILED RIVERSAND AND COLDMILL.(SOC 7FT. X 7 FT .CONCRETE BASE.)
201801956101 | 2018-11-08 | LEAD/PLASTIC | 3150 | MANSFIELD AV |  | WILK | WM-LEAK IN THE STREET INLET SERVICE LEAK BETWEEN CURB & STREET FLOODING AREA /** 1) MN: A321811 SN: 0150588, *TAP: SIZE: B LOC: 567 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: CDL6 LOC: ON MANSFIELD AVE., 25.8' FROM D.P.L. KENT, 2.5' ****/ | 2019-01-22 | WE EXACAVTED TO MAKE REPAIRS TO A 3/4 TAIL PEICE ON A 8" WATER MAIN IN THE SIDE WALK WE BACKFILL PLUS CLEAN UP
201801956501 | 2018-11-08 | LEAD | 722 | ALVAR | DAUPHINE | WOLK | ML- METER LEAK METER# A422460 ACCT# 127024-529789 EXAMINE OUTLET SERVICE FOR A LEAK WITH CONSTANT REGISTRATION /** 1) MN: A237764 SN: 0052008, *TAP: SIZE: A LOC: 136 FEET FROM P LINE AT DAUPHINE, *MB: CODE: CDM2 LOC: ON ALVAR,135' FROM U.R.P.L. DAUPHINE ****/ | 2019-01-10 | FOUND JOB COMPLETED WITH NO CONSTANT REGISTRATION + NO LEAK
201801956601 | 2018-11-08 | LEAD | 1918 | FOUCHER | DRYADES | WILK | ML- METER LEAK AT METER # B 041774 ACCT# 139942 - 727424 INLET SERVICE LEAK BEHIND CURB COCK, FLOODING MUDPLOT /** 1) MN: B032513 SN: 0029910, *TAP: SIZE: B LOC: 163 FEET FROM P LINE AT DRYADES, *MB: CODE: BDN4 LOC: METER ON FOUCHER 162.5 FT FROM PL DRYADES ****/ DOTTIE READY 12/12/18 EXP 01/01/19 | 2018-12-23 | ARRIVED AT ABOVE LOCTION,EXCAVATED AND MADE REPAIR TO STOP LEAK ON 3/4 INLET SERVICE LINE.BACKFILLED AND CLEANED UP JOB SITE TO COMPLETE JOB.
201801956801 | 2018-11-08 | LEAD | 5914 | N RAMPART | ALABO | WILK | ML- METER LEAKING METER# A278675 ACCT# 163701 - 426003 INLET SERVICE LEAK NEAR CURB /** 1) MN: A260314 SN: 0103680, *TAP: SIZE: A LOC: 50 FEET FROM P LINE AT GORDON, *MB: CODE: AD LOC: LPL CURB 50FT FROM PL GORDON 7' OUTSIDE ****/ | 2018-12-05 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND
201801956901 | 2018-11-08 | LEAD | 2441 | CHARTRES | SPAIN | WILK | METER BOX LEAK LOCATED ON SPAIN ST SIDE OF HOUSE; BEEN LEAKING FOR PAST FEW WEEKS INLET SERVICE LEAK IN SIDEWALK ON SPAIN /** 1) MN: A283031 SN: 0044131, *TAP: SIZE: A LOC: 38 FEET FROM P LINE AT CHARTRES, *MB: CODE: BDHN LOC: SIDE ST/SPAIN 38 FT FROM PL CHARTRES ****/ | 2018-11-26 | MADE 4 X 4 CUT IN DRIVEWAY AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201801957001 | 2018-11-08 | LEAD | 1428 | ST MAURICE AV | N ROBERTSON | WMTLK | MI: LEAK IN THE SIDEWALK CUST STATES LEAK OCCURED AFTER ENTERGY INSTALLED A POLE EXAMINE INLET AND OUTLET SERVICE IN MUDPLOT FOR A LEAK, SATURATED GRASS /** 1) MN: A114684 SN: 0093563, *TAP: SIZE: A LOC: 215 FEET FROM P LINE AT VILLERE N, *MB: CODE: BDL2 LOC: RES ON ST MAURICE 214FT FROM PL N VILLERE 6' OUT- ****/ | 2018-11-26 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201801957501 | 2018-11-08 | LEAD | 4238 | S CARROLLTON AV | D"HEMECOURT | WILK | ML-METER LEAK METER#C032383 ACCT3215582-505021 INLET SERVICE LEAK IN TREE ROOTS /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ DOTTIE READY 12/12/18 EXP 01/01/19 | 2018-12-30 | EXCAVATED AND REPAIRED INLET SERVICE LEAK IN TREE ROOTS. 3'X3' MUD CUT-->BACKFILLED--> NO DRESS UP NEEDED. JOB COMPLETE
201801958001 | 2018-11-08 | LEAD/PLASTIC | 2732 | LASALLE | WASHINGTON AV | WILK | MI--LEAK IN THE STREET INLET SERVICE LEAK BETWEEEN CURB/STREET FLOODING AREA /** 1) MN: E005623 SN: 0017108, *TAP: SIZE: CCC LOC: 65 FEET FROM P LINE AT WASHINGTON AVE, *MB: CODE: EN LOC: ON LASALLE 66FT FROM PL WASHINGTON AVE 4' OUTSIDE ****/ | 2018-11-17 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 3/4 ABANDON SERVICE LEAKING .REPLACED 8FT .OF 3/4 TUBING TIED INTO LEAD.(SOC8FT X 8FT . CONCRETE BASE)
201801959801 | 2018-11-09 | LEAD | 820 | BARTHOLOMEW |  | WOLK | INSP D JOHNSON STATES SERVICE IS LEAKING FROM BEHIND CASING. PLEASE REPAIR METER A432268 LOC ID 130422 EXAMINE OUTLET SERVICE @ PROPERTY LINE FOR A LEAK WITH CONSTANT REGISTRATION /** 1) MN: A125867 SN: 0060148, *TAP: SIZE: __ LOC: 152 FEET FROM P LINE AT DAUPHINE, *MB: CODE: BDM2 LOC: ON BARTHOLOMEW,153.6' FROM P.L. DAUPHINE ****/ | 2019-01-11 | REPLACED 5/8 INCH HANDWHEEL + GUTS I METER BOX
201801960401 | 2018-11-09 | LEAD | 830 | CONTI | BOURBON | WILK | MI- LEAK IN STREET ****** FLOODING AREA*** **********DAMAGE CLAIM********** J GILLIAM 11:28 BROKEN INLET SERVICE BY CONCRETE BY DESIGN, 329 CYPRESS LAKE DR, SLIDELL LA. 70458 (504) 723-0247 **DON ARMELIN*** /** 1) MN: E004328 SN: 0130233, *TAP: SIZE: E LOC: 198 FEET FROM P LINE AT BOURBON, *MB: CODE: OOO LOC: ON CONTI 198' FROM PL BOURBON 11' OUTSIDE PL ** 2) MN: SN: 0000000, *TAP: SIZE: H LOC: 79 FEET FROM P LINE AT DAUPHINE, *MB: CODE: __ LOC: ON CONTI ST 75.6' FROM URPL DAUPHINE 17.9' PL ****/ | 2018-11-10 | ARRIVED ON JOB SITE EXCAVATED IN MUD PLOT MADE REPAIRS ON A 2 INCH INCH SERVICE
201801961601 | 2018-11-09 | LEAD | 1801 | BIENVILLE |  | WOLK | LOCATION: 306369 MTR# A 417576 PER INSP UDEBOR, PLEASE REPAIR OUTLET SERVICE LEAKING. LEFT WATER OFF EXAMINE OUTLET SERVICE FOR A LEAK FOUND METER OFF LEFT METER OFF **HOUSE UNDER RENOVATIONS** /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-21 | EXCAVATED TO FIND A 5/8 INCH METER CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO MAKE THE REPAIRS
201801961801 | 2018-11-09 | LEAD | 2217 | TOURO | N MIRO | WMTLK | ML-METER LEAK ACCT#177931-495240 METER#A351181 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: A238628 SN: 0123186, *TAP: SIZE: A LOC: 138 FEET FROM P LINE AT MIRO N, *MB: CODE: CDM2 LOC: 138FT P/L N MIRO 7' OUTSIDE ****/ | 2018-11-20 | EXCAVATED 2 X 2 DRIVEWAY CUT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801962101 | 2018-11-09 | LEAD | 2314 | ANNETTE | TONTI | WMTLK | ML- METER LEAK MTR#A139360 ACCT #134370-431566 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: A321304 SN: 0068666, *TAP: SIZE: A LOC: 118 FEET FROM P LINE AT TONTI N, *MB: CODE: CD LOC: ON ANNETTE 118FT FROM N TONTI 27FT FROM CURB ****/ | 2018-11-21 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO MAKE THE REPAIRS
201801962901 | 2018-11-10 | LEAD | 5326 | WINGATE DR | RAPIDES DR | WOLK | ML- METER LEAK METER#A381025 ACCT#161705-504197 METER IN OFF POSITION MUST TURN ON TO FIND LEAK PROPERTY OCCUPIED *******CUSTOMER OUT OF WATER********* A LAGARDE @ 7:25AM EXAMINE OUTLET SERVICE @ PROPERTY LINE FOR LEAK /** 1) MN: A315544 SN: 0100218, *TAP: SIZE: A LOC: 12 FEET FROM P LINE AT RAPIDES DR, *MB: CODE: BDN3 LOC: ON WINGATE DR 12' FROM PL RAPIDES DR 7' OUTSIDE P ****/ | 2018-11-10 | ARRIVED ON JOB SITE EXAMINE CUSTOMER OUT OF WATER EXCAVAVTED IN MUD MUD PLOT BY HAND MADE REPAIRS ON SERVICE BACKFILLED DRESS UP WORK SITE
201801963901 | 2018-11-10 | LEAD | 1712 | KERLEREC | N ROMAN | WILK | LEAK ON THE SIDEWALK *****CHANGE FROM 1723 KERLEREC*** INLET AT THE CURB (C) /** 1) MN: A223380 SN: 0137678, *TAP: SIZE: A LOC: 137 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: ADEK LOC: 136FT FROM PL N DERBIGNY 7' OUTSIDE PL ****/ | 2018-11-20 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO MAKE THE REPAIRS MADE A 3 X3 MUD CUT BACKFILLED AND DRESS UP CUT
201801965101 | 2018-11-10 | LEAD | 1114 | MARIGNY | ST CLAUDE AV | WMTLK | LOCATIONID#113118-481204 METER#A420519 LEAK INSIDE METERBOX,KEEPS FILLING UP WHEN PUMPED OUT /** 1) MN: A289249 SN: 0047336, *TAP: SIZE: A LOC: 104 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: AF25 LOC: ON MARIGNY 105FT FROM ST CLAUDE ****/ | 2018-11-20 | EXCAVATED 2 X 2 CONCRETE DRIVEWAY CUT REPLACED 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA A BARREL WAS LEFT ON TOP OF CUT FOR SAFETY
201801965901 | 2018-11-11 | LEAD | 2711 | URSULINES AV | CRETE | WILK | ML- METER LEAK METER# A321060 ACCT#108102-563002 *PLEASE KNOCK ON DOOR WHEN INSPECTING METER, PER CUST REQUEST** EXAMINE INLET SERVICE FOR A LEAK 11/25/18 LEAK GETTING WORSE. PER S/R # 12858585 (PET) /** 1) MN: A321060 SN: 0017274, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT CRETE, *MB: CODE: BEM7 LOC: IN DRIVE 72' P.L. CRETE ****/ | 2018-11-27 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER COCK BACKFILLED AND CLEANED THE AREA
201801969601 | 2018-11-12 | LEAD | 1339 | TENNESSEE | N CLAIBORNE AV | WMTLK | ML- METER LEAK MTR# A432330 ACCT# 166471-593038 EXAMINE INLET AND OUTLET SERVICE FOR LEAK, METER UNDER WATER /** 1) MN: A146233 SN: 0107429, *TAP: SIZE: A LOC: 268 FEET FROM P LINE AT URQUHART, *MB: CODE: CDL LOC: ON TENNESSEE, 268' FROM P.L. URQUHART, 9' OUTSIDE ****/ | 2018-11-27 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201801970401 | 2018-11-12 | LEAD/PLASTIC | 2629 | ST PHILIP | N DORGENOIS | WILK | ML- METER LEAK MTR # A255026 ACCT# 110460-523689 CHANGED FROM 2627 ST PHILIP EXAMINE OUTLET SERVICE FOR LEAK IN BOX /** 1) MN: A195862 SN: 0011544, *TAP: SIZE: A LOC: 208 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CEM LOC: 209' P.L. N DORGENOIS ****/ | 2018-11-16 | EXCV 4 X 3 CUT IN SIDEWALK, REPLACED BOX STOP COCK RAISE TO GRADE BACKFILLED AND DRESS CUT WITH SAND AND COLDMILL.
201801970801 | 2018-11-12 | LEAD | 2532 | D"ABADIE |  | WILK | ML-METER LEAK ACCT#144942-489888 MTR#A399578 EXAMINE INLET SERVICE FOR LEAK IN BOX /** 1) MN: A318918 SN: 0076466, *TAP: SIZE: B LOC: 42 FEET FROM P LINE AT ROUSSELIN DR, *MB: CODE: ADLN LOC: 42FT FROM PL ROUSSELIN ON D ABADIE ****/ | 2018-11-26 | REPLACED 5/8 INCH WASHERS TO STOP LEAK
201801970901 | 2018-11-12 | LEAD | 1513 | JOURDAN AV | N ROBERTSON | WMTLK | ML-METER LEAK ACCT# 171398-422750 MTR#A407772 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: A256811 SN: 0114158, *TAP: SIZE: A LOC: 99 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: AEK LOC: RES ON JOURDAN 97FT FROM P.L. N.ROBERTSON 2' OUTSI ****/ | 2018-11-27 | MADE 2 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201801971601 | 2018-11-12 | LEAD | 1134 | GOV NICHOLLS | ST CLAUDE AV | WMTLK | ML-METER LEAK ACCT#121105-526234 MTR# A300117 EXAIMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A300117 SN: 0038863, *TAP: SIZE: A LOC: 548 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: CDM LOC: ON GOV. NICHOLLS,54.2' FROM U.R.P.L. ST. CLAUDE ****/ | 2018-11-26 | REPLACED 5/8 INCH WASHERS TO STOP LEAK
201801973801 | 2018-11-12 | LEAD | 2621 | DUMAINE | N DORGENOIS | WILK | WM-LEAK ON THE SIDEWALK INLET SERVICE LEAK BAD BLEEDER VALVE /** 1) MN: B028635 SN: 0055768, *TAP: SIZE: B LOC: 160 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: BEK5 LOC: ****/ | 2018-11-26 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 3/4 INCH METER BOX COCK BACKFILLED ND CLEANED THE AREA
201801974001 | 2018-11-12 | LEAD | 834 | LESSEPS | BURGUNDY | WILK | ML-METER LEAK METER#A279808 ACCT#131806-428887 INLET SERVICE LEAK IN METER BOX LEAKING FROM BLEEDER VALVE /** 1) MN: A279808 SN: 0062571, *TAP: SIZE: A LOC: 260 FEET FROM P LINE AT DAUPHINE, *MB: CODE: ADL LOC: ON LESSEPS 261' FROM PL DAUPHINE ****/ | 2018-11-26 | EXCAVATED 2 X 2 MUD PLOT THROUGH TREE ROOTS REPLACED 5/8 INCH METER COCK BACKFILLED AND CLEANED THE AREA
201801974401 | 2018-11-13 | LEAD | 813 | BARRACKS |  | WMTLK | LOCATIONID#110165-431491 METER#A258950 LEAK INSIDE METERBOX /** 1) MN: A258950 SN: 0015270, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT BOURBON, *MB: CODE: BEL5 LOC: ON BARRACKS 100 FT FROM PL BOURBON ****/ | 2019-02-14 | EXCAVATED 3 X 2 SIDEWALK CUT MADE REPAIR ON INLET SERVICE LINE AND REPLACE METER COCK BACKFILLED AND CLEANED THE AREA
201801975201 | 2018-11-13 | LEAD | 2309 | ANNETTE |  | WOLK | ML METERLEAK MTR#A211753 LOC/CUST#168727-496129 CONS REG ON METER. /** 1) MN: A269040 SN: 0110509, *TAP: SIZE: A LOC: 85 FEET FROM P LINE AT TONTI N, *MB: CODE: AD LOC: 86FT FROM PL N TONTI MTR ON ANNETTE 8FT OUTSIDE PL ****/ | 2018-11-21 | EXCAVATED IN GUTTER BOTTOM AND REPLACED 5/8 ICH CURB COCK BACKFILLED AREA
201801976501 | 2018-11-13 | LEAD | 2515 | BAYOU RD | N DORGENOIS | WOLK | ML- METER LEAK METER# A195112 ACCT#131637-489363 EXAMINE OUTLET SERVICE FOR LEAK CON REG /** 1) MN: A195112 SN: 0044932, *TAP: SIZE: A LOC: 120 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: __ LOC: ON BAYOU RD.,118.6' FROM S.P.L. NO. DORGENOIS ****/ | 2018-11-27 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801977401 | 2018-11-13 | LEAD/PLASTIC | 1119 | ERATO |  | WILK | INSP S BIBBINS WENT OUT FOR AN EXAMINE SERVICE ORDER AND FOUND THAT THE EMPTY BOX NEXT TO 1119 IS THE SERVICE LEAKING. CURB COCK BROKEN, VALVE IS IN THE OFF POSITION, AND IS LEAKING BADLY. PLEASE REPAIR LOC 217136 INLET SERVICE LEAK CURB COCK IN THE OFF POSITION WATER PASSING THROUGH, NO METER IN BOX /** 1) MN: A319005 SN: 0004334, *TAP: SIZE: B LOC: 163 FEET FROM P LINE AT CAMP, *MB: CODE: AEK2 LOC: ON ERATO 163FT FROM SPL OF MAGAZINE ****/ | 2018-12-24 | EXAMINED AREA CUT OUT CONCRETE EXCAVATED ON METER BOX INLET OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK BACKFILLED CLEANED AREA PICKED UP ROCKS AND DEBRIS LEAD ON INLET SERVICE. JOB COMPLETE
201801977601 | 2018-11-13 | LEAD | 2914 | CLEVELAND AV |  | WMTLK | LOCATIONID#106504-531125 METER#A119642 LEAK INSIDE METERBOX /** 1) MN: A220587 SN: 0043851, *TAP: SIZE: A LOC: 114 FEET FROM P LINE AT GAYOSO S, *MB: CODE: ADN LOC: ****/ | 2018-11-27 | EXCAVATED 2 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201801977701 | 2018-11-13 | LEAD | 2004 | DUMAINE |  | WILK | LOCATION: 123824 INSP UDEBOR EXAMINE METER, FOUND INLET SERVICE NEED REPAIRS, LEAKING BEHIND CURB COCK. PLEASE REPAIR AND CHANGE MTR# A 335440 INLET SERVICE LEAK ALSO CHNAGE METER **********J GILLIAM 09:06********** 11/19/18 PER INSP K GRIFFIN UPGRD TO AN A GIVE OUT CUSTOMER NOW OUT OF WATER /** 1) MN: A252637 SN: 0043700, *TAP: SIZE: B LOC: 37 FEET FROM P LINE AT PRIEUR N, *MB: CODE: ADL1 LOC: 38' P.L. N PRIEUR ****/ | 2018-11-19 | EXCAVATED 3 X 2 SIDEWALK CUT MADE REPAIRS INLET SERVICE TO STOP LEAK BACKFILLED AND CLEAN THE AREA
201801977801 | 2018-11-13 | LEAD | 2208 | TOURO |  | WILK | ML-METER LEAK ACCT#120962-494989 MTR#A413416 EXAMINE INLET SERVICE FOR LEAK CARS PARKING ON METER /** 1) MN: A113802 SN: 0058274, *TAP: SIZE: A LOC: 65 FEET FROM P LINE AT MIRO N, *MB: CODE: AEK1 LOC: ON TOURO 66.4FT FROM PL OF N MIRO 2FT INSIDE CURB ****/ | 2018-11-27 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801978201 | 2018-11-13 | LEAD | 2473 | N RAMPART | ST ROCH AV | WMTLK | ML: METER LEAK METER# A272073 ACCT# 113360-441227 EXAMINED INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A272073 SN: 0018386, *TAP: SIZE: A LOC: 66 FEET FROM P LINE AT ST ROCH AVE, *MB: CODE: BEKO LOC: METER ON N RANPART 66 FT FROM PL ST ROCH AVE ****/ | 2018-11-27 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201801978301 | 2018-11-13 | LEAD | 2024 | BAYOU RD |  | WILK | ML--METER LEAK METER#A416233 ACCOUNT#124563-585747 INLET SERVICE LEAK NO METER IN BOX /** 1) MN: A229052 SN: 0039888, *TAP: SIZE: B LOC: 50 FEET FROM P LINE AT JOHNSON N, *MB: CODE: OOO LOC: ON BAYOU ROAD 48.5' FROM URPL N JOHNSON ****/ | 2018-11-27 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201801980101 | 2018-11-14 | LEAD | 2025 | ALMONASTER AV | N GALVEZ | WMTLK | PP-POOR PRESSURE ACCT#112827-479291 METER#A407531 EXAMINE INLET AND OUTLET SERVICE FOR LEAK *****CUSTOMER ALSO HAD A LEAK INSIDE PROPERTY LINE PASS STOP AND WASTE***** /** 1) MN: A269473 SN: 0073188, *TAP: SIZE: A LOC: 161 FEET FROM P LINE AT GALVEZ N, *MB: CODE: CDN LOC: ON ALMONASTER 160.3FT FROM GALVEZ ****/ | 2018-12-03 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801981301 | 2018-11-14 | LEAD | 1717 | DELERY |  | WMRE | INSP L UDUEBOR STATES SERVICE IS BURIED. PLEASE RAISE TO GRADE AND CHANGE METER A403227 LOC 186423 LOCATE, RAISE TO GRADE AND CHANGE METER /** 1) MN: A317591 SN: 0141106, *TAP: SIZE: B LOC: 129 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: ADM2 LOC: ON DELERY 131FT FROM PL N DERBIGNY 7FT OUTSIDE PL ****/ | 2018-11-30 | EXCAVATED 3 X 2 LIMESTONE AREA FIND METER BOX UP TO GRADE REMOVED LIMESTONE FROM AREA ALSO MARKED METER TOP WITH BLUE MARKING PAINT
201801981801 | 2018-11-14 | LEAD | 2649 | LOUISA | FLORIDA AV | WILK | ML-METER LEAK ACCT#220631-725643 METER#A417636 EXAMINE INLET SERVICE FOR LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-11-28 | EXCAVATED 9 X 7 DRIVEWAY CUT CAULK 12 INCH BELL JOINT TO STOP LEAK BACKFILLED AND CLEAN ED THE AREA LEFT BARRELS AND FLAGS AROUND CUT DUE TO AREA SATURATED WITH WATER AREA SAFETY
201801983501 | 2018-11-14 | LEAD | 2612 | N RAMPART | ALMONASTER AV | WOLK | PP : POOR PRESSURE ACCT#116904-480786 METER# A415144 EXAMINE OUTLET SERVICE AT PROPERTY LINE FOR LEAK WITH CONSTANT REGISTRATION ON METER /** 1) MN: A320794 SN: 0061690, *TAP: SIZE: C LOC: 114 FEET FROM P LINE AT ALMONASTER, *MB: CODE: AEK LOC: 114FT FROM PL ALMONASTER ****/ | 2018-11-27 | REPLACED 5/8 INCH WASHERS
201801983601 | 2018-11-14 | LEAD | 1435 | LIZARDI | VILLERE | WMTLK | MI: LEAK IN SIDEWALK EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A153607 SN: 0117326, *TAP: SIZE: A LOC: 260 FEET FROM P LINE AT VILLERE N, *MB: CODE: BDL LOC: RES 265FT P.L. N.VILLERE OPP 1435 DOOR CRB 7' ****/ | 2018-11-30 | EXCAVATED 4 X 4 MUD PLOT MADE REPAIR ON INLET SERVICE LINE TO STOP LEAK
201801984301 | 2018-11-14 | LEAD | 1218 | FRENCHMEN | MARAIS | WILK | ML-METER L;EAK METER#A390341 ACCT#127040-487257 INLET SERVICE LEAK COMING FROM CURBCOCK /** 1) MN: A196591 SN: 0051836, *TAP: SIZE: A LOC: 132 FEET FROM P LINE AT MARAIS, *MB: CODE: AEKN LOC: ON FRENCHMEN,132; FROM U.S.P.L. MARAIS ****/ | 2018-11-27 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201801986401 | 2018-11-15 | LEAD | 1530 | PAINTERS |  | WILK | ML-- METER LEAK METER# A345521 ACCT# 205749-483170 INLET SERVICE LEAK NO METER IN BOX /** 1) MN: A345521 SN: 0054844, *TAP: SIZE: B LOC: 19 FEET FROM P LINE AT NO. ROBERTSON, *MB: CODE: OOO LOC: ON PAINTERS, 20' FROM D.P.L. NO. ROBERTSON, 9' ****/ | 2018-12-05 | EXCAVATED 4 X 2 GUTTER BOTTOM ALSO 5 X 4 SIDEWALK CUT RELOCATED METER BOX FROM GUTTER TO SIDEWALK TO PREVENT FUTURE VEHICLES ROLLING OVER THEM BACKFILLED AND CLEANED THE AREA
201801989001 | 2018-11-15 | LEAD | 2809 | ESPLANADE AV |  | WOLK | LOCATION ID-160857 MTR-D005388 LEAK BETWEEN STOP & WASTE AND MTR/CONS REG ON MTR EXAMINE OUTLET SERVICE FOR LEAK WITH CONSTANT REGISTRATION NO VISIBLE STOP-N-WASTE VALVE /** 1) MN: D005388 SN: 0050795, *TAP: SIZE: D LOC: 130 FEET FROM P LINE AT WHITE N, *MB: CODE: BDI2 LOC: ON LEPAGE 131FT FROM PL N WHITE 10' OUTSIDE PL 2' ****/ | 2018-12-03 | EXAMINE JOB + DID PERFORM STOP + WASTE TEST FOUND NO CONSTANT REGISTRATION BETWEEN METER AND STOP + WASTE
201801995901 | 2018-11-16 | LEAD | 908 | MONTEGUT | BURGUNDY | WILK | ML-METER LEAK METER#A197739 ACCT#112257-426663 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A293413 SN: 0014056, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT BURGUNDY, *MB: CODE: BFK LOC: ON MONTEGUT,75' FROM U.S.P.L. BURGUNDY ****/ | 2018-11-29 | EXCAVATED 2 X 2 BRICK SIDEWALK REPLACED 5/8 INCHMETER BOX COCK BACKFILLED AND CLEANED THE AREA
201801997002 | 2018-11-30 | LEAD | 3316 | N GALVEZ | DESIRE | WILK | EXAMINED JOB AT ABOVE LOCATION AND FOUD LEAK ON 2 INCH METER BOX LAUNDRY MAT MANAGEMENT OF THE BUSSINESS WAS UNABAILBLE TO MAKE ARRANGEMENT JOB REFER BACK TO ZONE 4 /** 1) MN: SN: 0177032, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT DESIRE, *MB: CODE: CD LOC: ON GALVEZ 150FT FROM P/L DESIRE ** 2) MN: E007221 SN: 0177032, *TAP: SIZE: E LOC: 126 FEET FROM P LINE AT PIETY, *MB: CODE: CD LOC: ON GALVEZ 126FT ROM PIETY 2FT OUTSIDE ****/ | 2019-01-20 | REPLACED 2 INCH UNION IN MANHOLE AT ABOVE LOCATION
201801997101 | 2018-11-17 | LEAD | 1600 | ELYSIAN FIELDS AV | N CLAIBORNE AV | WMLK | MI-LEAK IN STREET IN FRONT OF WALGREEN'S BY TREE LEAK ON WATER MAIN BETWEEN SAIDEWALK/CURB GETTING OFF INTO DRAIN CATCH BASIN LEAK LOCATED UNDERNEATH TREE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-11 | EXCAVATED 4 X 2 MUD PLOT THROUGH TREE ROOTS MADE REPAIR ON ABANDON INLET SERVICE LINE BACKFILLED NAD CLEANED THE AREA
201802000101 | 2018-11-18 | LEAD | 3404 | N RAMPART | DESIRE | WILK | ML-METER LEAK METER# A405059 ACCT#139057-427266 INLET SERVICE LEAK IN THE SIDEWALK FLOODING CURB CAUSING POOR PRESSURE /** 1) MN: SN: 0069642, *TAP: SIZE: A LOC: 53 FEET FROM P LINE AT DESIRE, *MB: CODE: CEMN LOC: 53FT FROM PL DESIRE ****/ | 2018-11-29 | EXCAVATED 4 X 2 SIDEWALK MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201802000501 | 2018-11-19 | LEAD | 1513 | N DORGENOIS | COLUMBUS | WOLK | ML MTR# A319872 LOC & CUST# 118870/487859 SERVICE ADDRESS: 1503 N DORGENOIS ST. INSP COMMENT: F/ ON-L/ON, NO CONS, NO VISIBLE OUTSIDE FAUCET NALT /** 1) MN: A319872 SN: 0029773, *TAP: SIZE: __ LOC: 100 FEET FROM P LINE AT COLUMBUS, *MB: CODE: CDM LOC: 105FT FROM LSPL COLUMBUS ****/ | 2018-12-03 | REPLACED 5/8 INCH WASHERS TO STOP LEAK
201802001501 | 2018-11-19 | LEAD/PLASTIC | 7805 | WILLOW | BURDETTE | WILK | WILK WATER LEAK-INLET SERVICE (COTRACTORS WENT OUT TO PAVE CUT AND FOUND JOB STILL LEAKING.) /** 1) MN: A139221 SN: 0062628, *TAP: SIZE: A LOC: 39 FEET FROM P LINE AT BURDETTE, *MB: CODE: CEM2 LOC: METER ON WILLOW 39 FT FROM PL BURDETTE ****/ | 2018-11-18 | MADE CUT IN STREET EXCAVATED IN MUDPLOT AND MADE REPAIR ON 3/4" INLET SERVICE LEAD LINE AND BACKFILLED. (SOC 4FT .X 4 FT. ASPHALT F/D)
201802003001 | 2018-11-19 | LEAD | 1817 | GEN TAYLOR |  | WILK | ML-- METER LEAK METER # A336476 ACCT # 119984-554924 READYINLET SERVICE LEAK BEHIND CURB COCK, FLOODING GRASS AND SIDEWALK /** 1) MN: A336476 SN: 0034364, *TAP: SIZE: A LOC: 128 FEET FROM P LINE AT BARONNE, *MB: CODE: BFL LOC: ON GEN TAYLOR 128.4FT FROM PL OF BARONNE ****/ DOTTIE READY 12/21/18 EXP 01/10/19 | 2018-12-30 | EXCAVATED IN MUD PLOT + REPLACED5/8 INC CURB COCK BACKFILED + DRESSED UP AREA
201802003401 | 2018-11-19 | LEAD | 1433 | TENNESSEE |  | WILK | WM-- LEAK IN STREET INLET SERVICE LEAK @ THE MAIN CALLER INQ. ABOUT W/O REPAIR /** 1) MN: A126332 SN: 0107284, *TAP: SIZE: A LOC: 132 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: ADL LOC: ON TENNESSEE, 132' FROM P.L. NO. ROBERTSON, 9' OUT ****/ | 2018-12-03 | MADE 6 X 6 CUT IN CONCRETE STREET AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201802003801 | 2018-11-19 | LEAD | 3114 | BANKS | S LOPEZ | WMTLK | ML METER LEAK METER# A357759 EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN BOX, FLOODING MUDPLOT HOUSE UN DER CONSTRUCTION /** 1) MN: A147504 SN: 0014565, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT LOPEZ S, *MB: CODE: CD LOC: ON BANKS 76FT FROM LOPEZ S ****/ | 2018-11-29 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201802004301 | 2018-11-19 | LEAD | 1008 | ST PETER | BURGUNDY | WILK | MI- LEAK IN THE SIDE WALK EXAMINE INLET SERIVE FOR A LEAK IN THE SIDEWALK /** 1) MN: A278519 SN: 0026940, *TAP: SIZE: A LOC: 52 FEET FROM P LINE AT BURGUNDY, *MB: CODE: OOOO LOC: 58' P/L BURGUNDY 4' OUTSIDE 4' INSIDE CURB ****/ | 2018-12-05 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802005101 | 2018-11-19 | LEAD | 623 | BARTHOLOMEW | CHARTRES | WILK | ML- METER LEAK ACCT# 128515-715837 MTR# A313469 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A313469 SN: 0031204, *TAP: SIZE: A LOC: 135 FEET FROM P LINE AT ROYAL, *MB: CODE: BEL2 LOC: ON BARTHOLOMEW 137FT FROM LRPL ROYAL ****/ | 2019-01-09 | EXCVATED 3 X 2 SIDEWALK CUT REPLACED BROKEN METER BOTTOM AND 5/8 INCH METER COCK BACKFILLED AND CLEANED THE AREA
201802005501 | 2018-11-19 | LEAD | 3616 | N RAMPART | CONGRESS | WILK | **********PICK UP********** INLET SERVICE LEAK NO METER IN BOX /** 1) MN: 000000 SN: 0054095, *TAP: SIZE: B LOC: 115 FEET FROM P LINE AT CONGRESS, *MB: CODE: CELN LOC: ON N RAMPART 116FT FROM PL CONGRESS 10' OUTSIDE PL ****/ | 2018-12-04 | EXACAVTED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA
201802006701 | 2018-11-19 | LEAD | 1023 | N DORGENOIS |  | WOLK | LOCATION ID-301989 MTR-A428824 MTR LEAK/MTR BOX OVER FLOWING/AREA FLOODED/CONS REG ON MTR EXAMINE OUTLET SERVICE FOR A LEAK @ PROPERTY LINE WITH CONSTANT REGISTRATION ON THE METER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-03 | EXCAVATED 3 X 2 MUD PLOT THROUGH SMALL LIMESTONE ROCK REPLACED 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA
201802007201 | 2018-11-19 | LEAD | 856 | OLGA | DUMAINE | WILK | ML-METER LEAK INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A311614 SN: 0037469, *TAP: SIZE: A LOC: 161 FEET FROM P LINE AT DUMAINE, *MB: CODE: CFM LOC: 161FT FROM URPL DUMAINE ON OLGA ST ****/ | 2018-12-03 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802007601 | 2018-11-19 | LEAD | 2616 | FLOOD |  | WMTLK | ML-- METER LEAK METER # A331262 ACCT # 161953-727573 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: A267262 SN: 0135608, *TAP: SIZE: A LOC: 127 FEET FROM P LINE AT LAW, *MB: CODE: ADN2 LOC: ON FLOOD, 127' FROM P.L. LAW, 7' OUTSIDE P.L. ****/ | 2018-12-04 | EXCAVATED 2 X 2 DRIVEWAY CUT REPLACED 5/8 INCH METER BOX COCK TO SHOP LEAK BACKFILLED AND CLEANED THE AREA
201802007701 | 2018-11-19 | LEAD | 2619 | DAUPHINE | FRANKLIN AV | WMTLK | ML - METER LEAK MTR # A414187 ACCT # 103531-706689 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: A288224 SN: 0053547, *TAP: SIZE: A LOC: 105 FEET FROM P LINE AT PORT, *MB: CODE: CEM LOC: ON DAUPHINE 105FT FROM USPL OF PORT ****/ | 2018-12-07 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802009001 | 2018-11-19 | LEAD | 2109 | COLUMBUS | N GALVEZ | WMTLK | ML- METER LEAK METR #A417572 ACCT# 125978-488196 *FLOODING AREA*** CHANGED FROM 2019 COLUMBUS EXAMINE INLET AND OUTLET SERVICE INSIDE METER BOX FOR A LEAK /** 1) MN: A306317 SN: 0048705, *TAP: SIZE: A LOC: 70 FEET FROM P LINE AT GALVEZ NO., *MB: CODE: CD LOC: ON COLUMBUS,69.5' FROM L.S.P.L. NO. GALVEZ ****/ | 2018-12-05 | EXCAVATED 4 X 6 LIMESTONE GUTTER BOTTOM FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201802009501 | 2018-11-19 | LEAD/PLASTIC | 2422-24 | JOSEPH |  | WILK | MI LEAK IN THE STREET (CURB) INLET SERVICE LEAK IN ASPHALT STREET FROM OLD PATCH /** AT 2422: 1) MN: A263106 SN: 0070286, *TAP: SIZE: A LOC: 216 FEET FROM P LINE AT MAGNOLIA, *MB: CODE: BDN1 LOC: ON JOSEPH 159' FROM PL MAGNOLIA 1' FROM CURB ****/ DOTTIE READY 11/26/19 EXPIRATION DATE 12/16/18 | 2018-11-28 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 3/4 CORP. COCK LEAKING.REPLACED CORP.COCK AND 6FT. OF 3/4 TUBING TIED INTO 3/4 TUBING AT CURB.(SOC 8FT. X 8 FT .ASPHALT STREET)
201802010001 | 2018-11-20 | LEAD | 219 | N PETERS | IBERVILLE | WOLK | ML METERLEAK MTR#B036113 LOC/CUST#106635-527017 CONS REG ON METER. /** 1) MN: SN: 0010110, *TAP: SIZE: B LOC: 136 FEET FROM P LINE AT IBERVILLE, *MB: CODE: BEM6 LOC: 129FT FROM LSPL IBERVILLE ****/ | 2019-02-01 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED HANDWHEEL INSIDE METER BOX LEAK STILL EXIST CAUSING CONSTANT REGISTRATION REFER BACK TOPROPERTY OWNER FOR LEAK ON PROPERTY BACKFILLED AND CLEANED THE AREA
201802010201 | 2018-11-20 | LEAD/PLASTIC | 2818 | ST ANDREW |  | WMRE | LOCATION: 306430 METER REMOVED IN 2006 PER INSP S BIBBINS - UNABLE TO LOCATE METER BOX. PLEASE LOCATE AND SET A 5/8 METER. CUSTOMER WAITING ON WATER LOCATE, RAISE TO GRADE AND SET 5/8 METER NO ONE LIVES @ LOCATION, HOUSE UNDER RENOVATION /** 1) MN: A291408 SN: 0022874, *TAP: SIZE: A LOC: 135 FEET FROM P LINE AT CLARA, *MB: CODE: AFKO LOC: 134FT FROM SPL CLARA,METER ON ST ANDREW ****/ DOTTIE READY 11/27/18 EXPIRATION 12/17/18 | 2018-12-11 | EXCAVATED IN MUDPLOT FOUND INLET SERVICE.SET 5/8 METER BOX AND 5/8 METER.RAISE METER TO GRADE.
201802010601 | 2018-11-20 | LEAD | 2707 | N CLAIBORNE AV |  | WILK | INSP D JOHNSON STATES SERVICE IS LEAKING FROM INLET, BEHIND THE CASING. PLEASE REPARI METER A432308 LOC 222828 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: B021091 SN: 0077639, *TAP: SIZE: B LOC: 61 FEET FROM P LINE AT PORT, *MB: CODE: CEL1 LOC: 60' P.L. PORT ****/ | 2018-12-03 | EXCAQVATED IN CONCRETE SIDEWALK + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA ALSO REPLACED 1 INCH TEE IN CUT
201802010701 | 2018-11-20 | LEAD | 813 | DECATUR |  | UNKN | INSP L UDUEBOR STATES BRICKS AND CEMENT IN METER BOX, UNABLE TO CHANGE METER. PLEASE REPAIR AND CHANGE METER A379205 LOC 106752 UNABLET TO INSTALL NEW METER DUE TO CONCRETE & BRICK IN THE BOX /** 1) MN: A124833 SN: 0027957, *TAP: SIZE: A LOC: 42 FEET FROM P LINE AT MADISON, *MB: CODE: BEL1 LOC: ON DECATUR,43' FROM U.S.P.L. MADISON ****/ | 2019-01-17 | REMOVE CEMENT FROM INSIDE OF METER BOX AND REPLACE 5/8 INCH METER *****************OLD METER INFO************* METER:A379205 FAC:73273636 MAKE:SENSUS READ:14229
201802011601 | 2018-11-20 | LEAD | 2257 | MARAIS | MARIGNY | WMTLK | ML- METER LEAK MTR # A418578 ACCT #128006-481434 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER LOCATED IN DRIVE /** 1) MN: A290662 SN: 0054708, *TAP: SIZE: A LOC: 123 FEET FROM P LINE AT MARIGNY, *MB: CODE: AD2 LOC: ON MARAIS,120.4' FROM L.S.P.L. MARIGNY ****/ | 2018-12-13 | REPLACED 5/8 INCH HABDWHEEL + GUTS IN METER BOX
201802012201 | 2018-11-20 | LEAD | 1701 | N GALVEZ |  | WMTLK | BAD MTR LEAK/MTR BOX OVER FLOWING/AREA FLOODED/VERY HAZARDOUS EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** 1) MN: SN: 0170457, *TAP: SIZE: B LOC: 58 FEET FROM P LINE AT N GALVEZ, *MB: CODE: ENF1 LOC: ON N GALVEZ 31' FROM PLN GALVEZ 6' OUTSIDE PL 9' I ****/ | 2018-12-05 | EXCAVATED 8 X 4 MUD PLOT THROUGH BRICK AND CONCRETE RAISED METER BOX UP TO GRADE BACKFILLED AND CLEANED THE AREA
201802012301 | 2018-11-20 | LEAD/PLASTIC | 437 | 1ST |  | WMTLK | INSP S BIBBINS STATES LOCATION NEEDS NEW SERVICE (OUTDATED SERVICE CURRENTLY AT LOCATION), HE IS UNABLE TO SET METER. CUSTOMER IS WAITING ON WATER. PLEASE REPAIR AND SET 5/8 METER. LOC 306372 EXAMINE INLET & OUTLET SERVICE FOR A LEAK , ALSO INSTALL HANDWHEEL , CURB COCK & 5/8 METER. ****HOUSE UNDER RENOVATIONS**** /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-26 | EXAMINED AREA TRUCK LINE TO FIND SERVICE THROUGH ROOTS AND BRICKS UNDER MUD ON CONSTRUCTION SITE IN FRONT HOUSE INSTALLED METER AND METER BOX COMPLETE BACKFILLED INLET AND CLEANED AREA LEAD ON INLET NEED TO BE REMOVED
201802013001 | 2018-11-20 | LEAD | 2915 | DUMAINE | N DUPRE | WOLK | **********PICK UP********** OUTLET SERVICE LEAK BEHIND HANDWHEEL METR IN SIDEWALK /** 1) MN: A224526 SN: 0030603, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT DUPRE N, *MB: CODE: CE LOC: 112' P.L. N DUPRE ****/ | 2018-12-05 | REPLACED BROKEN 5/8 INCH HANDWHEEL INSIDE OF BOX AT ABOVE LOCATION
201802014601 | 2018-11-20 | LEAD | 3022 | ST PHILIP | S SALCEDO | WOLK | PP-POOR PRRESSURE***A317714 EXAMINE OUTLET SERVICE FOR A LEAK /** 1) MN: A317714 SN: 0064956, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT SALCEDO NO., *MB: CODE: BD LOC: ON ST. PHILIP, 95' FROM U.R.P.L. NO. SALCEDO ****/ | 2018-12-04 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX NO OTHER LEAK EXCELLENT PRESSURE AT METER + BOTH FAUCETS
201802015001 | 2018-11-20 | LEAD | 1919 | MARIGNY | ELYSIAN FIELDS AV | WMLK | WM-LEAK IN THE STREET FLOODING AREA EXAMINE LEAK ON WATER MAIN IN STREET COMING FROM OLD SERVICE IN FRONT OF VACANT LOT /** 1) MN: A336012 SN: 0175160, *TAP: SIZE: A LOC: 129 FEET FROM P LINE AT PRIEUR N, *MB: CODE: BF LOC: ON MARIGNY 129FT FROMPL OF N PRIEUR ****/ | 2018-12-03 | EXAMINED ARA AT ABOVE LOCATION + FOUND LEAK COMING FROM METER IN MUD PLOT NO STREET LEAK EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201802017601 | 2018-11-21 | LEAD | 4120 | N TONTI |  | WILK | LOCATION ID-164634 MTR-A406480 MTR LEAK INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A320771 SN: 0104601, *TAP: SIZE: B LOC: 181 FEET FROM P LINE AT MAZANT, *MB: CODE: ADK LOC: ON N TONTI 164' FROM PL MAZANT 7' OUTSIDE PL ****/ | 2018-11-30 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH METER COCK BACKFILLED AND CLEANED THE AREA
201802018101 | 2018-11-21 | LEAD | 6325 | ST CLAUDE AV | TRICOU | WMTLK | ML- METER LEAK METER# A409048 ACCT# 180120-426538 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** 1) MN: A286061 SN: 0087875, *TAP: SIZE: A LOC: 186 FEET FROM P LINE AT TRICOU, *MB: CODE: ADK2 LOC: ON ST CLAUDE 186FT FROM PL TRICOU 11FT OUTSD ** 2) MN: A126258 SN: 0087875, *TAP: SIZE: A LOC: 186 FEET FROM P LINE AT TRICOU, *MB: CODE: __ LOC: ON ST. CLAUDE AVE., 183' FROM P.L. TRICOU, 9' OUT- ****/ | 2018-12-03 | EXCAVATED IN SMALL TREE ROOTS IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201802019701 | 2018-11-21 | LEAD | 611 | DESIRE |  | WMTLK | ML METER LEAK ACCOUNT#127763-427874 METER #A415318 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK METER BOX UNDER WATER IN DRIVEWAY /** 1) MN: A258779 SN: 0054064, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT CHARTRES, *MB: CODE: BDO2 LOC: 94FT FROM LSPL CHARTRES ON DESIRE ****/ | 2019-01-19 | MADE 4 X 4 CUT IN SIDEWALK AND MADE REPAIRS ON 3/4 INCH OUTLET SERVICE BACKFILLED AREA NO CONSTRANT REG ON METER
201802023801 | 2018-11-23 | LEAD | 2704 | N VILLERE | PORT | WMTLK | ML- METER LEAK METER# A416850 ACCT# 121284-426941 EXAMINE INLET AND OUTLET SERVICE INSIDE METER BOX FOR A LEAK /** 1) MN: A285390 SN: 0057075, *TAP: SIZE: A LOC: 38 FEET FROM P LINE AT PORT, *MB: CODE: CFLM LOC: 37' P.L. PORT ****/ | 2018-12-03 | REPLACED 5/8 INCH HANDWHEEL AND GUTS IN METER BOX
201802025201 | 2018-11-24 | LEAD | 2401 | ORLEANS AV | N TONTI | WILK | ML- METER LEAK METER# A120632 ACCT# 123425-524393 INLET SERVICE LEAK IN BOX /** 1) MN: A120632 SN: 0042709, *TAP: SIZE: A LOC: 58 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: OOO LOC: ON N TONTI ST 56.5' FROM LSPL ORLEANS AVE ** 2) MN: A337992 SN: 0042709, *TAP: SIZE: A LOC: 62 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: __ LOC: 62' P/L ORLEANS AV 8' OUTSIDE ON N TONTI THERE ARE 2 MORE NOT LISTED. ****/ | 2018-12-04 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA ALSO REPLACED 5/8 INCH METER BOX BOTTOM
201802025801 | 2018-11-24 | LEAD | 1100BLK | LEBOUEF | DIANA | WILK | MI- LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT FROM OLD PATCH GETTING OFF INTO DRAIN CATCH BASIN **CHANGED FROM 1000BLK LEBOUEF** /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-26 | ARRIVED ON JOB SITE EXAMINE AREA FOUND NO LEAK
201802029201 | 2018-11-26 | LEAD/PLASTIC | 425 | 2ND |  | WMTLK | LOCATIONID#208543-541674 METER#A118219 LEAK INSIDE METERBOX /** 1) MN: A118219 SN: 0052182, *TAP: SIZE: A LOC: 7 FEET FROM P LINE AT ROUSSEAU, *MB: CODE: __ LOC: ON SECOND 8FT FROM DIV PL ROUSSEAU 9'OUTSD PL ****/ | 2019-01-09 | ARRIVED ON JOB SITE EXAMINED LEAK IN MUD PLOT EXCAVATED IN MUD PLOT BY HAND MADE REPAIRS ON SERVICE BACKFILLED DRESS UP WORK SITE
201802031601 | 2018-11-26 | LEAD | 4610 | PRYTANIA | CADIZ | WILK | ML-METER LEAK ACCT# 107536-561017 METER# A335229 INLET SERVICE LEAK BAD CURB COCK FLOODING SIDEWALK /** 1) MN: A335229 SN: 0017138, *TAP: SIZE: A LOC: 89 FEET FROM P LINE AT CADIZ, *MB: CODE: BFMN LOC: 89 FT FROM PL CADIZ ****/ DOTTIE READY 12/21/19 EXPIRATION 1/10/19 | 2018-12-29 | EXCAVATED AND REPAIRED INLET SERVICE LEAK TREE ROOTS SLOWED PROGRESS 3X3 SIDEWALK CUT->BACKFILLED-> NEED PAVING
201802032301 | 2018-11-26 | LEAD | 640 | N PIERCE | ORLEANS AV | WILK | ML METER LEAK METER #A196475 INLET SERVICE LEAK /** 1) MN: A196475 SN: 0037426, *TAP: SIZE: A LOC: 167 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: CEM2 LOC: ON NO. PIERCE,163' FROM U.R.P.L. ORLEANS AVE. ****/ | 2018-12-12 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE IN SIDEWALK BACKFILLED JOB WITH RIVERSAND COLDMILL
201802033201 | 2018-11-26 | LEAD | 1611 | PRYTANIA | TERPSICHORE | WILK | **********PICK UP********** INLET SERVICE LEAK BAD BLEEDER VALVE FLOODING SIDEWALK /** 1) MN: A226998 SN: 0014019, *TAP: SIZE: B LOC: 93 FEET FROM P LINE AT TERPSICHORE, *MB: CODE: CEL LOC: 92FT FROM USPL OF TERPSICHORE ****/ DOTTIE READY12-21-18 EXPIRATION 1/10/19 | 2018-12-29 | REPLACED 5/8 INCH HANDWHEEL + WASHERS IN METER BOX
201802033501 | 2018-11-26 | LEAD | 2126 | ARTS |  | WMTLK | ML- METER LEAK MTR# A415925 ACCT # 304623-483507 EXAMINE INLET & OUTLET SERVICE FOR A LEK CARS ROLLING OVER METER /** 1) MN: A118953 SN: 0102537, *TAP: SIZE: A LOC: 102 FEET FROM P LINE AT MIRO N, *MB: CODE: CDKL LOC: ON ARTS, 102' FROM P.L. NO. MIRO, 8' OUTSIDE P.L. ****/ | 2018-12-07 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802033601 | 2018-11-26 | LEAD | 1721 | MONTEGUT |  | WMTLK | ML-METER LEAK ACCT#304197-703397 MTR#A431160 EXAMINE INLET & OUTLET SERVICE FOR A LEAK CARS ROLLING OVER METER /** 1) MN: SN: 0103079, *TAP: SIZE: B LOC: 168 FEET FROM P LINE AT N DERBIGNY, *MB: CODE: BGT LOC: ON MONTEGUT, 168' FROM P.L. NO. DERBIGNY, 7' OUT- ****/ | 2018-12-04 | REPLACED HANDWHEEL INSIDE METER BOX AND WASHERS TO STOP LEAK
201802035401 | 2018-11-26 | LEAD | 1025 | N BROAD | ST PHILIP | WOLK | ML- METER LEAK MTR# A402930 ACCT# 127167-521039 OUTLET SERVICE LEAK WITH CONSTANT REGISTRATION IN SIDEWALK /** 1) MN: A280674 SN: 0052458, *TAP: SIZE: A LOC: 118 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: CDN4 LOC: ** 2) MN: SN: 0052458, *TAP: SIZE: A LOC: 118 FEET FROM P LINE AT URSULINES AVE., *MB: CODE: __ LOC: ON NO. BROAD,119' FROM U.S.P.L. URSULINES AVE. ****/ | 2018-12-06 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH OUTLET SERVICE IN SIDEWALK BACKFILLED JOB WITH RIVERSAND COLDMILL
201802035601 | 2018-11-26 | LEAD | 2513 | EADS | LAW | WMTLK | MI LEAK IN THE STREET EXAMINE INLET/OUTLET SERVICE FOR LEAK NO LEAK IN STREET WATER RUNNING INTO STREET FROM METER /** 1) MN: 000000 SN: 0076559, *TAP: SIZE: A LOC: 147 FEET FROM P LINE AT DORGENOIS S, *MB: CODE: CDLN LOC: ON EADS, 146.6' FROM L.S.P.L. SO. DORGENOIS ****/ | 2018-12-13 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH HANDWHELL BACKFILLED + DRESSED UP AREA
201802036501 | 2018-11-26 | LEAD/PLASTIC | 1520 | SUMNER | LAWRENCE ST | WILK | ML- METER LEAK MTR# A246003 ACCT # 235650-404462 INLET SERVICE LEAK IN MUDPPLOT /** 1) MN: A312871 SN: 0160866, *TAP: SIZE: B LOC: 121 FEET FROM P LINE AT LAWRENCE, *MB: CODE: OOO LOC: ON SUMNER 121FT FROM PL LAWRENCE 9FT OUTSD PL ****/ | 2019-01-07 | EXAMINED AREA CLEANED OUT METER BOX EXCAVATED ON INLET AND OUTLET SERVICE ONSERVED LEAK ON INLET SERVICE REPAIRS LEAK BACKFILLED AND CLEANED AREA
201802038301 | 2018-11-27 | LEAD |  | JOURDAN AV | N ROBERTSON | WMLK |  | 2018-11-26 | EXCAVATED IN MUD PLOT + STOPPED LEAK ON 12 X 20 FULL CIRCLE REPAIR CLANP BACKFILLED + DRESSED UP AREA
201802039701 | 2018-11-27 | LEAD | 1417-19 | CONGRESS |  | WILK | CUSTOMER HAS NO WATER. INSP D JOHNSON HAD SERVICE ORDER TO CHANGE METER. WHEN HE REMOVED OLD METER, WATER STARTED POURING OUT (CURB COCK BLOWN) AND HE CANNOT GET THE NEW METER IN. BOX OVERFLOWING AND NEEDS TO BE FIXED AS SOON AS POSSIBLE AND 1" METER SET. LOC 158171 ******************J.GILLIAM @11:39AM******************* INLET SERVICE LEAK ALSO SET 1" METER CUSTOMER OUT OF WATER /** 1) MN: C024864 SN: 0095615, *TAP: SIZE: C LOC: 172 FEET FROM P LINE AT VILLERE N, *MB: CODE: BDM5 LOC: ON CONGRESS 172' FROM N VILLERE 7' OUTSIDE 2' INSI ****/ | 2018-11-27 | EXCAVATED 3 X 2 MUD PLOT REPLACED 1 INCH METER COCK AND SET 1 INCH METER TO GIVE CUSTOMER WATER BACKFILLED AND CLEANED THE AREA
201802040601 | 2018-11-27 | LEAD | 425 | N CLAIBORNE AV | ST LOUIS | WMLK | WM- LEAK IN THE STREET LEAK ON THE MAIN IN MUDPLOT ACROSS FROM ABOVE ADDRESS /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-10 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 INCHJ INLET SERVICE BACKFILLED AREA
201802041101 | 2018-11-27 | LEAD | 3321 | TULANE AV |  | WILK | WM--- LEAK IN BETWEEN THE SIDEWALK AND STREET(ON THE BACKSIDE OFF THE BUILDING NEXT TO DRAIN) INLET SERVICE LEAK IN MUDPLOT BEHIND BUILDING FLODING CURB GETTING OFF IN DCB, LEFT 1 CONE /** 1) MN: A231318 SN: 0031864, *TAP: SIZE: B LOC: 140 FEET FROM P LINE AT JEFF DAVIS PKWY S, *MB: CODE: CEIM LOC: ON D HEMECOURT 140FT FROM JEFFERSON DAVIS ****/ | 2018-12-06 | EXCAVATED AND MADE REPAIRS ON ABANDON 1 INCH INLET SERVICE IN UD BACKFILLED JOB WITH RIVERSAND
201802043101 | 2018-11-27 | LEAD | 2427 | ST BERNARD AV |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 119167-701113 METER NUMBER - A408526 INLET SERVICE LEAK INSIDE METER BOX FROM BAD CURBCOCK /** 1) MN: A310741 SN: 0083541, *TAP: SIZE: A LOC: 205 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BF LOC: ON ST. BERNARD AVE., 206.5' FROM P.L. N.ROCHEBLAVE ****/ | 2018-12-12 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE IN MUD PLOT BACKFILLED JOB WITH RIVERSAND RAISED METER BOX UP TO GRADE
201802043301 | 2018-11-27 | LEAD | 2260 | N DERBIGNY | MARIGNY | WMTLK | ML-METER LEAK ACCT# 125738-422669 METER# C035191 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: SN: 0057795, *TAP: SIZE: C LOC: 172 FEET FROM P LINE AT MARIGNY, *MB: CODE: OOO LOC: ON N DERBIGNY 138' FROM MARIGNY ****/ | 2018-12-07 | REPLACED BOTH INLET NAD OUTLET WASHERS AT ABOVE LOCATION
201802045501 | 2018-11-28 | LEAD | 1224 | BARRACKS | TREME | WILK | ML- METER LEAK METER#B034529 ACCT#105337-526052 INLET SERVICE LEAK IN BOX /** 1) MN: B025919 SN: 0013245, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT TREME, *MB: CODE: BEM LOC: ****/ | 2018-12-13 | EXCAVATED 4 X 2 SIDEWALK CUT REPLACED 3/4 INCH METER COCK TO STOP LEAK ALSO MADE REPAIR ON OUTLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201802046101 | 2018-11-28 | LEAD | 2027 | ALLEN | N GALVEZ | WILK | WM- LEAK ON THE STREET AND SIDEWALK CHANGE FROM 2031 ALLEN INLET @ THE MAIN IN STREET /** 1) MN: 000000 SN: 0047360, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT GALVEZ N, *MB: CODE: CDF LOC: ON ALLEN 110FT FROM GALVEZ N ****/ | 2018-12-11 | MADE A 12 X 8 CUT IN ASPHALT STREET IN SEARCH OF WATER LEAK FOUND LEAK + REPOACED 3/4 INCH CORPORATION COCK ON 6 INCH WATER MAIN COMPACTED BACKFILLED + DRESSED UP AREA
201802046201 | 2018-11-28 | LEAD | 2232 | PAULINE | N MIRO | WILK | ********************PICKUP******************** EXAMINE INLET SERVICE FOR LEAK TRAILER OVER METER ACC#155052-432586 MN#A254720 /** 1) MN: A309833 SN: 0091716, *TAP: SIZE: A LOC: 248 FEET FROM P LINE AT MIRO N, *MB: CODE: CDLM LOC: ON PAULINE,250.5' FROM P.L. NO. MIRO,6' OUTSIDE ****/ | 2018-12-12 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND
201802046301 | 2018-11-28 | LEAD | 1843 | ALABO | N PRIEUR | WILK | MI- LEAK ON THE SIDEWALK INLET ON ABANDON SERVICE INFRONT VACANT LOT GETTING OFF IN DCB /** 1) MN: A318541 SN: 0139796, *TAP: SIZE: A LOC: 412 FEET FROM P LINE AT NO. ROMAN, *MB: CODE: __ LOC: ON ALABO, 412' FROM P.L. NO. ROMAN, 7' OUTSIDE ****/ | 2018-12-19 | MADE 6 X 6 IN BLACK TOP STREET AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201802047601 | 2018-11-28 | LEAD | 1324 | MOSS | GRAND RTE ST JOHN | WILK | ML- METER LEAK ACCT # 109512-521972 MTR # A304519 INLET SERVICE LEAK /** 1) MN: A304519 SN: 0021523, *TAP: SIZE: B LOC: 195 FEET FROM P LINE AT GRAND RTE ST JOHN, *MB: CODE: BFN1 LOC: ON MOSS 195FT FROM GRAND RTE ST JOHN ****/ | 2018-12-13 | REPLACED 5/8 INCH WASHERS TO STOP LEAK
201802048101 | 2018-11-28 | LEAD | 1700-04 | ST ROCH AV | N DERBIGNY | WILK | ML: METER LEAK ACCT#109685-725391 METER# A417130 INLET SERVICE LEAK IN BOX /** AT 1700: 1) MN: A300329 SN: 0032174, *TAP: SIZE: A LOC: 38 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: CEN LOC: FRONT 04 38' P.L. N DERBIGNY ****/ | 2018-12-07 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH OUTLET SERVICE BACKFILLED JOB WITH RIVERSAND
201802049601 | 2018-11-28 | LEAD | 1228 | MUSIC |  | WILK | WM - LEAK IN THE STREET INLET SERVICE LEAK IN STREET CAUSING CAVE /** 1) MN: A215078 SN: 0004030, *TAP: SIZE: B LOC: 94 FEET FROM P LINE AT URQUHART, *MB: CODE: BE LOC: ON MUSIC,94' FROM R.P.L. URQUHART ****/ | 2018-12-07 | EXCAVTED 5 X 4 GUTTER BOTTOM MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201802050301 | 2018-11-28 | LEAD | 4327 | N CLAIBORNE AV | POLAND AV | WILK | MI- LEAK IN THE STREET INLET SERVICE LEAK AT CURB FLOODING CURB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-12 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INELT SERVICE OUTLET SERVICE RAISE METER BOX UP TO GRADE AND REPLACE BROKEN 5/8 INCH METER BACKFILLD JOB WITH RIVERSAND
201802051101 | 2018-11-29 | LEAD | 462 | WALNUT |  | WILK | ML- METER LEAK ACCT# 129489-710030 MTR# C0189928 INLET SERVICE LEAK BAD BLEEDER VALVE, FOUND METER OFF LEFT METER OFF /** 1) MN: C018928 SN: 0058229, *TAP: SIZE: Y LOC: 69 FEET FROM P LINE AT WALNUT, *MB: CODE: CDHN LOC: ON HURST,70' FROM U. CURB OF WALNUT ****/ DOTTIE READY 12/13/18 EXP 01/02/19 | 2018-12-29 | EXCAVATED AND REPAIRED INLET SERVICE LEAK TREE ROOTS SLOWED PROGRESS 3' X 3' MUD CUT - BACKFILLED - NO DRESS-UP NEEDED
201802051201 | 2018-11-29 | LEAD | 4508 | ST CLAUDE AV |  | WOLK | MI LEAK ON SIDEWALK OUTLET SERVICE LEAK IN MUDPLOT @ ENTRANCE OF DRIVEWAY /** 1) MN: SN: 0060115, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT KENTUCKY, *MB: CODE: AFL LOC: ON ST. CLAUDE AVE.,71.4' FROM L.R.P.L. KENTUCKY ****/ | 2018-12-17 | EXCAVATED IN CONCRETE SIDEWALK + MADE REPAIR ON 3/4 INCH OUTLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201802052301 | 2018-11-29 | LEAD | 1232 | LESSEPS | MARAIS | WOLK | MI- CONS ON METER PER INSPECTOR METER # A-427307 ACCT # 140048-430792 /** 1) MN: A319554 SN: 0070840, *TAP: SIZE: A LOC: 265 FEET FROM P LINE AT MARAIS, *MB: CODE: CEL1 LOC: ON LESSEPS 260' FROM PL MARAIS ****/ | 2018-12-17 | PERFORMED STOP + WASTE TEST + FOUND LEAK ON PROPERTY REFER BACK TO PROPERTY OWNER FOR REPAIRS
201802052401 | 2018-11-29 | LEAD | 2417 | ST ROCH AV | N DORGENOIS | WOLK | MI- CON ON METER PER INSPECTOR METER # A-264199 ACCT # 130968-484875 /** 1) MN: A264199 SN: 0105824, *TAP: SIZE: C LOC: 143 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CDN1 LOC: 159' P.L. N DORGENOIS ****/ | 2018-12-17 | EXAMINE JOB + FOUND NO LEAK THERE IS NO CONSTANT REGISTRATION ON THE METER
201802052601 | 2018-11-29 | LEAD | 4525 | N GALVEZ |  | WMTLK | LOCATIONID#146257-601959 METER#A421699 LEAK INSIDE METERBOX /** 1) MN: A190062 SN: 0078240, *TAP: SIZE: C LOC: 261 FEET FROM P LINE AT KENTUCKY, *MB: CODE: BDL4 LOC: ON NO. GALVEZ, 256' FROM P.L. KENTUCKY, 7' OUTSIDE ****/ | 2018-12-24 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER COCK TO STOP LEAK BACKFILLEDAND CLEANED THE AREA
201802053201 | 2018-11-29 | LEAD | 628 | ELYSIAN FIELDS AV | CHARTRES | WILK | WM - LEAK BETWEEN THE SIDEWALK AND THE STREET INLET SERVICE LEAK ON LARGE METER INSIDE MANHOLE /** 1) MN: D005377 SN: 0121466, *TAP: SIZE: C LOC: 219 FEET FROM P LINE AT CHARTRES, *MB: CODE: AEMD LOC: ON ELYSIAN FIELDS AVE., 218' FROM P.L. CHARTRES, ****/ | 2019-01-16 | EXCAVATED 4 X 2 DRIVEWAY CUT REPAIRS 2 INCH INLET SERVICE BACKFILLED AND CLEANED THE AREA
201802054501 | 2018-11-29 | LEAD | 7620-22 | W LAVERNE | CURRAN BL | WILK | MI- LEAK BETWEEN SIDEWALK AND CURB INLET SERVICE LEAK ON ABANDON SERVICE IN FRONT VACANT HOUSE /** AT 7620: 1) MN: A340916 SN: 0146501, *TAP: SIZE: A LOC: 103 FEET FROM P LINE AT CURRAN BLVD, *MB: CODE: CDM1 LOC: ON W. LAVERNE 103FT FROM PL CURRAN BLVD 8FT OUT- ** AT 7622: 2) MN: A264952 SN: 0146501, *TAP: SIZE: A LOC: 105 FEET FROM P LINE AT CURRAN BLVD, *MB: CODE: OOOO LOC: ON W LAVERNE 104FT PL CURRAN BL 9' OUTSIDE 3' IN- ****/ | 2019-02-02 | ARRIVED ON JOB SITE EXAMINED LEAK IN UD PLOT EXCAVATED IN MUD PLOT BY HAND MADE REPAIRS ON SERVICE BACKFILED DRESS UP WORK SITE NO METER
201802054901 | 2018-11-29 | LEAD | 2533 | COLUMBUS | N BROAD | WOLK | ML- METER LEAK METER# C036302 ACCT# 304353-718515 OUTLET SERVICE LEAK WITH CONSTANT REGISTRATION ON THE METER /** 1) MN: C018004 SN: 0044035, *TAP: SIZE: C LOC: 138 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CDM LOC: ON COLUMBUS,138' FROM P.L. NO. DORGEOIS,8' OUTSIDE ****/ | 2018-12-07 | EXAMINED JOB AT ABOVE ;OCATION FOUND NO CONSTANT REGISTRATION ON METER
201802055001 | 2018-11-29 | LEAD | 2233 | DAUPHINE | ELYSIAN FIELDS AV | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: B028331 SN: 0105638, *TAP: SIZE: B LOC: 248 FEET FROM P LINE AT ELYSIAN FIELDS AVE, *MB: CODE: ADMN LOC: 251FT FROM PL ELYSIAN FIELDS AVE 8' OUTSIDE PL 3' ****/ | 2018-12-07 | EXCAVATED AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND COLDMILL
201802057202 | 2018-12-19 | LEAD | 1379 | ST ANTHONY |  | WMRE | EXCAVATED 2 X 14 MUD PLOT TRENCH BY HAND UNABLE TO LOCATE METER BOX BACKFILLED AND CLEANED THE AREA /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-25 | EXCAVATED IN PREVIOUS CUT + LOCATED 5/8INCH METER BOX REPLACED 5/8 INCH METER BOX COMPLETE SET 5/8 INCH METER + MARKED WITH BLUE PAINT BACKFILLED + DRESSED UP AREA
201802058401 | 2018-11-30 | LEAD | 1701 | DESIRE |  | WOLK | ML METERLEAK MTR#A354745 LOC/CUST#148075-432034 CONS REG ON METER. /** 1) MN: A318188 SN: 0084930, *TAP: SIZE: B LOC: 14 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BD LOC: 12' P.L. N DERBIGNY ****/ | 2018-12-17 | REPLACED 5/8 INCH WASHERS IN METER BOX AFTER REPAIR METER STILL HAD CONSTANT REGISTRATION PERFORMED STOP + WASTE TEST FOUND LEAK ON PROPERTY REFER BACK TO PROPERTY OWNER FOR REPAIRS
201802060301 | 2018-11-30 | LEAD | 1727 | ALVAR | N DERBIGNY | WOLK | ACCT#144439-432400. METER#A346027. METER HAS A STOP AND GO CON REG. NO S&W VALVE TO PERFORM TEST. /** 1) MN: A238559 SN: 0089067, *TAP: SIZE: C LOC: 173 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BM2 LOC: ON ALVAR, 179.5' FROM P.L. NO. DERBIGNY,9' OUTSIDE ****/ | 2018-12-17 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX ALSO REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201802061101 | 2018-11-30 | LEAD | 2019 | TOURO |  | WILK | LOCATION ID-124713 MTR-A417880 METER LEAK INLET SERVICE LEAK CONTRACTORS ROLLING OVER METER, HOUSE UNDER RENOVATION /** 1) MN: A183414 SN: 0045624, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CD LOC: ON TOURO 147.5' FROM LSPL N JOHNSON ****/ | 2018-12-17 | EXCAVATED 8 X 5 MUD PLOT THROUGH ROOT AND BRICK RELOCATED METER BOX TO THE OTHER SIDE OF SIDEWALK TO PREVENT CONTRACTOR ROLLING OVER METER BOX BACKFILLED AND CLEANED THE AREA (SECOND METER BOX HAD NO METER INSIDE)
201802061401 | 2018-11-30 | LEAD | 1326 | ST ROCH AV | N VILLERE | WILK | ML-METER LEAK ACCT#113776-716410 MTR# A155178 EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A155178 SN: 0067813, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT VILLERE N, *MB: CODE: BFK LOC: ON ST ROCH 112FT FROM VILLERE N ****/ | 2018-12-18 | EXCAVATED 3 X 2 MUD PLOT THROUGH ROCK AND BRICK REPLACED5/8 INCH METER BOX COCK BACKFILLED AND CLEAN ED THE AREA
201802062201 | 2018-11-30 | LEAD | 405 | HOMER | NUNEZ | WILK | ML- METER LEAK METER# A364719 ACCT# 236088-401323 INLET SERVICE LEAK IN MUPLOT NEAR SIDEWALK, FLOODING AREA /** 1) MN: SN: 0165162, *TAP: SIZE: A LOC: 14 FEET FROM P LINE AT TECHE, *MB: CODE: OOOO LOC: ON HOMER, 13' FROM D.P.L. TECHE, 8' OUTSIDE, 4' ****/ | 2019-02-02 | EXAMINED AREA PUMP DOWN WATER LOCATED METER EXCAVATED ON INLET SERVICE OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK BACKFILLED CLEANED AREA
201802063201 | 2018-11-30 | LEAD/PLASTIC | 735 | CRYSTAL | SARDONYX | WDSM | DECREASE EXISTING SERVICE AND METER FROM 1 INCH TO 5/8 INCH SERVICE AND METER AT 735 CRYSTAL STREET, INC SAME LOCATION FOR THE FLAT SUM OF $100.00. WFA APP.: 123445 S & W B JOB #2732 /** 1) MN: C027729 SN: 0124102, *TAP: SIZE: C LOC: 282 FEET FROM P LINE AT SARDONYX, *MB: CODE: BGL1 LOC: 285FT PL SARDONYX 2FT OUTSD PL 10FT INSD ****/ | 2019-01-04 | EXCAVATED A 3 X 6 CUT AND DECREASE A 1" SERVICE AND METER TO 5/8" RAISE THE METER TO GRADE AND RENEW THE OUTLET SERVICE FROM METER TO PROPERTY BACKFILL CLEAN UP OLD METER INFO: SENSUS# C027729 FACT#59814320 RD:10220
201802063801 | 2018-11-30 | LEAD | 1936 | N TONTI |  | WILK | ML-- METER LEAK METER# A403241 ACCT # 155880-494215 ***REPAIRED ONCE LEAKING AGAIN*** INLET SERVICE LEAK BEHIND METER BOX /** 1) MN: A311753 SN: 0087267, *TAP: SIZE: A LOC: 36 FEET FROM P LINE AT ALLEN, *MB: CODE: CDK LOC: ON NO. TONTI, 35.5' FROM P.L. ALLEN,8.5' OUTSIDE ****/ | 2018-12-11 | EXCAVATED IN PREVIOUS CUT + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201802064101 | 2018-11-30 | LEAD | 1839 | LAPEYROUSE | N PRIEUR | WILK | MI-LEAK AT SIDEWALK INLET SERVICELEAK IN MUDPLOT /** 1) MN: A141003 SN: 0079323, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: ADH LOC: 48FT FROM LRPL LAPEYROUSE ON PRIEUR ****/ | 2018-12-12 | EXCAVATED AND MADE REPAIR ON 5/8 INCH INLET SERVICE IN MUD PLOT BACKFILLED JOB WITH RIVERSAND
201802067001 | 2018-12-01 | LEAD/PLASTIC | 3501 | LANG | BERKLEY DR | WILK | MI- LEAK IN SIDEWALK FLOODING AREA INLET SERVICE LAK IN SIDEWALK /** 1) MN: A137059 SN: 0135542, *TAP: SIZE: B LOC: 62 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: ADKM LOC: ON LANG, 60' FROM P.L. BERKLEY DR., 8' OUTSIDE, 3' ****/ | 2019-01-04 | ARRIVED ON JOB SITE EXAMINED LEAK IN MUD PLOT EXCAVATED IN MUD PLOT COMPLETE RENEWED OUTLET AND SET UP WORK NEW METER BOX COMPLETE BACKFILLED DRESS UP WORK SITE 0700AM 1000AM CREW TRUCK 567 HAD TO GER PM DINE
201802069701 | 2018-12-02 | LEAD | 1036 | ESPLANADE AV | N RAMPART | WMLK | MI- LEAK IN THE STREET LEAK ON WATER MAIN IN STREET @ CURB GETTING OFF IN DCB /** 1) MN: A269700 SN: 0062068, *TAP: SIZE: A LOC: 42 FEET FROM P LINE AT RAMPART N, *MB: CODE: BD LOC: ON ESPLANADE AVE.,41' FROM U.R.P.L. NO. RAMPART ** 2) MN: SN: 0000000, *TAP: SIZE: __ LOC: 0 FEET FROM P LINE AT , *MB: CODE: __ LOC: N RAMPART THERE ARE 2 MORE NOT LISTED. ****/ | 2018-12-11 | MADE 6 X 6 CUT IN CONCRETE BASE STREET AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILLED AREA
201802070601 | 2018-12-03 | LEAD | 919 | ORLEANS AV | DAUPHINE | WILK | MI- LEAK IN SIDEWALK CHANGED FROM 923 ORLEANS AV INLET SERVICE LEAK INSIDE METER BOX ON SIDEWALK /** 1) MN: A303609 SN: 0023954, *TAP: SIZE: A LOC: 168 FEET FROM P LINE AT DAUPHINE, *MB: CODE: AELK LOC: 162' P.L. DAUPHINE ****/ | 2018-12-17 | EXCAVATED 3 X 2 SIDEWALK REPLACED 5/8 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802071501 | 2018-12-03 | LEAD | 2408 | ANNETTE | N ROCHEBLAVE | WMTLK | ML MTR#4153685 LOC & CUST# 142967-495975 SERVICE ADDRESS: 2408 ANNETTE ST INSP COMM: F/ON HAVE CONS, DID TEST AND CONS STOP. NO LKS IN MTR BOX ...... MTR RD. 0514 /** 1) MN: A153685 SN: 0074281, *TAP: SIZE: A LOC: 80 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: CD LOC: ON ANNETTE ST 80' FROM PL N ROCHEBLAVE ST 2' INSI ****/ | 2018-12-17 | EXAMINED JOB + FOUND NO LEAK ALSO THERE IS NO CONSTANT REGISTRATION
201802072301 | 2018-12-03 | LEAD/PLASTIC | 1417 | CONSTANCE | EUTERPE | WILK | ML- METER LEAK ACCT# 104489-536897 MTR# A408119 INLET SERVICE LEAK BAD BLEEDER VALVE /** 1) MN: A292465 SN: 0001326, *TAP: SIZE: A LOC: 140 FEET FROM P LINE AT TERPSICHORE, *MB: CODE: BFLM LOC: 140FT FROM USPL TERPSICHORE ****/ | 2019-01-08 | WE EXCAVATED BY HAND TO MKAE REPAIR TO A 3/4 INLET LEAK ALSO REPLACE A 3/4 METER BOX COMPLETE WE BACKFILL PLUS CLEAN UP
201802072801 | 2018-12-03 | LEAD | 87 | CYPRESS GROVE CT | TULLIS DR | WILK | ML- METER LEAK METER# A 241529 ACCT# 235948 - 414097 INLET SERVICE LEAK IN THE DRIVEWAY FLOODING AREA /** 1) MN: A242015 SN: 0166217, *TAP: SIZE: B LOC: 35 FEET FROM P LINE AT TULLIS DR, *MB: CODE: OOOO LOC: ON CYPRESS GROVE CT 32FT FROM PL TULLIS 9FT OUT ** 2) MN: A241529 SN: 0168374, *TAP: SIZE: B LOC: 35 FEET FROM P LINE AT TULLIS DR, *MB: CODE: __ LOC: ON CYPRESS GROVE CT 32FT FROM PL TULLIS 9FT OUT ****/ | 2019-01-05 | MADE 2 X 4 CUT IN DRIVEWAY AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201802073301 | 2018-12-03 | LEAD | 2214 | LIZARDI | N TONTI | WILK | ML- METER LEAK METER# A223721 ACCT# 173817-424251 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A223721 SN: 0128571, *TAP: SIZE: B LOC: 120 FEET FROM P LINE AT MIRO N, *MB: CODE: CEL1 LOC: MTR ON LIZARDI 120FT FROM PL MIRO 6FT OUTSIDE PL ****/ | 2018-12-11 | EXAMINED AND PUMPED METER BOX DOWN AND REPLACED 5/8 INCH WASHERS ON INLET AND OUTLET
201802074701 | 2018-12-03 | LEAD | 2922 | PAUGER |  | WILK | WM-LEAK IN SIDEWALK EXAMINE INLET SERVICE LEAK INSIDE METER BOX LOCATED IN THE MUD PLOT /** 1) MN: A214304 SN: 0060555, *TAP: SIZE: A LOC: 127 FEET FROM P LINE AT TONTI N, *MB: CODE: OOO LOC: ON PAUGER,127' FROM U.R.PP.L. NO. TONTI ****/ | 2018-12-18 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH HANDWHEEL TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802075001 | 2018-12-03 | LEAD | 5401 | N CLAIBORNE AV | ANDRY | WILK | MI- LEAK IN STREET ***AT INTERSECTION*** CHANGED FROM 1600BLK ANDRY INLET SERVICE LEAK IN THE STREET, METER SITS ON ANDRY. GETTING OFF IN THE DCB /** 1) MN: A328750 SN: 0123920, *TAP: SIZE: A LOC: 67 FEET FROM P LINE AT NO. CLAIBORNE AVE., *MB: CODE: ADHL LOC: ON ANDRY, 67' FROM P.L. NO. CLAIBORNE AVE., 6.5' ****/ | 2018-12-18 | MADE 6 X 6 CUT IN BLACK TOP STREET AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILED AREA
201802075801 | 2018-12-03 | LEAD | 908 | S TELEMACHUS |  | WILK | MI LEAK ON THE SIDEWALK INLET SERVICE LEAK BEHIND CURB COCK FLOODING GRASSY AREA /** 1) MN: A214902 SN: 0090251, *TAP: SIZE: A LOC: 71 FEET FROM P LINE AT HOWARD AVE, *MB: CODE: ADM2 LOC: ON SO. TELEMACHUS,71' FROM P.L. HOWARD AVE.,8'OUT- ****/ DOTTIE READY 01/10/19 EXP 01/30/19 | 2019-01-16 | ARRIVED AT ABOVE LOCATION ,EXAMINED ,EXCAVTED BY HAND AND MADE REPAIR TO STOP LEAK ON 3/4 INLET SERVICE LINE .BACKFILLED CLEANED UP AND WASHED DOWN WORK AREA TO COMPLETE JOB.(LEADD INLET)
201802076901 | 2018-12-03 | LEAD | 1810 | TERPSICHORE |  | WILK | WM-LEAK ON THE SIDEWALK CHANGED FROM 1812 TERPSICHORE INLET SERVICE LEAK IN THE DRIVEWAY. ***HOUSE VACANT*** /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ DOTTIE READY 01/10/19 EXP 01/30/19 | 2019-01-16 | ARRIVED DAT ABOVE LOCATION ,EXAMINED EXCAVTED AND MADE REPAIR TO STOP LEAK ON 3/4 INLET SERVIC-ED LINE.BACKFILLED CLEANED UP AND WASHED DOWN AREA TO COMPLETE JOB.(LEAD INLET)(SOC 2FT. X 2 FT. CONCRETE) (JOB COMPLETE)
201802077601 | 2018-12-03 | LEAD | 3137 | N MIRO | CLOUET | WILK | ML-METER LEAK ACCT#163263-703480 METER#A406417 INLET SERVICE LEAK /** 1) MN: A296441 SN: 0102657, *TAP: SIZE: A LOC: 294 FEET FROM P LINE AT CLOUET, *MB: CODE: ADK2 LOC: ON N MIRO 294' FROM PL CLOUET 8' OUTSIDE PL ****/ | 2018-12-13 | STOPPED LEAK ON 5/8 INCH CURB IN METER BOX NO METER
201802078601 | 2018-12-04 | LEAD | 1424 | N CLAIBORNE AV | KERLEREC | WMTLK | ACCOUNT# 106940-486208 METER# A322578 FOUND LEAK INSIDE MTR BOX AROUND CURB COCK /** 1) MN: A322578 SN: 0035330, *TAP: SIZE: B LOC: 98 FEET FROM P LINE AT KERLEREC, *MB: CODE: AEMO LOC: ON N CLAIBORNE AVE 98' FROM URPK KERLEREC ****/ | 2018-12-19 | EXCAVATED 3 X 3 SIDEWALK IN RAIN REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802079601 | 2018-12-04 | LEAD | 2130 | CONGRESS |  | WILK | ML METER LEAK ACCOUNT #304223-432687 EXAMINE INLET SERVICE METER BURIED CONTRACTORS WORKING ON THE HOUSE /** 1) MN: A215235 SN: 0084861, *TAP: SIZE: B LOC: 247 FEET FROM P LINE AT GALVEZ N, *MB: CODE: CD LOC: 247' P.L. N GALVEZ ****/ | 2018-12-24 | EXCAVATD 3 X 3 GUTTER BOTTOM ALSO 4 X 2 MUD PLOT RELOCATED METER BOX TO MUD PLOT TO PREVENT FUTURE ROLL OVER BAQCKFILLED AND CLEANED THE AREA
201802079701 | 2018-12-04 | LEAD | 446 | THAYER | ELIZA | WILK | ML-METER LEAK ACCT#228416-403350 METER#C031514 INLET SERVICE LEAK IN THE MUD PLOT FLOODING SIDEWALK /** 1) MN: C019605 SN: 0120758, *TAP: SIZE: C LOC: 3 FEET FROM P LINE AT THAYER, *MB: CODE: AD LOC: ON ELIZA, 3' FROM P.L. THAYER, 7' OUTSIDE ****/ | 2019-02-02 | EXAMINED AREA BROKE OUT CONCRETE EXPOSED LEAK ON OUTLET SERVICE REPAIRED LEAK RAISED METER TO GRADE BACKFILLED CLEANED AREA
201802079901 | 2018-12-04 | LEAD | 819 | N DUPRE |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 128674-521083 METER NUMBER - A406099 EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A220794 SN: 0056146, *TAP: SIZE: B LOC: 182 FEET FROM P LINE AT DUMAINE, *MB: CODE: CD LOC: 181' P.L. DUMAINE ****/ | 2018-12-19 | REPLACED 5/8 INCH WASHERS AND HANDWHEEL INSIDE METER BOX TO STOP LEAK
201802082001 | 2018-12-04 | LEAD | 2441 | FORSTALL | N DORGENOIS | WMLK | WATER MAIN LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-21 | MADE 4 X 4 CUT IN CONCRETE BASE STREET AND MADE REPAIR ON 3/4 INCH INLET SERVICE FOR ABANDON LOT BACKFILLED AREA. JOB COMPLETE
201802082201 | 2018-12-04 | LEAD | 2138 | REYNES | N MIRO | WMLK | WATER MAIN LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-21 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 INCH TAILPIECE FOR ABANDON LOT BCKFILLED AREA. JOB COMPLETE
201802082501 | 2018-12-04 | LEAD | 1905 | LIZARDI | N PRIEUR | WMLK | WATER MAIN LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-21 | ARRIVED AT ABOVE LOCATION + FOUND AREA FLOODED FOUND LEAK IN MUD PLOT FLOODING CURB EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH ABANDONED INLET SERVICE IN HIGH GRASS IN FRONT OF ABANDONED LOT BACKFILLED + DRESSED UP AREA
201802082801 | 2018-12-04 | LEAD | 1937 | BENTON | N JOHNSON | WMLK | WATER MAIN LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-21 | EXCAVATED IN ASPHALT STREET + MADE REPAIRS ON3/4 INCH ABANDONED SERVICE LINE COMPACTED BACKFILLED + DRESSED THE AREA
201802083001 | 2018-12-04 | LEAD | 1941 | HOPE | A P TUREAUD AV | WOLK | ML- METER LEAK MTR#A406069 ACCT#303887-719934 OUTLET SERVICE LEAK INSIDE METER BOX, WITH CONSTANT REGISTRATION ON THE METER /** 1) MN: A319349 SN: 0078025, *TAP: SIZE: A LOC: 79 FEET FROM P LINE AT LONDON AVE, *MB: CODE: CDN1 LOC: ON HOPE, 79' FROM P.L. LONDON AVE. ****/ | 2018-12-20 | EXCAVATED 3 X 2 DRIVEWAY CUT MADE REPAIR OUTLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201802083201 | 2018-12-04 | LEAD/PLASTIC | 1124 | KABEL DR | GEN MEYER AV | WMTLK | ML-METER LEAK ACCT#227370-728125 METER#A405661 ***CUSTOMER STATES WATER IS SHOOTING INTO AIR**** EXAMINE INLET & OUTLET SERVICE FOR A LEAK INSIDE METER BOX ***SPOKE WITH CUSTOMER*** /** 1) MN: A309194 SN: 0126015, *TAP: SIZE: B LOC: 429 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: BDK LOC: ON KABEL DR., 429' FROM P.L. GEN. MEYER AVE., 9' ****/ | 2018-12-17 | EXAMINED AREA EXCAVATED ON INLET AND OUTLET SERVICE OBSERVED LEAK ON INLET SERVICE REMOVED LEAD ON OUTLET RAISED METER TO GRADE BACKFILLED CLEANED AREA
201802084801 | 2018-12-04 | LEAD | 1900 | GORDON | N PRIEUR | WMLK | WATER MAIN LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-24 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH ABANDONED INLET SERVICE LINE THAT WAS FLOODING AREA (NO METER) JOB COMPLETE
201802084903 | 2019-01-12 | LEAD | 1800 | GORDON | N PRIEUR | WMLK | WATER LEAK CONTINUES AFTER PREVIOUS REPAIR. /** 1) MN: A152010 SN: 0145118, *TAP: SIZE: A LOC: 1 FEET FROM P LINE AT ROMAN N, *MB: CODE: ADKL LOC: RES ON GORDON 4' P/L N ROMAN 7' OUTSIDE ****/ | 2019-02-07 | EXAMINE JOB FIND NO LEAK JOB COMPLETE
201802085001 | 2018-12-04 | LEAD | 1301 | FRANKLIN AV | ALMONASTER AV | WMTLK | ML-METER LEAK ACCT#124357-479766 METER#A360805 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK /** 1) MN: A331469 SN: 0045137, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT ALMONASTER AVE, *MB: CODE: BDH1 LOC: SIDE ST ON URQUHART 49' P.L. ALMONASTER AVE ****/ | 2018-12-18 | MADE 2 X 2 SIDEWALK CUT AND MADE REPAIRS ON COPPER 3/4 INCH LINE BEHIND METER BOX ALSO REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201802086201 | 2018-12-04 | LEAD | 221 | N JOHNSON | IBERVILLE | WMBK | MI- SET 5/8 METER ****PER SUPERVISOR JUNE LARCHE*** *************1ST AM************ BROKEN METER BOX UNABLE TO SET 5/8 METER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-03 | EXCAVATED 4 X 4 MUD PLOT AND REPLACE 5/8 INCH METER BOX BOTTOM ALSO SET A 5/8 INCH WATER MEER AT ABOVE LOCATION BACKFILLED JOB WITH RIVERSAND. THE METER WAS REQUESTED & .RESET ON 12/5/18. PER SERVICE REQUEST #12859674
201802086301 | 2018-12-04 | LEAD | 5446-48 | DAUPHINE | ANDRY | WMTLK | WM- LEAK ON SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR A LEAK FLOODING AREA /** AT 5446: 1) MN: A302865 SN: 0041517, *TAP: SIZE: A LOC: 175 FEET FROM P LINE AT FLOOD, *MB: CODE: CDL LOC: ON DAUPHINE 177FT FROM URPL FLOOD ** AT 5448: 2) MN: SN: 0041516, *TAP: SIZE: A LOC: 147 FEET FROM P LINE AT FLOOD, *MB: CODE: CD LOC: ON DAUPHINE 147FT FROM URPL FLOOD ****/ | 2018-12-19 | EXAMINED AND PUMPED AREA DOWN AND FOUND NO LEAK
201802087201 | 2018-12-04 | LEAD | 2128 | DESIRE | N GALVEZ | WMTLK | ML-METER LEAK METER#A258264 ACCT#171040-434216 EXAMINE INLET AND OUTLET SERVICE INSIDE METER BOX FOR LEAK /** 1) MN: A298392 SN: 0113720, *TAP: SIZE: A LOC: 244 FEET FROM P LINE AT NO. GALVEZ, *MB: CODE: CD LOC: ON DESIRE, 229' FROM P.L. NO. GALVEZ, 8' OUTSIDE ****/ | 2018-12-17 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201802088101 | 2018-12-05 | LEAD | 3534 | GENTILLY BL | IRIS | WOLK | ACCOUNT # 156125-478142 METER # B026100 FOUND LK AT CURB COCK SIDE OF METER /** 1) MN: B026100 SN: 0093157, *TAP: SIZE: B LOC: 285 FEET FROM P LINE AT IRIS, *MB: CODE: OOO LOC: ON GENTILLY AVE 285' FROM PL IRIS 14.5' OUTSIDE PL ****/ | 2018-12-05 | EXCAVATED IN MUDPLOT REPAIR 3/4 STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND JOB COMPLETE
201802090001 | 2018-12-05 | LEAD/PLASTIC | 826 | BELLEVILLE | SLIDELL | WILK | MI- MISSING METER COVER ACCT# 227996-709707 METER# A421394 INLET SERVICE LEAK IN THE MUD PLOT FLOODING THE AREA, ALSO REPLACE BROKEN METER BOX CASING. LEFT 1 CONE FOR SAFETY /** 1) MN: A328381 SN: 0118412, *TAP: SIZE: B LOC: 220 FEET FROM P LINE AT SLIDELL, *MB: CODE: BD LOC: ON BELLEVILLE 220FT FROM SLIDELL 8' OUTSIDE ****/ | 2019-01-22 | ARRIVED ON JOB SITE EXAMINED LEAK IN MUD PLOT EXCAVATED IN MUD PLOT BY HAND MADE REPAIRS ON SERVICE BACKFILLED DRES UP WORK SITE
201802091901 | 2018-12-05 | LEAD | 1529 | MAZANT |  | WILK | MI METER BOX LEAKING ACCOUNT #207616 METER #A353781 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A295446 SN: 0075952, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: OOO LOC: ON MAZANT 100FT FROM PL N CLAIBORNE AVE 8FT OUT- ****/ | 2018-12-17 | EXAMINED AND PUMPED METER DOWN AND REPLACED 5/8 INCH WASHERS ON INLET AND OUTLET
201802092101 | 2018-12-05 | LEAD | 2114 | ALLEN |  | WMRE | INSP L UDUEBOR STATES SERVICE IS BURIED UNDER ROCKS. PLEASE RAISE TO GRADE AND CHANGE METER C035598 LOC 190946 LOCATE, RAISE TO GRADE & CHANGE METER /** 1) MN: C012516 SN: 0149310, *TAP: SIZE: C LOC: 173 FEET FROM P LINE AT GALVEZ N, *MB: CODE: BDK LOC: 171FT PL N GALVEZ 7FT OUTSIDE P/L ****/ | 2018-12-20 | EXCAVATED 3 X 3 EXISTING SIDEWALK CUTREPLACED 1 INCH METER ADOPTER AND CASING BACKFILLED AND CLEANED THE AREA REPLACED 1' METER NOT REGISTERING OLD METER INFO: C035598 FACT: 15551184 MAKE: HERSEY READ: 0
201802092301 | 2018-12-05 | LEAD | 2954 | BLAIR | GEN MEYER AV | WILK | WM- LEAK ON THE SIDEWALK EXAMINE INLET SERVICE LEAK IN THE MUD PLOT FLOODING SIDEWALK LEAK ON GEN MEYER /** 1) MN: A238600 SN: 0132127, *TAP: SIZE: B LOC: 46 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: AD LOC: ON BLAIR 46' FROM PL GEN MEYER AVE 7' OUTSIDE PL 4 ****/ | 2019-01-06 | EXCAVATED IN MUD PLOT AND CORKED JOINT ON 12 INCH WATER MAIN BACKFILLED AREA. JOB COMPLETE
201802094101 | 2018-12-05 | LEAD | 2234 | SERE | MARIGNY | WILK | MI- LEAK IN THE SIDE WALK INLET SERVICE LEAK IN MUDPLOT FLOODING SIDEWALK 12/26/18 CUSTOMER STATES LEAK IS A HEALTH HAZARD (KSW) /** 1) MN: A212433 SN: 0099221, *TAP: SIZE: B LOC: 165 FEET FROM P LINE AT MARIGNY, *MB: CODE: CDLN LOC: FRONT - 165' P.L. MARIGNY ****/ | 2019-02-03 | ARRIVED ON JOB SITE EXAMINED LEAK IN MUD PLOT EXCAVATED IN MUD PLOT AND STREET MADE REPAIRS ON INLET SERVICE AND SET UP NEW METER BOX COMPLETE BACKFILED DRESS UP WORK SITE
201802094701 | 2018-12-05 | LEAD | 5009 | ROYAL | REYNES | WILK | ML- METER LEAK MN:A415455 ACCT#167545-424590 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A337611 SN: 0108880, *TAP: SIZE: A LOC: 138 FEET FROM P LINE AT REYNES, *MB: CODE: BDK7 LOC: ON ROYAL, 138' FROM P.L. REYNES, 8' OUTSIDE P.L. ****/ | 2018-12-19 | REPLACED 5/8 INCH HANDWHEEL +GUTS IN METER BOX + DAMAGED 5/8 INCH WATER METER **************OLD METER INFO**************** METER:A415455 FAC:15480901 HERSEY READ:200
201802094801 | 2018-12-05 | LEAD | 414 | N DUPRE | ST LOUIS | WOLK | MI- LEAK IN BETWEEN STREET AND SIDEWALK OUTLET SERVICE LEAK IN MUDPLOT CONSTANT REG LEFT ONE CONE FOR SAFETY /** 1) MN: A300011 SN: 0105720, *TAP: SIZE: A LOC: 86 FEET FROM P LINE AT CONTI, *MB: CODE: CDM2 LOC: ON NO. DUPRE, 88' FROM P.L. CONTI, 7' OUTSIDE P.L. ****/ | 2018-12-14 | EXAMINJED JOB AT ABOVE LOCATION AND FOUND LEAK COMING FROM FAUCET ON PROPERTY SIDE P.O.P
201802095001 | 2018-12-05 | LEAD | 1726 | TRICOU | N DERBIGNY | WILK | MI-LEAK IN THE STREET INLET SERVICE LEAK IN MUDPLOT FLOODING CURB /** 1) MN: A114173 SN: 0125579, *TAP: SIZE: A LOC: 198 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: DLM LOC: RES ON TRICOU 198FT FROM PL DERBIGNY 7' OUTSIDE PL ****/ | 2018-12-19 | EXCAVATED IN ASPHALT STREET + MUD PLOT + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201802095401 | 2018-12-05 | LEAD | 1746 | N ROMAN |  | WILK | ML-METER LEAK ACCT#123152-439830 MTR#A342272 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A342272 SN: 0048979, *TAP: SIZE: A LOC: 74 FEET FROM P LINE AT ALLEN, *MB: CODE: ADK LOC: ON N ROMAN 74.5' FROM LSPL ALLEN ****/ | 2018-12-19 | MADE 4 X 4 CUT IN SIDEWALK AND MADE REPAIRS ON 3/4 INCH OUTLET SERVICE INSIDE METER BOX BACKFILLED AREA
201802096401 | 2018-12-06 | LEAD | 3022 | ST PHILIP |  | WMTLK | ML- METER LEAK MTR# A-317714 ACCT # 134148-532599 /** 1) MN: A317714 SN: 0064956, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT SALCEDO NO., *MB: CODE: BD LOC: ON ST. PHILIP, 95' FROM U.R.P.L. NO. SALCEDO ****/ | 2018-12-14 | EXAMINED PUMPED METER BOX DOWN AND REPLACED 5/8 INCH WASHERS ON INLET AND OUTLET
201802097001 | 2018-12-06 | LEAD | 1812 | IBERVILLE |  | WMTLK | LOCATIONID#116457-522412 METER#A401760 METERBOX OVERFLOWING /** 1) MN: SN: 0045893, *TAP: SIZE: A LOC: 120 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: CFN6 LOC: METER ON IBERVILLE 120 FT FROM PL N DERBIGNY ****/ | 2018-12-14 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201802097201 | 2018-12-06 | LEAD | 3005 | ROBERT |  | WILK | LOCATIONID#162538-574412 METER#A418440 BLEEDER LEAK /** 1) MN: A254340 SN: 0017041, *TAP: SIZE: A LOC: 34 FEET FROM P LINE AT DERBIGNY S, *MB: CODE: BD1 LOC: 34FT FROM PL DERBIGNY ON ROBERT 8FT OUTSIDE PL ****/ DOTTIE READY 1-30-19 EXP 2-19-19 | 2019-02-03 | ARRIVED ON JOB SITE EXAMINED LEAK IN METER BOX EXCAVATED IN UD PLOT MADE REPAIRS ON SERVICE BACKFILLED DRESS UP WORK SITE
201802098601 | 2018-12-06 | LEAD | 1013 | LEBOUEF |  | WILK | MI LEAK ON SIDEWALK INLET SERVICE LEAK IN THE MUD PLOT FLOODING SIDEWALK & NEXT DOOR /** 1) MN: A151891 SN: 0093193, *TAP: SIZE: A LOC: 115 FEET FROM P LINE AT NEWTON, *MB: CODE: CD LOC: ON LE BOEUF 114' FROM PL NEWTON 8' OUTSIDE PL 2' I ****/ | 2019-01-05 | EXCAVATED IN GUTTER BOTTOM AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201802099201 | 2018-12-06 | LEAD | 1806 | ROBERT | DANNEEL | WILK | MI- LEAK IN THE STREET EXAMINE INLET SERVICE FOR LEAK IN ASPHALT STREET FLOODING GUTTER BOTTOM 12/10/18 BROKEN METER BOX CASING ***(RIM AROUND CASING BROKEN)*** (KSW) /** 1) MN: C026592 SN: 0055839, *TAP: SIZE: C LOC: 54 FEET FROM P LINE AT DANNEEL, *MB: CODE: AD25 LOC: ON ROBERT,52.5' FROM U.S.P.L. DANNEEL ****/ DOTTIE READY 12/13/18 EXP 01/02/19 | 2018-12-30 | EXCAVATED AND REPAIRED INLET SERVICE LEAK AT MAIN 5 X 7 STREET CUT BACKFILLED NEED PAVING
201802100101 | 2018-12-06 | LEAD | 2213 | TENNESSEE |  | ECLS | MI - TURN OF METER - IRRIGATION METER - NEED TO MAKE REPAIRS OUTSIDE PLEASE CALL UPON ARRIVAL CHANGED FROM 2207 TENNESSEE EMGCY CLOSE SERVICE CUSTOMER REQUEST BURIED SERVICE BE TURNED OFF TO MAKE REPAIRS /** 1) MN: A210931 SN: 0101517, *TAP: SIZE: B LOC: 471 FEET FROM P LINE AT GALVEZ N, *MB: CODE: ADK LOC: ON TENNESSEE 471FT FROM PL OF N GALVEZ 7FT OUTSIDE ****/ | 2018-12-19 | ARRIVED AT ABOVE LOCATION + FOUND WATER TURNED OFF ALREADY METER MARKED WITH BLUE PAINT AFTER LOCATING IT
201802102201 | 2018-12-06 | LEAD | 726 | MARIGNY | DAUPHINE | WOLK | ML- METER LEAK METER#A267563 ACT# 120034-480823 EXAMINE OUTLET SERVICE FOR A LEAK, WITH CON REG /** 1) MN: A267563 SN: 0034172, *TAP: SIZE: A LOC: 104 FEET FROM P LINE AT DAUPHINE, *MB: CODE: BDLM LOC: ON MARIGNY 104FT FROM DAUPHINE ****/ | 2018-12-19 | MADE 4 X 4 BRICK WORK CUT AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA NO CONSTANT ON METER
201802104301 | 2018-12-06 | LEAD | 817 | ATLANTIC AV | SLIDELL | WILK | ML-METER LEAK METER#A392206 ACCT#224769-402465 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A287309 SN: 0052706, *TAP: SIZE: __ LOC: 149 FEET FROM P LINE AT SLIDELL, *MB: CODE: CDK2 LOC: ON ATLANTIC 147FT FROM SLIDELL ****/ | 2019-01-05 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201802104701 | 2018-12-06 | LEAD | 1719 | LAMANCHE | N DERBIGNY | WILK | WM-LEAK IN THE STREET INLET SERVICE LEAK IN STREET INTERFERRING WITN CONTRACTORS WORK FOUND JOB EXCAVATED /** 1) MN: A256692 SN: 0135010, *TAP: SIZE: B LOC: 153 FEET FROM P LINE AT NO. DERBIGNY, *MB: CODE: OOOO LOC: ON LAMANCHE, 153' FROM P.L. NO. DERBIGNY, 8' OUT- ****/ | 2018-12-19 | FOUND JOB COMPLETED
201802105901 | 2018-12-07 | LEAD | 5914 | N VILLERE | GORDON | WILK | ML- METER LEAK METER# A416861 ACCT# 305186-722097 EXAMINE INLET SERVICE FOR A LEAK. FOUND METER OFF LEFT METER OFF /** 1) MN: SN: 0089776, *TAP: SIZE: C LOC: 9 FEET FROM P LINE AT VILLERE N, *MB: CODE: OOO LOC: ON GORDON 9FT FROM VILLERE ****/ | 2018-12-19 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK + ALSO RAISED 5/8 INCH METER BOX BOTTOM TO GRADE BACKFILLED + DRESSED UP AREA
201802107401 | 2018-12-07 | LEAD/PLASTIC | 1719 | GEN TAYLOR |  | WRMS | INSP L UDEUBOR STATES METER IS UNABLE TO BE CHANGED. SERVICE IS UNDER A FENCE AND NEEDS TO BE RELOCATED. PLEASE REPAIR AND CHANGE METER A387465 LOC 103271 RELOCATE METER FROM UNDER FENCE AND CHANGE METER /** 1) MN: A148531 SN: 0005864, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT CARONDELET, *MB: CODE: AFLM LOC: ON GENERAL TAYLOR 149.5FT FROM LSPL CARONDELET ****/ DOTTIE READY 12/13/18 EXP 01/02/19 | 2019-01-05 | ARRIVED AT ABOVE LOCATION ,EXCAVTED AND RELOCATED METER BOX FROM UNDER FENCE TO SIDEWALK.BACKFILLED CLEANED UP AND WASHED DOWN AREA TO COMPLETE JOB.(SOC 5FT .X 2 FT S/W) CHANGED METER LEAD (INLET & PLASTIC OUTLET) *****************OLD METER INFO************** METER:A387465 FAC:74973083 MAKE:SENUS READ:36802
201802109501 | 2018-12-07 | LEAD | 2722 | TOULOUSE | N BROAD | WMTLK | WM-LEAK ON SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** 1) MN: C021361 SN: 0153299, *TAP: SIZE: C LOC: 253 FEET FROM P LINE AT WHITE N, *MB: CODE: CDL LOC: ON TOULOUSE 253FT FROM WHITE 10FT OUTSIDE ****/ | 2019-02-11 | EXCAVATED IN EXISTING CUT AND MADE REPAIRS ON 1 INCH OUTLET SERVICE BACKFILLED AREA
201802116101 | 2018-12-10 | LEAD | 1707 | PALMER AV | PALMER AV | WMTLK | ACCT#145732-567856. METER#C024907.METERHAS A CON REG. NO VISIBLE S7W TO PERFORM TEST. /** 1) MN: A190436 SN: 0008693, *TAP: SIZE: A LOC: 94 FEET FROM P LINE AT PALMER AVE, *MB: CODE: BEHM LOC: SIDE WALK SIDE ST 9305 FT FROM PALMER AVE. ** 2) MN: C024907 SN: 0008693, *TAP: SIZE: C LOC: 96 FEET FROM P LINE AT PALMER AV, *MB: CODE: __ LOC: 93'FROM LOWER P/L PALMER- IN. MAIN LOCATED IN SWA ****/ DOTTIE READY 12-13-18 EXP 1-2-19 | 2019-01-01 | EXAMINED AND PUMPED METER BOX DOWN AND REPLACED 3/4 INCH WAHERS ON INLET AND OUTLET
201802117401 | 2018-12-10 | LEAD | 1236 | GALLIER | URQUHART | WOLK | WM-LEAK IN SIDEWALK EXAMINE OUTLET SERVICE @ PROPERTY LINE /** 1) MN: A233278 SN: 0044848, *TAP: SIZE: A LOC: 43 FEET FROM P LINE AT URQUHART, *MB: CODE: CDL4 LOC: CURB 44' P.L. URQUHART ****/ | 2018-12-25 | EXCAVATED 3 X 2 MU DPLOT AT PROPERTY MADE REPAIR ON OUTLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802118501 | 2018-12-10 | LEAD | 500 | NAPOLEON AV |  | WMBK | LOCATION: 116268 PER INSP LU, METER BOX BURIED UNDER CEMENT INSIDE METER BOX. PLEASE LOCATE AND CHANGE METER# A 212280 REPAIR BROKEN CURB COCK & METER BOX CASING, ALSO SET 5/8 METER /** 1) MN: A212280 SN: 0172685, *TAP: SIZE: A LOC: 74 FEET FROM P LINE AT TCHOUPITOULAS, *MB: CODE: BEK2 LOC: ON NAPOLEON AVE 74FT FROM PL OF TCHOUPITOULAS ****/ DOTTIE READY 12-17-18 EXP 1-6-19 | 2019-01-01 | EXAMINED JOB AND BROKE CEMENT FROM INSIDE METER BOX AND REPLACED 5/8 INCH METER OLD METER INFO: A212280 FACT: 28187076 MAKE: ROCKWELL READ: 3897
201802119401 | 2018-12-10 | LEAD | 3920 | LOUISIANA AV | DELACHAISE | WILK | ML-- METER LEAK METER# B042844 ACCT# 303852-723172 INLET SERVICE LEAK BEHIND CURB COCK, FLOODING GUTTER BOTTOM /** 1) MN: A218029 SN: 0044739, *TAP: SIZE: A LOC: 168 FEET FROM P LINE AT DORGENOIS S, *MB: CODE: OOOO LOC: ON DELACHAISE 162FT FROM CORNER PL S DORGENOIS ****/ DOTTIE READY 1-30-19 EXP 2-19-19 | 2019-02-03 | ARRIVED ON JOB SITE EXAMINED LEAK EXCAVATED IN MUD PLOT BY HAND MADE REPAIRS ON SERVICE ANDSET UP NEW METER BOX COMPETE BACKFILLED DRESSED UP WORK SITE
201802120901 | 2018-12-10 | LEAD | 3327 | JEFFERSON AV |  | WMBK | INSP J DESSELLE STATES HE IS UNABLE TO SET METER. SERVICE NEEDS BOTTOM PLATE REINSTALLED. PLEASE REPAIR AND CHANGE METER A340498 LOC 154671 UPPER METER BOX CASING SHIFTED OVER HANDWHEEL /** 1) MN: A262298 SN: 0091002, *TAP: SIZE: A LOC: 207 FEET FROM P LINE AT GALVEZ S, *MB: CODE: CD LOC: 207FT FROM PL S GALVEZ ON JEFFERSON AVE ****/ DOTTIE READY 12-26-18 EXP 1-15-19 | 2019-01-01 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH BOTTOM AND METER BACKFILLED AREA **************OLD METER INFO********* METER:A340498 FAC:59811627 MAKE:SENSUS READ:960
201802121301 | 2018-12-10 | LEAD | 1701 | PRYTANIA | EUTERPE | WILK | WM - LEAK ON THE SIDEWALK CHANGED FROM N/A PRYTANIA INLET SERVICE LEAK BEHIND CURB COCK FLOODING GRASSY ARE & GUTTER ABOTTOM 3 HOUSES DOWN /** 1) MN: A316223 SN: 0013696, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT PRYTANIA, *MB: CODE: AEHN LOC: ON EUTERPE,44' FROM U.S.P.L. PRYTANIA ** 2) MN: A312772 SN: 0013696, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT PRYTANIA, *MB: CODE: AEHN LOC: SIDE ST/EUTERPE 40.5 FT FROM PL PRYTANIA THERE IS 1 MORE NOT LISTED. ****/ DOTTIE READY 12-14-18 EXP 1-3-18 | 2018-12-29 | REPLACED 5/8 ICH HNDWHEEL + GUTS IN METER BOX ALSO REPLACED DAMAGED 5/8INCH WATER METER ALSO REPLACED 5/8 INCH METER BOX BOTTOM OLD METER INFO: A312772 FACT: 52532255 MAKE: SENSUS READ: 572
201802122101 | 2018-12-10 | LEAD | 4001 | TOULOUSE |  | WILK | ML-METER LEAK ACCT#152320-518587 MTR#A221651 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A221651 SN: 0053098, *TAP: SIZE: A LOC: 69 FEET FROM P LINE AT TOULOUSE, *MB: CODE: BDH3 LOC: ON NO PIERCE 69FT. FRM TOULOUSE PL 9' OUTSIDE PL ****/ | 2018-12-26 | EXCAVATED GUTTER BOTTOM MUD PLOT OF PROPERTY RENEWED OUTLET FROM METER BOX TO PROPERTY AND REPLACED 5/8 INCH METER BOX COCK BACKFILED AND CLEANED THE AREA
201802122801 | 2018-12-10 | LEAD/PLASTIC | 19 | PINEWOOD CT | CYPRESS ACRES DR | WILK | ML-METER LEAK METER#A384155 ACCT#235893-407186 INLET SERVICE LEAK IN GRASS FLOODING GUTTER BOTTOM /** 1) MN: A224149 SN: 0164462, *TAP: SIZE: B LOC: 0 FEET FROM P LINE AT , *MB: CODE: __ LOC: ON PINEWOOD 25FT FROM PL CYPRESS ACRES 9FT OUTS ****/ | 2019-02-06 | ARRIVED ON JOB SITE EXAMAINED LEAK IN MUD PLOT EXCAVATED IN MUD PLOT MADE REPAIRS ON INLET SERVICE BACKFILLED DRESS UP WORK SITE
201802123501 | 2018-12-10 | LEAD | 1660 | TREASURE | BRUXELLES | WILK | ML-METER LEAK METER#A419821 ACCT#162180-726650 INLET SERVICE LEAK IN GUTTER BOTTOM /** 1) MN: A343699 SN: 0101060, *TAP: SIZE: A LOC: 208 FEET FROM P LINE AT BRUXELLES, *MB: CODE: ADKO LOC: 208FT FROM PL BRUXELLES 9' OUTSIDE PL ****/ | 2018-12-21 | REPLACED 5/8 INCH WASHER S TO STOP LEAK
201802123601 | 2018-12-10 | LEAD | 3129 | DAUPHINE |  | WMTLK | ML METER LEAK ACCOUNT #104522-427141 METER#A376924 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A148991 SN: 0014349, *TAP: SIZE: A LOC: 0 FEET FROM LINE AT DAUPHINE, *MB: CODE: CEM LOC: ****/ | 2018-12-20 | MADE 2 X 4 CUT IN SIDEWALK AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201802123901 | 2018-12-10 | LEAD | 2651 | TOURO |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 134425-496372 METER NUMBER - A355889 EXAMINE INLET SERVICE FOR LEAK VEHICLES RUNNING OVER METER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-20 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK + 5/8 INCH METER BOX BOTTOM BACKFILLED + DRESSED UP AREA
201802124101 | 2018-12-10 | LEAD | 2025 | TOURO |  | WILK | WM-LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET /** 1) MN: A276274 SN: 0064426, *TAP: SIZE: A LOC: 108 FEET FROM P LINE AT GALVEZ N, *MB: CODE: BD LOC: ON TOURO,110' FROM P.L. NO. GALVEZ ****/ | 2018-12-25 | ARRIVED AT ABOVE LOCATION FOUND LEAK IN STREET COMPLETED EXAMINED METER + FOUND LEAK ON 5/8 INCH HANDWHEEL REPLACED HANDWHEEL DRESSED UP AREA
201802124401 | 2018-12-10 | LEAD | 6418 | GEN DIAZ | BRAGG | WILK | WM- LEAK BETWEEN SIDEWALK AND STREET INLET SERVICE LEAK IN MUDPLOT **CHANGED FROM 6424 GEN DIAZ** /** 1) MN: A151962 SN: 0104492, *TAP: SIZE: A LOC: 141 FEET FROM P LINE AT BRAGG, *MB: CODE: BDLM LOC: ON GEN DIAZ 142' FROM PL BRAGG 8' OUTSIDE PL ****/ | 2019-01-02 | EXCAVATED A 4 X 6 MUDPLOT CUT & REPAIED A 5/8 INLET SERVICE LEAK. FOUND LEAD PIPE ON INLET SERVICE. BACKFILL DRESSED JOBSITE.
201802126701 | 2018-12-11 | LEAD | 1816 | ALLEN | N ROMAN | WILK | WATER INLET SERVICE /** 1) MN: A301045 SN: 0065133, *TAP: SIZE: A LOC: 153 FEET FROM P LINE AT ROMAN N, *MB: CODE: CDK LOC: 2FT RIVER SIDE OF POST 152FT FROM PL N ROMAN ****/ | 2018-12-07 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH METER COCK BACKFILLED AND CLEANED THE AREA
201802126801 | 2018-12-11 | LEAD | 1375 | ANNETTE | N VILLERE | WMLK | WATER MAIN LEAK /** 1) MN: A237314 SN: 0049915, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT VILLERE N, *MB: CODE: AE LOC: ON ANNETTE 76FT FROM PL OF N VILLERE ****/ | 2018-12-09 | EXCAVATED IN ASPHALT STREET + MADE REPAIR ON ABANDONED 3/4 INCH INLET SERVICE LINE COMPACTED BACKFILLED + DRESSED UP AREA
201802126901 | 2018-12-11 | LEAD | 1717 | MC SHANE PL | ST BERNARD AV | WILK | *************PICKUP**************** BAD CURB COCK ACC#152069-486055 MN#A280677 /** 1) MN: A280677 SN: 0039903, *TAP: SIZE: A LOC: 2 FEET FROM P LINE AT MC SHANE PL, *MB: CODE: BFNO LOC: 89FT FROM PL ST BERNARD AVE ON MC SHANE PL ****/ DOTTIE READY 12-14-18 EXPIRE 01-03-19 | 2018-12-26 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201802128301 | 2018-12-11 | LEAD | 5314 | BURGUNDY |  | WILK | INSP L UDUEBOR STATES HE IS UNABLE TO SET METER BECAUSE THERE IS A BAD INLET LEAK THAT IS FLOODING AREA. PLEASE REPAIR AND SET 5/8 METER. LOC 306454 INLET SERVICE LEAK ALSO SET 5/8 METER HOUSE UNDER RENOVATION /** 1) MN: A288873 SN: 0095622, *TAP: SIZE: A LOC: 143 FEET FROM P LINE AT EGANIA, *MB: CODE: ADK LOC: ON BURGUNDY 123FT FROM PL OF EGANIA 9FT OUTSIDE PL ****/ | 2018-12-21 | EXAMINED JOB AT ABOVE LOCATION AND UNABLE TO DO JOB DUE TO CONTRACTOR HAVE PILE WOOD ON JOB SITE
201802128302 | 2018-12-22 | LEAD | 5314 | BURGUNDY |  | WILK | EXAMINED JOB AT ABOVE LOCATION AND UNABLE TO DO JOB DUE TO CONTRACTOR HAVE PILE WOOD ON JOB SITE /** 1) MN: A288873 SN: 0095622, *TAP: SIZE: A LOC: 143 FEET FROM P LINE AT EGANIA, *MB: CODE: ADK LOC: ON BURGUNDY 123FT FROM PL OF EGANIA 9FT OUTSIDE PL ****/ | 2018-12-28 | EXCAVATED 3 X 2 GUTTER BOTTOM ALSO 4 X 2 MUD PLOT RELOCATED METER FROM GUTTER TO MUD PLOT AND LEFT WHIP OUT FOR CUSTOMER TO TIE INTO BACKFILLED AND CLEANED THE AREA
201802128801 | 2018-12-11 | LEAD | 1711 | N ROMAN |  | WILK | WATER INLET SERVICE /** 1) MN: 000000 SN: 0062455, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT NEW ORLEANS, *MB: CODE: BDK LOC: ON N ROMAN ST 76' FROM LSPL NEW ORLEANS ****/ | 2018-12-20 | ARRIVED AT ABOVE LOCATION + FOUND AREA FLOODED PUMPED DOWN + EXCAVATED IN MUD PLOT + MADE REPIR ON 3/4 INCH ABANDONED WATER SERVICE IN EMPTY LOT BACKFILLED + DRESSED UP AREA
201802128901 | 2018-12-11 | LEAD | 2118 | N DORGENOIS |  | WILK | WATER INLET SERVICE LEAK /** 1) MN: A235328 SN: 0099936, *TAP: SIZE: A LOC: 157 FEET FROM P LINE AT PAUGER, *MB: CODE: BDK LOC: ON NO. DORGENOIS, 157' FROM P.L. PAUGER, 6.5' OUT- ****/ | 2018-12-20 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201802129201 | 2018-12-11 | LEAD | 2215 | N GALVEZ |  | WMBK | SERVICE NEEDS A NEW CASING AND LID. PLEASE REPAIR METER A326855 LOC 146192 BROKEN METER BOX BOTTOM ALSO MISSING METER BOX COVER, LEFT 1 BARRICADE ON SITE /** 1) MN: A294201 SN: 0047328, *TAP: SIZE: B LOC: 132 FEET FROM P LINE AT ELYSIAN FIELDS AVE, *MB: CODE: ADN1 LOC: 132' P.L. ELYSIAN FIELDS AV ****/ | 2018-12-20 | CLEANED OUT DIRT + ROCK OUT OF METER BOTTOM PLACED METER BOX ASING AND COVER AT THIS LOCATION
201802132101 | 2018-12-11 | LEAD | 4834 | DAUPHINE |  | WILK | ML-- METER LEAK METER # A321010 ACCT# 120088-424374 EXAMINE INLET SERVICE FOR LEAK IN BOX /** 1) MN: A314674 SN: 0034234, *TAP: SIZE: B LOC: 43 FEET FROM P LINE AT DESLONDE, *MB: CODE: CF LOC: BY STEPS 43' P.L. DESLONDE ****/ | 2018-12-20 | EXCAVATED IN MJD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201802134601 | 2018-12-11 | LEAD | 2741 | DUMAINE | N WHITE | WILK | ML-METER LEAK METER#A226812 ACCT#131441-725752 INLET SERVICE L EAK IN SIDEWALK /** 1) MN: A144508 SN: 0047619, *TAP: SIZE: A LOC: 319 FEET FROM P LINE AT BROAD N, *MB: CODE: CDK1 LOC: ON DUMAINE,319' FROM P.L. NO. BROAD ****/ | 2018-12-24 | EXCAVATED IN MUD PLOT THROUGH HEAVY TREE ROOTS + REPLACED REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201802134801 | 2018-12-11 | LEAD | 3157 | TRAFALGAR | GENTILLY BL | WILK | ML-METER LEAK METER#C036447 ACCT#302274-190977 INLET SERVICE LEAKING INTO METER BOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-24 | REPLACED 1 ICH WASHERS IN METER BOX
201802136101 | 2018-12-12 | LEAD | 2207 | TENNESSEE |  | WILK | WATER METER LEAK /** 1) MN: A210931 SN: 0101517, *TAP: SIZE: B LOC: 471 FEET FROM P LINE AT GALVEZ N, *MB: CODE: ADK LOC: ON TENNESSEE 471FT FROM PL OF N GALVEZ 7FT OUTSIDE ****/ | 2018-12-12 | EXCAVATED 2 X 2 MUD PLOT LOCATED METER BOX AND RAISED TO GRADE ALSO MARKED METER BOX WITH BLUE PAINT BAKFILLED AND CLEANED THE AREA LEFT METER BOX OFF FOR CUSTOMER AS REQUESTED
201802137501 | 2018-12-12 | LEAD | 2925 | ESPLANADE AV |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 144798-490934 METER NUMBER - A374404 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A290067 SN: 0076283, *TAP: SIZE: A LOC: 60 FEET FROM P LINE AT GAYOSO N, *MB: CODE: CDIO LOC: ON ESPLANADE 60' FROM PL OF GAYOSO N ****/ | 2018-12-24 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201802137801 | 2018-12-12 | LEAD | 822 | NEWTON | ELMIRA AV | WILK | WM- LEAK AT THE CURB INLET SERVICE LEAK IN MUDPLOT FLOODINR CURB /** 1) MN: A260158 SN: 0045779, *TAP: SIZE: A LOC: 152 FEET FROM P LINE AT ELMIRA AVE, *MB: CODE: AD LOC: ON NEWTON 150FT FROM U.R.P.L. ELMIRA AVE ****/ | 2019-01-05 | EXCAVATED IN MUD PLOT AND REPLACED 5/8INCH CURB COCK BACKFILLED AREA JOB COMPLETE
201802138901 | 2018-12-12 | LEAD | 437 | S RENDON | BANKS | WILK | MI-LEAK IN GRASSY AREA EXAMINE INLET SERVICE FOR AL EAK BETWEEN CURB & STREET /** 1) MN: 000000 SN: 0067049, *TAP: SIZE: B LOC: 188 FEET FROM P LINE AT BANKS, *MB: CODE: ADN2 LOC: ON S RENDON 201FT PL BANKS 8' OUTSIDE 3' INSIDE CU ** 2) MN: A116125 SN: 0067030, *TAP: SIZE: B LOC: 188 FEET FROM P LINE AT BANKS, *MB: CODE: BDN2 LOC: ON RENDON 187' FROM PL OF BANKS ****/ | 2018-12-24 | EXCAVATED IN GUTTER BOTTOM AND MADE REPAIR ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201802139301 | 2018-12-12 | LEAD | 946 | WILSON DR | DUMAINE | WOLK | ML- METER LEAK METER #: A408192 ACCT#: 141354-514245 CUSTOMER HAS METER LEAK OUTLET SERVICE LEAK IN MUDPLOT /** 1) MN: A275683 SN: 0072257, *TAP: SIZE: B LOC: 329 FEET FROM P LINE AT DUMAINE, *MB: CODE: BDM2 LOC: ON WILSON DR 329' FROM PL DUMAINE ST ****/ | 2018-12-20 | EXCAVATWED 3 X 3 MUD PLOT RENEW OUTLET SERVICE TO CUSTOMER BACKFILLED AND CLEANED THE AREA
201802141301 | 2018-12-12 | LEAD | 1412 | POLAND AV | N CLAIBORNE AV | WOLK | MI- LEAD WHIP *****AREA EXPOSED****** CHANGE LEAD WHIP HOLE OPENED /** 1) MN: A223964 SN: 0060438, *TAP: SIZE: A LOC: 102 FEET FROM P LINE AT VILLERE N, *MB: CODE: ADL1 LOC: ON POLAND AVE.,102' FROM U.S.P.L. NO. VILLERE ****/ | 2018-12-17 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8INCH METER BOX TO STOP LEAK AND TIED I OUTLET SERVICE INTO CUSTOMER NEW LINE BACKFILED AND CLEANED THE AREA
201802142001 | 2018-12-12 | LEAD | 2019 | N RAMPART | TOURO | WILK | MI-METER BOX LEAKING NO METER IN BOX INLET SERVICE LEAK IN METER BOX FROM BAD BLEEDER VALVE NO METER IN BOX /** 1) MN: A231442 SN: 0040324, *TAP: SIZE: A LOC: 146 FEET FROM P LINE AT FRENCHMEN, *MB: CODE: CFLM LOC: ON N RAMPART ST 147' FROM USPL FRENCHMEN ST 8' ****/ | 2018-12-28 | EXCAVATED IN CONCRETE SIDEWALK + RPLACED 5/8INCH CURB COCK BACKFILLED + DRESSED UP AREA NO METER
201802142601 | 2018-12-12 | LEAD | 3109 | PITTARI PL | GEN MEYER AV | WILK | MI-LEAK AT THE CURB INLET SERVICE LEAK IN CONCRETE STREET FLOODING STREET & GUTTER BOTTOM FROM PREVIOUS CUT /** 1) MN: B033172 SN: 0126026, *TAP: SIZE: B LOC: 71 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: CD LOC: ON PITTARI PL 71' FROM PL GEN MEYER AVE 8' OUTSID ****/ | 2019-01-26 | ARRIVED ON JOB SITE EXAMINED LEAK IN STREET MADE CUT IN STREET EXCAVATED IN MUD PLOT OVER WATER MAIN MADE REPAIRS ON SRVICE AT WATER MAIN BACKFILLED DRESSED UP WORK SITE
201802143201 | 2018-12-12 | LEAD | 1730 | FELICIANA | N DERBIGNY | WMTLK | ML-METER LEAK METER#A428759 ACCT#302075-481817 EXAMINE INLET/OUTLET SERVICE FOR LEAK INSIDE METER BOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-20 | REPLACED 5/8 INCH WASHERS TO STOP LEAK
201802144101 | 2018-12-13 | LEAD | 2539 | ST ANN |  | WOLK | LOCATION# 222108 CUSTOMER# 523562 METER# A375871 INSPECTOR DID AN OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION ON METER, CAN'T DETERMINE WHERE LEAK IS COMING FROM...........PLEASE REPAIR /** 1) MN: A274430 SN: 0031862, *TAP: SIZE: A LOC: 124 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CFLM LOC: ON ST ANN ST 124' FROM LRPL N. DORGENOIS ST ****/ | 2018-12-20 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201802144701 | 2018-12-13 | LEAD | 920 | ST ANN |  | WMTLK | LOCATIONID#210355-528572 METER#A265186 LEAK INSIDE METERBOX /** 1) MN: A292344 SN: 0031064, *TAP: SIZE: B LOC: 2 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CD LOC: ON ST ANN 2' FROM DIV. P.L. BURGUNDY, 8' OUTSIDE, ****/ | 2018-12-26 | EXCAVATED 3 X 2 TILE SIDEWALK CUT AND WAS UNABLE TO SAVETILE REPLACED 5/8 INCH METER BOX TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802144801 | 2018-12-13 | LEAD | 928 | ST ANN |  | WMTLK | LOCATIONID#107803-708011 METER#B018539 METERBOX OVERFLOWING /** 1) MN: B018539 SN: 0029592, *TAP: SIZE: B LOC: 129 FEET FROM P LINE AT BURGUNDY, *MB: CODE: BEK2 LOC: 129' P.L. BURGUNDY ****/ | 2018-12-26 | REPLACE WASHERS TO STOP LEAK
201802144901 | 2018-12-13 | LEAD | 1013 | ST ANN |  | WMTLK | LOCATIONID#107607-528366 METER#A378630 LEAK INSIDE METERBOX /** 1) MN: A125503 SN: 0001758, *TAP: SIZE: B LOC: 103 FEET FROM P LINE AT BURGUNDY, *MB: CODE: AELN LOC: ON ST ANN 103FT FROM PL OF BURGUNDY ** 2) MN: G001893 SN: 0000000, *TAP: SIZE: G LOC: 91 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CD LOC: ON ST. ANN 98' FROM PL BURGUNDY 17' OUTSIDE PL ****/ | 2019-03-08 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802146101 | 2018-12-13 | LEAD | 6936 | DEANNE | PINE | WMTLK | ML- METER LEAK METER# A365089 ACCT# 168619-451508 EXAMINE INLET & OUTLET SERVICE FOR A LEAK AREA SATURATED /** 1) MN: A264111 SN: 0115899, *TAP: SIZE: A LOC: 279 FEET FROM P LINE AT PINE, *MB: CODE: AFM LOC: RES 276FT FROM PL PINE 7' OUTSIDE PL 2' INSIDE CUR ****/ DOTTIE READY 12-21-18 EXPIRE 01-10-19 | 2018-12-25 | EXCAVATED AND REPAIRED INLET SERVICE
201802147601 | 2018-12-13 | LEAD | 810 | FRENCH | MEMPHIS | WILK | ML- METER LEAK MN:A253459 ACCT#141889-510693 INLET SERVICE LEAK /** 1) MN: A253459 SN: 0090930, *TAP: SIZE: A LOC: 114 FEET FROM P LINE AT MEMPHIS, *MB: CODE: CDM LOC: 108' P.L. MEMPHIS ****/ | 2018-12-13 | EXCAVATED IN CONCRETE SIDEWALK REPAIR 5/8 STOP & WASTE LEAD LINE DRESS UP WITH RIVERSAND & COLDMILL
201802148001 | 2018-12-13 | LEAD/PLASTIC | 609 | HUNTLEE DR | HERSCHEL | WMTLK | MI-LEAK IN SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR LEAK INSIDE BOX /** 1) MN: A297893 SN: 0115508, *TAP: SIZE: A LOC: 151 FEET FROM P LINE AT HERSCHEL, *MB: CODE: AFL LOC: ON HUNTLEE 151FT FROM HERSHEL 5FT OUTSIDE ****/ | 2019-01-04 | EXAMINED AREA REMOVED WATER FROM AREA EXCAVATED ON INLET AND OUTLET OBSERVED LEAK ON INLET REPAIRED LEAK RENEWED OUTLET FROM METER TO PROERTY REPLACING LEAD LINE RAISED METER TO GRDAE AND BACKFILLED AND CLEANED AREA
201802148201 | 2018-12-13 | LEAD | 3206 | BARONNE | HARMONY | WILK | ML- METER LEAK METER # A423670 ACCT# 120025-548085 INLET SERVICE LAK BAD BLEEDER VALVE /** 1) MN: A282775 SN: 0034474, *TAP: SIZE: A LOC: 70 FEET FROM P LINE AT HARMONY, *MB: CODE: CD LOC: ON BARONNE 70.7FT HARMONY ****/ | 2018-12-13 | EXCAVATED IN MUDPLOT REPAIR 5/8 STOP & WASTE LEAD LINE DRESS UO WITH RIVERSAND JOB COMPLETE
201802148901 | 2018-12-13 | LEAD | 413 | N MIRO | CONTI | WMLK | WATER LEAK -MAIN. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A117000 SN: 0073339, *TAP: SIZE: A LOC: 105 FEET FROM P LINE AT CONTI, *MB: CODE: CDLN LOC: 105FT FROM PL CONTI 9' OUTSIDE PL ****/ | 2018-12-25 | EXCAVATED AND REPAIRED INLET SERVICE LEAK
201802149001 | 2018-12-13 | LEAD | 617 | HAGAN AV | ST PETER | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-25 | REPAIRED 1 INCH INLET SERVICE LEAK THIS IS A FUTHER SERVICE. NO DRESS-UP NEEDED. JOB COMPLETE
201802149501 | 2018-12-13 | LEAD | 2041 | TERPSICHORE |  | WILK | WM - LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET FLOODING STREET & GUTTER BOTTOM GETTING OFF IN DCB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ DOTTIE READY 12/20/18 EXP 1/9/19 | 2018-12-30 | EXCAVATED IN ASPHALT STREET + REPLACED 1 INCH BEND ADAPTER ON WATER MAIN COMPACTED BACKFILL + DRESSED UP AREA
201802149601 | 2018-12-13 | LEAD | 1932 | LAPEYROUSE |  | WMBK | INLET IS A 5/8 OUTLET IS A 3/4 PLEASE REPAIR AND SET A 3/4 METER CUSTOMER IS WAITING ON WATER LOCATION #306599 METER BOX BOTTOM BROKEN /** 1) MN: B024224 SN: 0045388, *TAP: SIZE: B LOC: 51 FEET FROM P LINE AT JOHNSON N, *MB: CODE: BFK LOC: 51FT FROM URPL JOHNSON ****/ | 2018-12-20 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK WITH A 3/4 INCH CURB COCK ALSO REPLACED BROKEN 3/4 INCH METER BOX BOTTOM + RING BACKFILLED + DRESSED UP AREA ALSO SET 34/ INCH METER
201802150001 | 2018-12-13 | LEAD | 5416 | ANNUNCIATION | JEFFERSON AV | WILK | WM - LEAK IN THE STREET CHANGED FROM 5400 ANNUNICATION EXAMINE INLET SERVICE LEAK IN ASPHALT STREET CAUSING DEPRESSION IN STREET FOUND ONE SKINNY BARREL ON SITE /** 1) MN: A245604 SN: 0124458, *TAP: SIZE: A LOC: 145 FEET FROM P LINE AT JEFFERSON AVE, *MB: CODE: AEK7 LOC: ON ANNUNCIATION 145FT PL JEFFERSON AV 4' OUTSIDE ****/ DOTTIE READY 12/20/18 EXP 1/9/19 | 2018-12-30 | EXCAVATED IN ASPHALT STREET + REPLACED 3/4 INCH BEND ADAPTER ON WATER MAIN COMPACTED BACKFILL + DRESSED UP AREA. JOB COMPLETE
201802150301 | 2018-12-13 | LEAD | 1918 | GORDON | N PRIEUR | WILK | MI- LEAK IN THE SIDE WALK INLET SERVICE LEAK IN MUDPLOT FLOODING AREA **CHANGED FROM 1124 GORDON** /** 1) MN: A265009 SN: 0129585, *TAP: SIZE: A LOC: 231 FEET FROM P LINE AT PRIEUR N, *MB: CODE: CDLN LOC: MTR ON GORDON 231FT FROM PL PRIEUR BY MAIL BOX ****/ | 2018-12-26 | FOUND AREA FLOODS EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH ABANDONED INLET SERVICE LINE BACKFILLED + DRESSED UP AREA NO METER
201802151301 | 2018-12-14 | LEAD | 3237 | ST ANN | HAGAN AV | WOLK | ACCT# 190693-520574 MTR# A401232 INSPECTOR FOUND SLOW CONSTANT REGISTRATION ON METER /** 1) MN: A143142 SN: 0049832, *TAP: SIZE: A LOC: 44 FEET FROM P LINE AT ST ANN, *MB: CODE: AD4L LOC: ON HAGAN 42' FROM PL ST ANN 8' OUTSIDE PL 4' INSID ****/ | 2018-12-26 | EXCAVATED IN MUD PLOT AND MADE REPAIRS 3/4 ICH OUTLET SERVICE BACKFILLED AREA NO CONSTRANT ON METER.METER WAS ALREADY OFF WHEN EXAMINED JOB
201802153901 | 2018-12-14 | LEAD | 2177 | N DORGENOIS |  | WILK | ML-- METER LEAK MTR# A317397 ACT # 147939-496483 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A231330 SN: 0080053, *TAP: SIZE: B LOC: 90 FEET FROM P LINE AT FRENCHMEN, *MB: CODE: CDL LOC: METER ON N DORGENOIS 91 FT FROM PL FRENCHMEN ****/ | 2018-12-26 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK AND METER BOTTOM BACKFILLED AREA
201802154401 | 2018-12-14 | LEAD | 2122 | ALMONASTER AV |  | WMRE | ***********************PICKUP*********************** LOCATE SERVICE, RAISE TO GRADE AND MARK /** 1) MN: A214891 SN: 0067550, *TAP: SIZE: A LOC: 154 FEET FROM P LINE AT GALVEZ NO., *MB: CODE: CDIL LOC: ON EADS,152.4' FROM P.L. NO. GALVEZ ****/ | 2018-12-27 | EXCAVATED IN MUD PLOT AND LOCATED AND RAISED MEER TO GRADE MARK WITH BLUE PAINT BACKFILLED AREA
201802154801 | 2018-12-14 | LEAD | 1429 | N VILLERE | KERLEREC | WILK | PP-POOR PRESSURE ACCT# 113883- 486290 METER# A350431 EXAMINE INLET SERVICE FOR LEAK, METER BOX SHIFTED OVER CURB COCK /** 1) MN: A234182 SN: 0016703, *TAP: SIZE: A LOC: 127 FEET FROM P LINE AT KERLEREC, *MB: CODE: AFM3 LOC: 126' P/L KERLEREC ****/ | 2018-12-26 | EXCAVATED IN GARDEN AND FOUND NOLEAK AND PRESSURE GOOD REPLACED METER BOX CASING BACKFILLED AREA
201802155701 | 2018-12-14 | LEAD | 2725 | AMAZON | FLORENCE DR | WILK | MI- LEAK BETWEEN STREET AND SIDEWALK EXAMINE INLET SERVICE LEAK IN MUDPLOT @ CURB FOR A LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-05 | EXCAVATED AND REPLACED INLET SERVICE FROM MAIN TO METER BOX ALSO RAISED METER BOX TO GRADE 3 X 5 MUD CUT BACKFILLED NO DRESS UP NEEDED 5 X 7 MUD CUT BACKFILLED NO DRESS UP NEEDED
201802156001 | 2018-12-14 | LEAD | 1725 | ST CLAUDE AV | ST ANTHONY | WILK | MI-LEAK IN GRASSY AREA IN FRONT VACANT PROPERTY INLET SERVICE LEAK ON SIDEWALK FLOODING CURB/STREET /** 1) MN: A300005 SN: 0059756, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT ST ANTHONY AVE, *MB: CODE: BD LOC: 131' P.L. ST ANTHONY AVE ****/ | 2018-12-25 | EXCVAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201802157501 | 2018-12-15 | LEAD/PLASTIC | 2418 | MARTIN LUTHER KING BL | FRERET | WMLK | MI- LEAK IN STREET LEAK ON WATER MAIN IN STREET /** 1) MN: A154439 SN: 0011894, *TAP: SIZE: B LOC: 99 FEET FROM P LINE AT FRERET, *MB: CODE: BDIN LOC: 97FT FROM URPL FRERET ****/ DOTTIE READY 12/20/18 EXP 1/09/19 | 2019-01-08 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 3/4 CORP.COCK LEAKING AT 4"WATER MAIN .REPLACED 3/4 CORP. COCK AND 5FT .OF 3/4 TUBING TIED INTO LEAD.
201802157601 | 2018-12-15 | LEAD | 2122 | FELICITY | S LIBERTY | WILK | ML- METER LEAK METER#A334622 ACCT#112674-545427 INLET SERVICE LEAK INSIDE METER BOX ALSO BAD CURB COCK NO METER IN BOX /** 1) MN: SN: 0014548, *TAP: SIZE: D LOC: 154 FEET FROM P LINE AT LIBERTY S, *MB: CODE: ADFL LOC: 142FT FROM PL LOYOLA ON LIBERTY S ****/ DOTTIE READY 12/20/18 EXP 1/9/19 | 2018-12-26 | ARRIVED ON THE SITE EXAMINE THE PROBLEM .CURB COCK WAS LEAKING.FROM THE FRONT ANDD THE BLEEDER WAS LEAKING BROKE SIDE WALK WITH MAUL ALSO LEAD ON THE INLET SIDE CHANGED CURB COCK ALSO METER IN BOX ALSO USED A NIPPLE.(2FT. X 2 FT. S/W)
201802158201 | 2018-12-15 | LEAD | 1639 | SOUTHLAWN BL |  | WILK | ML-METER LEAK ACCT#237992-406955 MTR#A413492 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: C023740 SN: 0141373, *TAP: SIZE: __ LOC: 0 FEET FROM P LINE AT SOUTHLINE DR, *MB: CODE: BDKM LOC: ON SOUTHLAWN BLVD., 51' FROM D.P.L. AMGELLAN, 1' ****/ | 2019-01-05 | EXAMINE AND PUMPED METER DOWN AND REPLACED 1 INCH WAHERS IN INLET OUTLET INSIDE METER BOX
201802159201 | 2018-12-15 | LEAD | 2682 | CLOVER |  | WMTLK | LOCATIONID#127553-476820 METER#A320816 LEAK INSIDE METERBOX /** 1) MN: A320816 SN: 0084968, *TAP: SIZE: B LOC: 10 FEET FROM P LINE AT LOTUS, *MB: CODE: AD LOC: ON CLOVER,9' FROM P.L. LOTUS ****/ | 2019-01-02 | EXCAVATED IN MUDPLOT TO TRY AND REPAIR LEAK ON LEAD INLET SERVICE. DID NOT HAVE ENOUGH ROOM TO REPAIR LEAK FROM MUDPLOT SO WE HAVE TO CATCH IT FROM THE STREET AND REMVOE LEAD SERVICE. (JOB CONTINUED)
201802159301 | 2018-12-15 | LEAD | 2004 | ST ROCH AV |  | WMTLK | LOCATIONID#129084-483350 METER#A392918 LEAK INSIDE METERBOX /** 1) MN: A208788 SN: 0057482, *TAP: SIZE: C LOC: 46 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CD LOC: ON ST ROCH AVE 45FT FROM PL OF N JOHNSON ****/ | 2018-12-31 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH WHEEL ON OUTLET BACKFILLED AREA
201802161301 | 2018-12-16 | LEAD | 814 | N GALVEZ | ST ANN | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLGICS. /** 1) MN: A309812 SN: 0045549, *TAP: SIZE: A LOC: 86 FEET FROM P LINE AT ST ANN, *MB: CODE: AFL1 LOC: ON N GALVEZ 112.8' FROM LRPL ST ANN ****/ | 2019-02-13 | EXAMINE JOB AT ABOVE LOCATION FOUND COMPLETE AT AN EARLIER DATE
201802162001 | 2018-12-16 | LEAD | 1738 | FLOOD | N ROMAN | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A319622 SN: 0138826, *TAP: SIZE: A LOC: 303 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BD LOC: ON FLOOD 303FT FROM PL DERBIGNY ****/ | 2018-12-31 | EXCAVATED 3 X 2 MUD PLOT IN RAIN REPLACED 5/8 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802162101 | 2018-12-16 | LEAD | 1807 | FORSTALL | N ROMAN | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: 000000 SN: 0096530, *TAP: SIZE: B LOC: 53 FEET FROM P LINE AT ROMAN N, *MB: CODE: DK LOC: RES - 53' P.L. N ROMAN ****/ | 2019-01-02 | EXAMINED PUMPED METER DOWN AND REPLACED 5/8 INCH WASHERS ON INLET AND OUTLET
201802162201 | 2018-12-16 | LEAD | 1842 | INDUSTRY | NEW ORLEANS | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A316686 SN: 0078678, *TAP: SIZE: B LOC: 16 FEET FROM P LINE AT NEW ORLEANS, *MB: CODE: CDL1 LOC: 16' P.L. NEW ORLEANS ****/ | 2019-01-02 | EXCAVATED 3 X 2 MUD PLOT REPLACED METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802162301 | 2018-12-16 | LEAD | 2000 | TUPELO | N PRIEUR | WMLK | WATER LEAK -MAIN. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A283832 SN: 0130767, *TAP: SIZE: A LOC: 7 FEET FROM P LINE AT JOHNSON N, *MB: CODE: ADLN LOC: RES ON TUPELO 6FT P.L. N JOHNSON 6' OUTSIDE ****/ | 2019-01-04 | EXCAVATED IN MUD POT AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED AREA REFERRED TO P. DAVENPORT ALSO (PET)
201802162401 | 2018-12-16 | LEAD | 1926 | BENTON | N JOHNSON | WMLK | WATER LEAK -MAIN. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. ***LEAK IS IN FRONT OF OVERGROWN LOT.**** /** 1) MN: A280574 SN: 0129855, *TAP: SIZE: A LOC: 206 FEET FROM P LINE AT PRIEUR N, *MB: CODE: CELM LOC: ON BENTON 206' PL N PRIEUR OPP 3RD IRON POST 7' ****/ | 2019-01-02 | MADE 8 X 8 CUT IN BLACK TOP STREET AND MADE REPAIR ON 3/4 INCH TAILPIECE ON 6 INCH WATER MAIN BACKFILLED AREA. JOB COMPLETE
201802162501 | 2018-12-16 | LEAD | 1932 | INDUSTRY | ANNETTE | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A310276 SN: 0078613, *TAP: SIZE: A LOC: 94 FEET FROM P LINE AT ANNETTE, *MB: CODE: BDK LOC: ON INDUSTRY 94' FROM URPL OF ANNETTE ****/ | 2019-01-02 | EXCAVATED 3 X 2 MUD PLOT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA METER INFO FOR VACANT LOT NEXT TO ADDRESS ABOVE
201802162701 | 2018-12-16 | LEAD | 1940 | BENTON | N JOHNSON | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A220186 SN: 0131503, *TAP: SIZE: A LOC: 15 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CDM1 LOC: ON BENTON 15FT FROM PL N JOHNSON 6FT INSIDE CURB ****/ | 2019-01-02 | EXCAVATED IN MUD PLOT AND MADE REPAIR ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201802162901 | 2018-12-16 | LEAD | 2110 | FLOOD | N MIRO | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A264767 SN: 0136006, *TAP: SIZE: B LOC: 110 FEET FROM P LINE AT NO. GALVEZ, *MB: CODE: CD24 LOC: ON FLOOD, 110' FROM P.L. NO. GALVEZ, 7' OUTSIDE ****/ | 2019-01-02 | EXCAVATED AT EDGE OF STREET AND MADE REPAIR ON 1 INCH SERVICE FOR ABANDON LOT BACKFILLED. JOB COMPLETE
201802163001 | 2018-12-16 | LEAD | 2111 | CONTI | N GALVEZ | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: C027982 SN: 0090315, *TAP: SIZE: C LOC: 90 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CDL LOC: ON CONTI,90' FROM P.L. NO. JOHNSON,8' OUTSIDE P.L. ****/ | 2018-12-31 | EXCAVATED IN BRICK SIDEWALK + REPLACED 5/8 INCH CURB COCK+ 5/8 INCH HANDWHEEL + 3/4 INCH OUTLET SERVICE LINE FROM METER BOX TO PROOERTY BACKFILLED + DRESSED UP AREA
201802163101 | 2018-12-16 | LEAD | 2417 | TUPELO | N DORGENOIS | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: SN: 0135229, *TAP: SIZE: A LOC: 142 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: ADL2 LOC: ON TUPELO 143FT FROM PL ROCHEBLAVE N 8FT OUTSIDE ****/ | 2019-01-02 | EXCAVTED 3 X 2 DRIVEWAY CUT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802163401 | 2018-12-16 | LEAD | 2510 | CHARBONNET | N DORGENOIS | WMLK | WATER LEAK -MAIN. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A263902 SN: 0136369, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: ADLM LOC: ON CHARBONNET 83FT FROM PL DORGENOIS ****/ | 2019-01-07 | MADE 10 X 10 CUT IN BLACK TOP STREET AND CORKED JOINT ON 12 INCH WATER MAIN BACKFILLED AREA
201802163501 | 2018-12-16 | LEAD | 2548 | BIENVILLE | N DORGENOIS | WOLK | WATER LEAK -OUTLET. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A268032 SN: 0047080, *TAP: SIZE: B LOC: 54 FEET FROM P LINE AT BIENVILLE, *MB: CODE: DHL LOC: ON NO. DORGENOIS,56.8' FROM U.R.P.L. BIENVILLE ****/ | 2018-12-31 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED TWO 3/4 INCH OUTLET SERVICE LINE FROM METER BOX TO PROOERTY BACKFILLED + DRESSED UP AREA
201802164301 | 2018-12-16 | LEAD | 2622 | CHARBONNET | FLORIDA AV | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A311567 SN: 0134215, *TAP: SIZE: A LOC: 166 FEET FROM P LINE AT LAW, *MB: CODE: ADEM LOC: RES ON CHARBONNET 163FT PL LAW 6FT OUTSIDE ****/ | 2019-01-07 | MADE 6 X 6 CUT IN BLACK TOP STREET AND MADE REPAIR ON 3/4 INCH TAILPIECE FOR ABANDONED LOT BACKFILLED AREA
201802164501 | 2018-12-16 | LEAD | 2832 | LAFITTE | N WHITE | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: D004512 SN: 0125868, *TAP: SIZE: CCC LOC: 141 FEET FROM P LINE AT WHITE N, *MB: CODE: __ LOC: ON LAFITTE 141FT. FROM PL WHITE 2' OUTSIDE PL 9' I ****/ | 2019-01-04 | EXCAVATED 4 X 3 SIDEWALK CUT FOUND LEAK AT PROPERTY UNABLE TO MAKE REPAIR DUE TO BUILDING FOUNDATION LEFT METER OFF TO STOP LEAK AND DUE TO BUILDING BEING ABANDONED BACKFILLED AND CLEANED TEH AREA
201802165701 | 2018-12-16 | LEAD | 3028 | ORLEANS AV | N SALCEDO | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT /** 1) MN: A299941 SN: 0029428, *TAP: SIZE: B LOC: 43 FEET FROM P LINE AT SALCEDO N, *MB: CODE: CDLM LOC: 44FT. FRM PL N SALCEDO ON ORLEANS ****/ | 2018-12-31 | EXCAVATED IN MUD PLOT + SIDEWALK +REPLACED 5/8 INCH CURB COCK + 5/8 INCH HANDWHEEL + TWO 3/4 INCH OUTLET SERVICE LINE AT ABOVE LOCATION BACKFILLED + DRESSED UP AREA ALSO REPLACED ONE 5/8 INCH METER BOX BOTTOM
201802166601 | 2018-12-16 | LEAD | 520 | FLOOD | DOUGLAS | WILK | ML- METER LEAK METER# A404667 ACCT# 120903-425315 INLET SERVICE LEAK INSIDE BOX /** 1) MN: 000000 SN: 0054838, *TAP: SIZE: A LOC: 105 FEET FROM P LINE AT CHARTRES, *MB: CODE: BFL LOC: ON FLOOD ST 103.5' FROM URPL CHARTRES ST ****/ | 2019-01-02 | REPLACED WASHERS TO STOP LEAK
201802166701 | 2018-12-16 | LEAD | 4016 | ROYAL | BARTHOLOMEW | WILK | ML- METER LEAK METER# A336912 ACCT# 100979-716079 ****FLOODING AREA***** INLET SERVICE LEAK IN SIDEWALK FLOODING SIDEWALK /** 1) MN: A336912 SN: 0004088, *TAP: SIZE: B LOC: 120 FEET FROM P LINE AT BARTHOLOMEW, *MB: CODE: OOO LOC: ON ROYAL,120' FROM L.P.L. ROYAL ****/ | 2019-01-02 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED METER BOX COCK BACKFILL AND CLEANED THE AREA
201802168801 | 2018-12-17 | LEAD | 717 | DESLONDE | ROYAL | WILK | WM-LEAK IN SIDEWALK NEAR GRASSY AREA CHANGED FROM 711 DESLONDE INLET SERVICE LEAK INSIDE METER BOX BAD BLEEDER VALVE, ***METER # A645426 IN FRONT 711 DESLONDE*** , ALSO LEAK INSIDE PROPERTY /** 1) MN: A323211 SN: 0057991, *TAP: SIZE: A LOC: 77 FEET FROM P LINE AT ROYAL, *MB: CODE: BDL7 LOC: ON DESLONDE 79.6FT FROM PL OF ROYAL ****/ | 2019-01-11 | EXCAVATED 2 X 2 DRIVEWAY CUT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802169301 | 2018-12-17 | LEAD | 1214 | ALVAR | MARAIS | WILK | ML- METER LEAK METER# A360520 ACCT# 117231-430155 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A283124 SN: 0024149, *TAP: SIZE: A LOC: 119 FEET FROM P LINE AT MARAIS, *MB: CODE: DL1 LOC: 119' P.L. MARAIS ****/ | 2018-12-27 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201802169701 | 2018-12-17 | LEAD | 1320 | TULANE AV | LOYOLA AV | WILK | WM-LEAK IN SIDEWALK **********DAMAGE CLAIM********** *****1ST AM***** CUT INLET SERVICE BY COASTAL DRILLING UTILITY INTERFERING WITH CONTRACTORS WORK. *****RUSSELL BAKER***** UNSURE IF ANYONE OUT OF WATER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-18 | EXCAVATED 5 X 3 SIDEWALK CUT BY HAND MADE REPAIR 1 INCH ABANDON INLET SERVICE CUT BY COASTAL DRILLING UTILITY BACKFILLED AND CLEANED THE AREA
201802169801 | 2018-12-17 | LEAD | 5759 | DAUPHINE |  | WILK | CUSTOMER HAS BEEN WAITING ALMOST A MONTH FOR WATER. PREVIOUS SR 12858865, ISSUED BY JUNE M LARCHE ISSUED ON 11/27/18. SERVICE IS BURIED AND NEEDS TO BE RAISED TO GRADE. OUTLET NEEDS TO BE TIED IN ALSO. PLEASE REPAIR AND SET 5/8 METER. CUSTOMER ASKED TO BE CALLED WHEN SOMEONE GOES TO LOCATION TO COMPLETE JOB. MR HAMDAN 5043334817 LOC 306149 CUSTOMER WAINTING FOR TIE IN ***HOUSE UNDER RENOVATIONS*** /** 1) MN: A178542 SN: 0062094, *TAP: SIZE: A LOC: 158 FEET FROM P LINE AT CHARBONNET, *MB: CODE: BF LOC: ON DAUPHINE,157' FROM P.L. CHARBONNET ****/ | 2018-12-25 | EXCVATED 5 X 2 MUD PLOT TO LOCATE BURNIED METER BOX SET ONE METER BOX COMPLETE WITH 5/8 INCH METER ALSO LEFT WHIP OUT FOR CUSTOMER TO TIE INTO BACKFILLED AND CLEANED THE AEA
201802172001 | 2018-12-17 | LEAD | 2108 | MUSIC |  | WILK | WM-LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET FLOODING AREA GETTING OFF IN DCB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-25 | EXCAVATED IN ASPHALT STREET + MADE REPAIRS ON 3/4 INCH ABANDONED INLET SERVICE LINE THAT WAS FLOODING AREA
201802172501 | 2018-12-17 | LEAD | 2934 | CLEVELAND AV | S GAYOSO | WMTLK | ML: METER LEAK ACCT# 117712-714799 MTR# A397892 EXAMINE INLET & OUTLET SERVICE LEAK IN MUDPLOT & TREE ROOTS METER BOX UNDER WATER /** 1) MN: A339972 SN: 0026789, *TAP: SIZE: A LOC: 58 FEET FROM P LINE AT CLEVELAND AVE, *MB: CODE: BFH6 LOC: SIDE ST 2ND METER ON S GAYOSA 58 FT CLEVELAND AVE ****/ | 2018-12-27 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH HANDWHEEL + 3/4 INCH OUTLET SERVICE LINE FROM METER BOX TO PROPERTY BACKFILLED + DRESSED UP AREA
201802172601 | 2018-12-17 | LEAD | 1016 | PAULINE | N RAMPART | WOLK | ML- METER LEAK MN:A406977 ACCT#115605-702816 OUTLET SERVICE LEAK INSIDE METER BOX CONSTANT REG /** 1) MN: A279018 SN: 0019682, *TAP: SIZE: A LOC: 138 FEET FROM P LINE AT RAMPART N, *MB: CODE: CELM LOC: 138FT FROM USPL N RAMPART,METER ON PAULINE ****/ | 2018-12-27 | EXCAVATED 3 X 2 BRICK SIDEWALK RENEWED OUTLET UP TO PROOETY BACKFILED AND CLEANED THE AREA LEFT BRICK STACKED UP AGAINST THE FENCE
201802174001 | 2018-12-17 | LEAD | 1519 | ELEONORE | HURST | WMTLK | ML--METER LEAK ACCOUNT # 121669-564110 METER # A393548 EXAMINE INLET/OUTLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: A329518 SN: 0039312, *TAP: SIZE: B LOC: 138 FEET FROM P LINE AT HURST, *MB: CODE: CDL LOC: ON ELEONORE 138FT FROM PL OF HURST ****/ DOTTIE READY 12-26-18 EXP 1-15-19 | 2018-12-30 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201802174201 | 2018-12-17 | LEAD | 2216 | ALMONASTER AV | N TONTI | WOLK | ML-METER LEAK ACCT#164344-484712 METER#A415919 EXAMINE OUTLET SERVICE INSIDE METER BOX CONSTANT REG ON METER /** 1) MN: A298532 SN: 0078270, *TAP: SIZE: B LOC: 204 FEET FROM P LINE AT TONTI N, *MB: CODE: OOO LOC: ON ALMONASTER AVE., 208' FROM P.L. NO. TONTI ****/ | 2019-02-12 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION NO CONSTANT REGISTRATION METER
201802174701 | 2018-12-18 | LEAD/PLASTIC | 308 | NEIL AV | AURORA DR | WOLK | LOCATION#229881-417325. METER HAS A CON REG. NO S&W TO PERFORM TEST. METER#A400409 /** 1) MN: A233988 SN: 0139208, *TAP: SIZE: B LOC: 112 FEET FROM P LINE AT AURORA DR, *MB: CODE: CDL1 LOC: ON NEIL AVE 112FT FROM P.L. AURORA DR 6FT OUTSIDE ****/ | 2018-12-28 | WE EXCAAVTED BY HAND AND DID FIND A LEAK ON A 5/8 LEAD LINE LEAK SO WE REPLACE THE OLD ONE WITH A NEW ONE THERE IS STILL A LEAK ON THE OWNER WE BACKFILL PLUS CLEAN UP WE DUG IN TREE ROOTS
201802177401 | 2018-12-18 | LEAD | 1122 | BURGUNDY | URSULINES AV | WILK | MI-METER LEAK BAD BLEEDER VALVE LEKAING IN SIDEWALK /** 1) MN: A139005 SN: 0021719, *TAP: SIZE: A LOC: 131 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: AE LOC: 141' P.L. GOV NICHOLLS ****/ | 2018-12-27 | MADE 4 X 4 CUT IN SLATE SIDEWALK AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201802179701 | 2018-12-18 | LEAD | 1625 | JOURDAN AV |  | WMBK | INSP D JOHNSON STATES SERVICE NEEDS TO BE REPAIRED. CASING SMASHED AND HE IS UNABLE TO CHANGE METER. PLEASE REPAIR AND CHANGE METER C032697 LOC 179042 UPPER METER BOX CASING /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2018-12-21 | EXCAVTED 2 X 2 MUD PLOT REPLACED 1 INCH METER AND ADOPTER RING WITH CASING BACKFILLED AND CLEANED THE AREA ***********OLD METER INFO******* METER: C036372 FAC:16359065 MAKE:SENSUS READ:0
201802182301 | 2018-12-18 | LEAD | 1100 | ELYSIAN FIELDS AV | ST CLAUDE AV | WILK | MI LEAK AT CURB FLOODING AREA CHANGED FROM 1100 ST CLAUDE AV/ELYSIAN FIELDS **********1ST AM******** INLET SERVICE LEAK IN MUDPLOT ON SIDE OF TREE FLOODING CURB & STREET IN FRONT WALGREENS PARKING LOT /** 1) MN: C021266 SN: 0171292, *TAP: SIZE: C LOC: 125 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: BDK1 LOC: ON ELYSIAN FIELDS AVE 125FT FROM P.L. ST CLAUDE AV ** 2) MN: SN: 0000000, *TAP: SIZE: __ LOC: 0 FEET FROM LINE AT , *MB: CODE: __ LOC: HYDRANT IS LOCATED ON THE CORNER OF ELYSIAN FIELDS ****/ | 2018-12-20 | MADE 8 X 8 CUT IN CONCRETE BASE STREET AND MADE REPAIR ON 3/4 INCH INLET SERVICE THAT ABANDON BACKFILLED AREA
201802182701 | 2018-12-18 | LEAD | 2719 | PALMYRA | JANE AL | WILK | WM-LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET /** 1) MN: A256274 SN: 0047994, *TAP: SIZE: A LOC: 79 FEET FROM P LINE AT JANE ALLEY, *MB: CODE: AF LOC: ON PALMYRA,80.5' FROM L.R.P.L. JANE ALLEY ****/ | 2018-12-28 | EXCAVATED INGUTTER BOTTOMAND MADE REPIR ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201802183901 | 2018-12-19 | LEAD/PLASTIC | 3213 | LUNA | HORACE | WMTLK | LOCATIONID#226763-408217 METER#A356433 LEAK INSIDE METERBOX /** 1) MN: A288244 SN: 0145858, *TAP: SIZE: A LOC: 147 FEET FROM P LINE AT HORACE, *MB: CODE: L LOC: ON LUNA 147FT FROM HORACE 4FT OUTSIDE ****/ | 2019-01-07 | EXAMINED AREA PUMPED DOWN WATER IN METER BOX EXCAVATED ON INLET SERVICE REPAIRED LEAK ON INLET SERVICE BACKFILLED CLEANED AREA
201802185401 | 2018-12-19 | LEAD | 327 | S WHITE |  | WMTLK | LOCATIONID#170944-531581 METER#B042832 LEAK INSIDE METERBOX /** 1) MN: B020744 SN: 0113532, *TAP: SIZE: B LOC: 205 FEET FROM P LINE AT PALMYRA, *MB: CODE: AFK6 LOC: ON SO. WHITE, 205' FROM P.L. PALMYRA, 3' OUTSIDE ****/ | 2018-12-27 | REPLACED 3/4 INCH WASHER TO STOP LEAK
201802185701 | 2018-12-19 | LEAD/PLASTIC | 1012 | BROOKLYN |  | WMTLK | LOCATIONID#223777-708071 METER#B032918 METERBOX OVERFLOWING /** 1) MN: B024671 SN: 0034238, *TAP: SIZE: B LOC: 106 FEET FROM P LINE AT NEWTON, *MB: CODE: BFK2 LOC: ON BROOKLYN, 106' FROM P.L. NEWTON, 1' INSIDE P.L. ****/ | 2019-02-04 | EXAMINED AREA EXCAVATED ON INLET AND OUTLET SERVICE OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK BACKFILLED CLEANED AREA
201802185801 | 2018-12-19 | LEAD | 544 | ESPLANADE AV | CHARTRES | WOLK | ACCOUNT # 104300-427047 METER #D005058 CONST REG /** 1) MN: D005058 SN: 0002220, *TAP: SIZE: D LOC: 99 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: BEHM LOC: MH ON CHARTRES IN SIDEWALK OPP DOOR OF 315 CHARTRE ** 2) MN: SN: 0006745, *TAP: SIZE: C LOC: 62 FEET FROM P LINE AT CHARTRES, *MB: CODE: __ LOC: ON ESPLANADE AVE 61.5FT FROM PL OF CHARTRES ****/ | 2019-04-15 | EXAMINED AND FOUND NOTHING WRONG ABOVE LOCATION
201802186101 | 2018-12-19 | LEAD | 1711 | MARIGNY |  | WMTLK | LOCATIONID#301468-705111 METER#A430868 LEAK INSIDE METERBOX /** 1) MN: A290996 SN: 0058576, *TAP: SIZE: A LOC: 68 FEET FROM P LINE AT DERBIGNY NO., *MB: CODE: BDMK LOC: ON MARIGNY,69.6' FROM L.S.P.L. NO. DERBIGNY ****/ | 2018-12-27 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER BOX COCK TO STOP LEAK BACKFILED AND CLEANED THE AREA
201802186201 | 2018-12-19 | LEAD | 2456 | N ROMAN |  | WILK | LOCATIONID#128117-546790 METER#A421381 BLEEDER LEAK /** 1) MN: A235243 SN: 0042491, *TAP: SIZE: A LOC: 161 FEET FROM P LINE AT MUSIC, *MB: CODE: CDL7 LOC: 900 2455 XXX ON WALL CURB - 160' P.L. MUSIC ****/ | 2018-12-27 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH HANDWHEEL TO STOP LEAK BACKFILED AND CLEANED THE AREA
201802187301 | 2018-12-19 | LEAD | 1305 | FLOOD | URQUHART | WILK | WM: LEAK IN STREET INLET SERVICE LEAK IN THE STREET NEAR CURB GETTING OFF IN THE DCB /** 1) MN: A336815 SN: 0100573, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT URQUHART, *MB: CODE: D LOC: ON FLOOD, 47' FROM P.L. URQUHART, 7' OUTSIDE P.L. ****/ | 2018-12-30 | EXCAVATED 14 X 10 STREET CUT MADE REPAIR ON INLETSERVICE LINE AT MAIN BACKFILLED AND CLEANED THE AREA
201802187401 | 2018-12-19 | LEAD | 223 | N RENDON |  | WILK | WM-- LEAK IN STREET NEAR CURB EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A258990 SN: 0051821, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT BIENVILLE, *MB: CODE: N2 LOC: ON N RENDON 116.5FT FROM PL OF BIENVILLE 2FT IN- ****/ | 2019-01-01 | MADE REPAIR INSIDE METER BOX REPLACED HAND WHEEL AND METER BOX WAHERS
201802188001 | 2018-12-19 | LEAD/PLASTIC | 317 | BELLEVILLE | PELICAN | WMTLK | ML- METER LEAK METER# A351887 ACCT# 223854-401744 EXAMINE INLET & OUTLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A260571 SN: 0039099, *TAP: SIZE: A LOC: 109 FEET FROM P LINE AT PELICAN, *MB: CODE: BFK1 LOC: MTR ON BELLEVILLE 109FT FRM PL PELICAN ****/ | 2019-02-01 | WE EXCAVATED TO MAKE REPAIRS TO A 5/8 OUTLET WE ALSO REPAIRS THE LEAD LINE AND INSTALL NEW PLASCTIC FROM METER BOX COMPLETE BY HAND IN TREE ROOTS WE BACKFILL PLUS CLEAN UP
201802189201 | 2018-12-19 | LEAD/PLASTIC | 1623 | BEHRMAN AV | MARDI GRAS BL | WMTLK | ML-- METER LEAK METER #277287 ACCT# 225444-409808 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A277287 SN: 0095493, *TAP: SIZE: B LOC: 144 FEET FROM P LINE AT LAWRENCE, *MB: CODE: CFLN LOC: ON BEHRMAN AVE 144' FROM PL LAWRENCE ****/ | 2019-01-08 | EXAMINED AREA CLEANED OUT METER BOX OBSERVED LEAK ON OUTLET SERVICE EXCAVATED ON INLET AND OUTLET SERVICE REPAIRED LEAK BACKFILLED CLEANED AREA
201802190001 | 2018-12-20 | LEAD | 2138 | ANNETTE |  | WILK | LOCATIONID#136802-434094 METER#A388890 INLET CONNECTION LEAK /** 1) MN: 000000 SN: 0067405, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT ANNETTE, *MB: CODE: CEH LOC: ON NO. MIRO, 54' FROM P.L. ANNETTE ****/ | 2019-01-01 | EXCAVATED AND REPLACED INELT SERVICE ALSO RAISED METER BOX TO GRADE 2' X 2' SIDEWALK CUT BACKFILLED NEED PAVING
201802190101 | 2018-12-20 | LEAD | 2026 | FRENCHMEN |  | WILK | LOCATIONID#112666-494955 METER#A405752 BLEEDER LEAK /** 1) MN: A311051 SN: 0028317, *TAP: SIZE: A LOC: 113 FEET FROM P LINE AT GALVEZ N, *MB: CODE: CD LOC: ON FRENCHMEN 113FT FROM GALVEZ N ****/ | 2018-12-31 | EXCVAVTED 3 X 2 SIDEWALK CUT RENEWED OUTLET TO PROPERTY AND REPLACED 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA **ALSO REPLACED 5/8 METER BOTTOM
201802190201 | 2018-12-20 | LEAD | 1822 | AGRICULTURE |  | WMTLK | LOCATIONID#304525-530194 METER#A415781 LEAK INSIDE METERBOX /** 1) MN: SN: 0078587, *TAP: SIZE: A LOC: 194 FEET FROM P LINE AT LONDON AVE, *MB: CODE: CE LOC: METER ON FRONT STREET ACROSS FROM 2831 NEW ORLEANS ****/ | 2018-12-27 | MADE 4 X 4 CUT IN NEW DRIVEWAY AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201802190301 | 2018-12-20 | LEAD | 2618 | ALLEN |  | WMTLK | LOCATIONID#208096-495809 METER#A359567 LEAK INSIDE METERBOX /** 1) MN: A317241 SN: 0082753, *TAP: SIZE: A LOC: 22 FEET FROM P LINE AT HOPE, *MB: CODE: LFT1 LOC: ON LAW 9FT FROM DIV P/L HOPE 8FT OUTSIDE ****/ | 2018-12-27 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201802191501 | 2018-12-20 | LEAD | 5450 | DAUPHINE | ANDRY | WMTLK | WATER METER LEAK /** 1) MN: A238195 SN: 0041516, *TAP: SIZE: A LOC: 147 FEET FROM P LINE AT FLOOD, *MB: CODE: CD LOC: ON DAUPHINE 147FT FROM URPL FLOOD ****/ | 2018-12-19 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA
201802192501 | 2018-12-20 | LEAD | 1638 | POLAND AV |  | WILK | LOCATION: 306629 INSP UDEBOR SET METER# A 432497 (LEFT WATER OFF) PLEASE REPAIR INLET SERVICE LEAK BEHIND CURB COCK. CUSTOMER WAITING ON WATER BAD BLEERDER VALVE IN SIDEWALK, FOUND OFF LEFT OFF /** 1) MN: A259923 SN: 0136118, *TAP: SIZE: B LOC: 48 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: CDL2 LOC: 45' P/L N DERBIGNY 7' OUTSIDE 3' INSIDE CURB ****/ | 2018-12-27 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201802196101 | 2018-12-21 | LEAD | 3022 | ST PHILIP |  | WILK | ML--METER LEAK ACCOUNT #134148-532599 METER #A317714 EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX. (C) /** 1) MN: A317714 SN: 0064956, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT SALCEDO NO., *MB: CODE: BD LOC: ON ST. PHILIP, 95' FROM U.R.P.L. NO. SALCEDO ****/ | 2019-01-01 | EXCAVATED ND REPLACED OUTLET SERVICE FROM METER BOX TO PROPERTY... 2 X 2 SIDEWALK CUT-->BACKFILLED-->NEED PAVING
201802196501 | 2018-12-21 | LEAD | 2825 | D"ABADIE |  | WMTLK | LOCATIONID#155571-727338 METER#A136742 LEAK INSIDE METERBOX /** 1) MN: A338706 SN: 0071590, *TAP: SIZE: B LOC: 168 FEET FROM P LINE AT DUPRE N, *MB: CODE: CDLN LOC: ON D'ABADIE,166.5'F ROM P.L. NO. DUPRE,11' OUT- ****/ | 2018-12-31 | EXCAVTED IN MUD PLOT WITH TREE ROOTS AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201802201801 | 2018-12-23 | LEAD/PLASTIC | 208 | FOREST OAKS |  | WMTLK | LOCATIONID#302972 METER#C036573 METERBOX OVERFLOWING /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-01 | ARRIVED ON JOB SITE EXAMINE LEAK EXCAVATED IN MUD PLOT MADE REPAIRS ON INLET SERVICE BACKFILLED DRESS UP WORK SITE
201802203001 | 2018-12-23 | LEAD | 5800 | CHARBONNET | FLORIDA AV | WILK | MI- LEAK IN THE STREET CHANGED FROM 5800 FLORIDA AV/PEOPLES AV INLET SERVICE LEAK COMING FROM A VACANT LOT DRAIN STOPPED UP /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-07 | EXAMINED JOB AT ABOVE LOCATION AND FOUND NO LEAK
201802204001 | 2018-12-23 | LEAD/PLASTIC | 2017 | ELIZARDI BL | VESPASIAN BL | WMTLK | ML- METER LEAK METER# A353873 ACCT# 231814-419994 **********1ST AM********** EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER, ALSO WATER POURING OUT OF METER BOX FLOODING CURG GETTING OFF IN THE DCB /** 1) MN: A345258 SN: 0143624, *TAP: SIZE: B LOC: 407 FEET FROM P LINE AT VESPASIAN, *MB: CODE: BDM2 LOC: ON ELIZARDI 18FT FROM DIV P/L WALL 2FT INSIDE ****/ | 2018-12-24 | WE EXCAAVTED TO MAKE REPAIRS TO A 5/8 OUTLET LEAK PLUS A BROKEN METER BOX WE BACKFILL PLUS CLEAN UP
201802205401 | 2018-12-24 | LEAD | 2514 | S TONTI | THIRD | WILK | WM-LEAK IN SIDEWALK ***************J.GILLIAM @ 11:58AM****************** INLET SERVICE LEAK IN MUDPLOT FLOODING AREA /** 1) MN: A232022 SN: 0072371, *TAP: SIZE: A LOC: 126 FEET FROM P LINE AT SECOND, *MB: CODE: AL5 LOC: ON SO. TONTI, 126' FROM P.L. SECOND ****/ | 2018-12-24 | EXCAVATED 3 X 3 GUTTER BOTTOM THROUGH BRICK MADE REPAIR ON INLET SERVICE LINE TO STOP LEAK BACKFILLD AND CLEANED THE AREA
201802206801 | 2018-12-24 | LEAD | 2307 | TENNESSEE | N TONTI | WILK | *************PICKUP*********** INLET SERVICE LEAK IN MUDPLOT FLOODING CURB AT VACANT LOT /** 1) MN: A287375 SN: 0126417, *TAP: SIZE: B LOC: 47 FEET FROM P LINE AT TONTI N, *MB: CODE: BDK LOC: ON TENNESSEE, 48' FROM P.L. NO. TONTI, 8' OUTSIDE ****/ | 2019-01-03 | EXCAVATED 5 X 3 MUD PLOT THROUGH TREE ROOTS RAISED METER BOX UP TO GRADE AND LEFT WHIP OUT FOR FUTURE BUILDING BACKFILL ND CLEANED THE AREA
201802207201 | 2018-12-25 | LEAD | 1509 | MAZANT | N ROBERTSON | WILK | **********************PICKUP*********************** INLET SERVICE LEDAK IN BOX LEAKING FROM CURB COCK @ VACANT LOT /** 1) MN: A113194 SN: 0074066, *TAP: SIZE: B LOC: 65 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: BEK5 LOC: METER ON MAZANT 65 FT FROM PL N ROBERTSON ****/ | 2019-01-03 | EXCAVATED 2 X 2 GUTTER BOTTOM ALSO 1 X 1 SIDEWALK CUT REPLACE METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802208401 | 2018-12-26 | LEAD | 2512 | ANNETTE | HOPE | WILK | INLET SERVICE LEAK /** 1) MN: A287093 SN: 0064930, *TAP: SIZE: A LOC: 111 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CDL LOC: ON ANNETTE ST 11.5' FROM PL N DORGENOIS ****/ | 2018-12-25 | EXCAVATED AND REPAIRED INLET SERVICE LEAK ALSO RAISED METER BOX TO GRADE 3' X 10' STREET CUT BACKFILLED NEED PAVING 3' X 5' STREET CUT BACKFILLED NEED PAVING
201802208801 | 2018-12-26 | LEAD/PLASTIC | 205 | NORLAND AV | AURORA DR | WILK | MI: LEAK IN THE STREET CHANGED FROM 200BLK NORLAND AV INLET SERVICE LEAK IN ASPHSLT STREET FLOODING AREA /** 1) MN: A328536 SN: 0118010, *TAP: SIZE: A LOC: 204 FEET FROM P LINE AT WESTCHESTER, *MB: CODE: CE LOC: MTR ON NORLAND 204FT FRM WESTCHESTER 11FT INSD CRB ****/ | 2019-01-24 | WE EXCAVATED TO MAKE REPAIR TO A 5/8 INLET LEAK IN THE STREET WE BACKFILL PLUS CLEAN
201802209801 | 2018-12-26 | LEAD | 2531 | N CLAIBORNE AV | PAINTERS | WOLK | ML: METER LEAK ACCT# 193632-728832 MTR#A399915 EXAMINE OUTLET SERVICE FOR LEAK @ PROPERTY LINE /** 1) MN: 000000 SN: 0055681, *TAP: SIZE: B LOC: 263 FEET FROM P LINE AT ARTS, *MB: CODE: CDLM LOC: ON NO. CLAIBORNE AVE.,264' FROM P.L. ARTS,8' OUT- ****/ | 2019-01-03 | EXCAVATED 2 X 2 GUTTER BOTTOM REPLACED METER COCK FOR ADDRESS 2531 N CLAIBORNE ALSO FOUND OUTLET SERVICE NOT CONNECT TO THIS ADDRESS BACKFILLED AND CLEANED THE AREA
201802210001 | 2018-12-26 | LEAD/PLASTIC | 426 | THAYER | ALIX | WILK | ML- METER LEAK METER# A428516 ACCT# 302161-475129 INLET SERVICE LEAK IN MUDPLOT FLOODING DRIVEWAY /** 1) MN: A249651 SN: 0127744, *TAP: SIZE: A LOC: 213 FEET FROM P LINE AT ALIX, *MB: CODE: C LOC: ON THAYER, 210' FROM P.L. ALIX, 6' OUTSIDE ****/ | 2019-02-06 | ARRIVED ON JOB SITE EXAMINED LEAK IN MUD PLOT EXCAVATED IN MUD PLOT MADE ON INLET SERVICE BACKFILLED DRESS UP WORK SITE
201802210101 | 2018-12-26 | LEAD | 3820 | PACKARD |  | WILK | ML--METER LEAK ACCOUNT #169270-454947 METER # A367429 EXAMINE INLET SERVICE FOR LEAK IN MUDPLOT /** 1) MN: A305698 SN: 0111206, *TAP: SIZE: A LOC: 129 FEET FROM P LINE AT CHICKASAW, *MB: CODE: BD LOC: MTR ON PACKARD 129FT FRM PL CHICKASAW ****/ | 2019-01-17 | EXCAVATED DOWN ON INLET AND OUTLET SERVICES FROM METER TO PROPERTY. FOUND LEAD SERVICES AND COCK WAS LEAKING. ALSO METER WAS BELOW GRADE. MADE REPAIRS BY REPLAING COCK WASHERS HANDWHEEL ALSO OUTLET SERVICE FROM METER TO PROPERTY AND RAISED METER TO GRADE. BACKFILLED
201802210601 | 2018-12-26 | LEAD | 1925 | PAULINE | N JOHNSON | WILK | MI- LEAK IN THE SIDEWALK INLET SERVICE LEAK INFRONT ABANDON LOT NO METER IN BOX /** 1) MN: A261300 SN: 0084457, *TAP: SIZE: B LOC: 160 FEET FROM P LINE AT PRIEUR N, *MB: CODE: AM2 LOC: 160FT FROM N.PRIEUR ****/ | 2019-01-03 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201802211601 | 2018-12-26 | LEAD | 821 | LAMANCHE | DAUPHINE | WMTLK | ML-METER LEAK MTR # C030047 ACCT# 130825-425379 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** 1) MN: C023043 SN: 0061026, *TAP: SIZE: Y LOC: 159 FEET FROM P LINE AT DAUPHINE, *MB: CODE: CD LOC: ON LAMANCHE 156' FROM LPL DAUPHINE ST ****/ | 2018-12-31 | REPLACE WASHERS AND DAMAGE 1 INCH METER TO STOP LEAK **************OLD METER INFO********* METER:C030047 FAC:70692471 MAKE:SENSUS READ:3167
201802211701 | 2018-12-26 | LEAD | 1841 | LAMANCHE |  | WOLK | ML METERLEAK MTR#A244642 LOC/CUST#184203-424022 CONS REG ON METER. /** 1) MN: A244642 SN: 0136189, *TAP: SIZE: B LOC: 48 FEET FROM P LINE AT LAMANCHE, *MB: CODE: CEHL LOC: RES ON N PRIEUR 50' PL LAMANCHE 6' OUTSIDE ****/ | 2018-12-31 | REPLACE 5/8 INCH WASHERS TO STOP LEAK
201802212901 | 2018-12-26 | LEAD | 1110 | LIZARDI | FORSTALL | WILK | ML-METER LEAK ACCT#142244-706604 METER# A421441 /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ INLET LEAK IN THE DRIVEWAY FL00DING THE CURB. | 2019-01-03 | REPLACED WASHERS TO STOP LEAK
201802213001 | 2018-12-26 | LEAD | 2233 | CANAL | N MIRO | WILK | WM- LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET FLOODING STREET **1ST AM** /** 1) MN: B025002 SN: 0001777, *TAP: SIZE: B LOC: 100 FEET FROM P LINE AT FROM RLPL CANAL, *MB: CODE: AEH LOC: 99.9" FROM RLPL CANAL ST. ****/ | 2018-12-27 | EXAMINED ABOVE LOCATION FOUND NOTHING WRONG WITH WATER METER
201802213601 | 2018-12-26 | LEAD/PLASTIC | 108 | MAUMUS AV | WESTCHESTER PL | WOLK | MI-LEAK IN SIDEWALK****CUSTOMER STATES SIDEWALK IS CONSTANTLY WET WHEN THERE IS NO RAIN***** EXAMINE OUTLET SERVICE LEAK IN SIDEWALK FLOODING SIDEWALK /** 1) MN: A277995 SN: 0117022, *TAP: SIZE: A LOC: 16 FEET FROM P LINE AT WOODLAND HWY, *MB: CODE: BDLD LOC: ON MAUMUS 18' FROM PL WOODLAND HWY 4' OUTSIDE PL ****/ | 2019-01-25 | EXAMINED AREA CLEANED OUT METER BOX TESTED METER METER CHOKED EXCAVATED ON OUTLET SERVICE TO PROPERTY OBSERVED LEAK ON OUTLET SERVICE RENEWED OUTLET SERVICE BACKFILLED CLEANED AREA INSTALLED NEW METER DRESSED UP AREA WITH SAND OLD METER INFO: A277995 FACT: 45181365 MAKE: ROCKWELL READ: 3148
201802213801 | 2018-12-26 | LEAD | 2945 | PONCE DE LEON | SAUVAGE | WILK | WM-LEAK IN THE STREET INLET SERVICE LEAK IN MUDPLOT FLOODING CURB/STREET /** 1) MN: SN: 0045330, *TAP: SIZE: B LOC: 178 FEET FROM P LINE AT SAUVAGE, *MB: CODE: CDLM LOC: 180FT FROM PL SAUVAGE 8' OUTSIDE PL 2' INSIDE CURB ****/ | 2019-01-04 | REPLACED WAHERS TO STOP LEAK
201802213901 | 2018-12-26 | LEAD | 6000 | BURGUNDY |  | WOLK | MI - SET METER PER JUNE LARCHE SUP ACCT#306662-728826 5/8 METER HANDWHEEL HAS BEEN REMOVED UNABLE TO SET 5/8 METER VACANT BUILDING UNDER RENOVATIONS /** 1) MN: 000000 SN: 0079219, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CDHN LOC: 1ST SIDE GUTTER PIPE - ON GORDON 47' P.L. BURGUNDY ****/ | 2018-12-27 | EXCAVATED 2 X 2 MUD PLOT REPLACED 5/8 INCH HANDWHEEL AND SET 5/8 METER BACKFILLED AND CLEANED THE AREA
201802215601 | 2018-12-27 | LEAD | 1301 | FRANKLIN AV |  | WMTLK | WM - LEAK ON THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR LEAK, METER UNDER WATER CARS PARKING ON METER /** 1) MN: A331469 SN: 0045137, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT ALMONASTER AVE, *MB: CODE: BDH1 LOC: SIDE ST ON URQUHART 49' P.L. ALMONASTER AVE ****/ | 2019-01-07 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201802216501 | 2018-12-27 | LEAD/PLASTIC | 3600 | BENNETT |  | WMTLK | MI - LEAK AT WHEEL SIDE OF METER MTR # A346053 LOC/SER # 238560-411116 /** 1) MN: SN: 0999999, *TAP: SIZE: A LOC: 40 FEET FROM P LINE AT RANKIN, *MB: CODE: CD LOC: ON BENNETT 40FT FROM RANKIN 4FT OUTSIDE ****/ | 2019-01-08 | EXAMINED AREA CLEANED OUT METER BOX OBSERVED LEAK ON INLET SERVICE EXCAVATED ON INLET SERVICE REPAIRED LEAK BACKFILLED AND CLEANED AREA
201802216701 | 2018-12-27 | LEAD/PLASTIC | 5721 | WICKFIELD DR | PRENTISS AV | WOLK | LOCATION ID-166632 MTR-A384068 UNDERGROUND LEAK BETWEEN MTR AND STOP & WASTE/CONS ON MTR /** 1) MN: A271972 SN: 0107178, *TAP: SIZE: A LOC: 258 FEET FROM P LINE AT PRENTISS AVE, *MB: CODE: ADLZ LOC: 258FT FROM PL PRENTISS MTR ON WICKFIELD 5FT OUTSD ****/ | 2019-01-16 | EXCAVATED IN MUD PLOT REPAIR OUTLET SERVICE LEAK RENEW OUTLET AND CHANGE BAD METER BOX COCK FOUND LEAD ON INLET
201802218201 | 2018-12-27 | LEAD | 1228 | N ROBERTSON | ESPLANADE AV | WILK | ML: METER LEAK ACCT#209754-525897 METER# A420883 INLET SERVICE LEAK ON SIDEWALK ON THREE (3) ABANDON SERVICES NO METER IN BOXES 1ST TWO (2) METER BOXES FROM ESPLANADE AV LEAKING FROM CURBCOCK WITH LOCKING DEVICE IN EACH BOX 3RD METER BOX FROM GOV NICHOLLS /** 1) MN: A191173 SN: 0007481, *TAP: SIZE: B LOC: 38 FEET FROM P LINE AT ESPLANADE, *MB: CODE: BEL1 LOC: ON N ROBERTSON 39FT FROM D.P.L. ESPLANADE AVE ** 2) MN: A298100 SN: 0007481, *TAP: SIZE: C LOC: 38 FEET FROM P LINE AT ESPLANADE, *MB: CODE: BEL1 LOC: ON N ROBERTSON 38FT FROM D.P.L. ESPLANADE AVE 5FT THERE ARE 6 MORE NOT LISTED. ****/ | 2019-01-07 | EXCAVATED 2 X 2 SIDEWALK CUT MADE REPAIR ON INLET SERVICE LINE AT METER BOX BACKFILLED AND CLEANED THE AREA
201802220301 | 2018-12-28 | LEAD | 1919 | PORT |  | WMBK | UNABLE TO SET METER. SERVICE ONLY HAS A METER PAN. PLEASE INSTALL CASING AND SET 5/8 METER. LOC 131050 BROKEN METER BOX ALSO SET 5/8 METER /** 1) MN: A327793 SN: 0071968, *TAP: SIZE: A LOC: 196 FEET FROM P LINE AT PRIEUR NO., *MB: CODE: CD LOC: ON PORT,193' FROM L.P.L. NO. PRIEUR ****/ | 2018-12-30 | EXCAVATED 3 X 2 MUD PLOT REPLACE METER BOTTOM AND SET 5/8 METER ALSO TIE INTO OUTLET BACKFILLED AND CLEANED THE AREA
201802220802 | 2018-12-28 | LEAD | 7521 | JEANNETTE | LOWERLINE | SLEAD | FOUND THE SEWER LINE BROKE 8 FT. OUT /** 1) MN: A281940 SN: 0062935, *TAP: SIZE: A LOC: 179 FEET FROM P LINE AT LOWERLINE, *MB: CODE: CDN LOC: 179' P.L. LOWERLINE ****/ | 2018-12-29 | EXAM AND FOUND 8 INCH S.M.L AND 6 INCH SHC CHOKED WALKED MAIN LINE AND FOUND DOWN S.M.H AND FLUSHED 350 FT OUT TO BREAK REEXAM 6 INCH SHC AND FLUSHED 50 FT OUT TO MAIN LEFT BOTH SYSTEM DOWN AND RUNNING (JOB COMPLETE)
201802222201 | 2018-12-28 | LEAD | 1018 | BIENVILLE | N RAMPART | WILK | ML: METER LEAK METER#C035220 ACCT#207484-522153 INLET SERVICE LEAK IN BRICK SIDEWALK /** 1) MN: C023202 SN: 0168099, *TAP: SIZE: C LOC: 42 FEET FROM P LINE AT RAMPART N, *MB: CODE: OOO LOC: ON BIENVILLE 41FT FROM PL N RAMPART ** 2) MN: C022237 SN: 0168099, *TAP: SIZE: C LOC: 42 FEET FROM P LINE AT RAMPART N, *MB: CODE: OOO LOC: ON BIENVILLE APT D 44FT FROM PL N RAMPART THERE ARE 3 MORE NOT LISTED. ****/ | 2019-01-07 | REPLACED 1 INCH WASHERS IN METER BOX ALSOREPLACED DAMAGE METER WATER METER WAS A 5/8 INCH METER WITH 1 INCH ADAPTERS ON IT REPLACED METER BOX WITH PROPER 1 INCH WATER METER
201802222901 | 2018-12-29 | LEAD | 810 | ST PETER | BOURBON | WILK | MI- LEAK IN SIDEWALK BAD BLEEDER VALVE IN BRICK SIDEWALK, NO METER IN BOX /** 1) MN: G001446 SN: 0028943, *TAP: SIZE: G LOC: 122 FEET FROM P LINE AT BOURBON, *MB: CODE: BRW LOC: ON ST. PETER IN FRONT OF 817 ST. PETER IN ST. ** 2) MN: SN: 0028943, *TAP: SIZE: B LOC: 91 FEET FROM P LINE AT BOURBON, *MB: CODE: __ LOC: ****/ | 2019-02-05 | EXCAVATED 2 X 2 SIDEWALK CUT THROUGH BRICKS REPLACED 5/8 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE
201802225601 | 2018-12-30 | LEAD | 5442 | DAUPHINE | FLOOD | WMTLK | ML- METER LEAK METER#A335497 ACCT#122739-425324 EXAMINE INLET & OUTLET SERVICE FOR A LEAK (C) /** 1) MN: 000000 SN: 0041518, *TAP: SIZE: A LOC: 205 FEET FROM P LINE AT FLOOD, *MB: CODE: ADL LOC: ON DAUPHINE,209' FROM URPL FLOOD ST ****/ | 2019-01-07 | REMOVED MUD + SAND OUT OF METER BOX FOUND NO LEAK AT THIS LOCATION
201802227201 | 2018-12-31 | LEAD | 1912 | INDEPENDENCE | N PRIEUR | WMTLK | ML-METER LEAK ACCT#158741-432227 METER#A389837 EXAMIN INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** 1) MN: A322115 SN: 0096390, *TAP: SIZE: B LOC: 167 FEET FROM P LINE AT PRIEUR N, *MB: CODE: BD LOC: 167'PL N PRIEUR ON INDEPENDENCE 8FT OUT PL 2FT ****/ | 2019-01-07 | EXAMINED JOB + FOUND NO LEAK
201802227401 | 2018-12-31 | LEAD | 102 | E PARK PL | CENTRAL PARK PL | WILK | WM-LEAK IN SIDEWALK **********1ST AM********** INLET SERVICE LEAK IN MUDPLOT IN FRONT OF METER NEAR TREE FLOODING AREA /** 1) MN: A124099 SN: 0092768, *TAP: SIZE: A LOC: 278 FEET FROM P LINE AT CENTRAL PARK PL, *MB: CODE: ADM2 LOC: ON EAST PARK PL.,278' FROM P.L. CENTRAL PARK PL., ****/ | 2019-01-01 | EXCAVATED AND REPAIRED INLET SERVICE LEAK IN TREE ROOTS
201900001401 | 2019-01-02 | LEAD | 733 | ADELE |  | WILK | WM-LEAK ON THE SIDEWALK INLET SERVICE LEAK IN MUDPLOT AT CURB /** 1) MN: A351534 SN: 0176977, *TAP: SIZE: A LOC: 493 FEET FROM P LINE AT LAUREL, *MB: CODE: CD LOC: ON ADELE 131FT FROM ANNUNCATION 8FT OUTSIDE ****/ | 2019-02-02 | ARRIVD ON JOB SITE EXAMINED LEAK IN MUD PLOT EXCAVATED IN MUD PLOT BY HAND MADE REPAIRS ON INLET SERVICE BACKFILLED DRESSED UP WORK SITE
201900001701 | 2019-01-02 | LEAD | 2226 | PAULINE | MIRO | WMTLK | ML: METER LEAK METER# A325456 ACCT# 154822-432575 EXAMINE INLET & OUTLET SERVICE INSIDE METER BOX FOR A LEAK /** 1) MN: A325456 SN: 0091355, *TAP: SIZE: A LOC: 193 FEET FROM P LINE AT MIRO N, *MB: CODE: CDL LOC: 196.5 FROM P.L. N. MIRO 8' OUTSIDE PL ****/ | 2019-01-10 | REPLACED 5/8 INCH HANDWHEEL GUTS IN METER BOX
201900002901 | 2019-01-03 | LEAD | 1431 | ST ANTHONY AV |  | WILK | INSP L UDUEBOR STATES SERVICE HAS A BAD LEAK FROM THE BLEEDER VALVE. PLEASE REPAIR METER A432375 LOC 267032 INLET SERVICE LEAK BAD BLEEDER VALVE LEAK INSIDE METER BOX /** 1) MN: A133239 SN: 0015588, *TAP: SIZE: A LOC: 126 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: BFK1 LOC: 126' P.L. N ROBERTSON ****/ | 2019-01-08 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900003001 | 2019-01-03 | LEAD | 864 | ROOSEVELT PL |  | WMBK | LOCATION: 113553 MTR# A 357228 INSP M. FRAZIER UNABLE TO CHANGE WASHER, INLET TOO FAR APART. BROKEN METER BOX COVER METER BOX EXPANDED UNABLE TO CHANGE WASHER /** 1) MN: A292655 SN: 0029128, *TAP: SIZE: A LOC: 4 FEET FROM P LINE AT ROOSEVELT PL, *MB: CODE: BFZ LOC: ON DUMAINE NEAR CARROLLTON INSIDE OF WALK ****/ | 2019-01-07 | EXCAVATED IN MUD PLOT + REPLACED BROKEN 5/8 INCH METER BOX CASING + 5/8 INCH WASHERS
201900005501 | 2019-01-03 | LEAD | 1932 | LAPEYROUSE | N JOHNSON | WOLK | ML-METER LEAK ACCT#306599-703191 METER#B042380 OUTLET TIE IN. FOUND METER OFF LEFT METER OFF. *****HOUSE UNDER RENOVATIONS***** /** 1) MN: B024224 SN: 0045388, *TAP: SIZE: B LOC: 51 FEET FROM P LINE AT JOHNSON N, *MB: CODE: BFK LOC: 51FT FROM URPL JOHNSON ****/ | 2019-01-07 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED BROKEN 5/8INCH METER BOX BOTTOM + TIED 3/4 INCH OUTLET SERVICE LINE IN TO METER BOX BACKFILLED + DRESSED UP AREA
201900006701 | 2019-01-03 | LEAD | 2008 | BURGUNDY | TOURO | WOLK | ML-METER LEAK METER#A260056 ACCT3101048-529200 OUTLET SERVICE LEAK IN BRICK SIDEWALK CONSTANT REG /** 1) MN: A260056 SN: 0001248, *TAP: SIZE: A LOC: 92 FEET FROM P LINE AT TOURO, *MB: CODE: BEK3 LOC: AT 2012. ON BURGUNDY 92FT FROM PL TOURO ****/ | 2019-01-30 | REMOVED BRICK AND RXCAVATED OVER 6 INCH WATER MAIN AND REPLACED CARBRATION COCK DAMAGED BY ENTERGY GAS LINE RENEWED 3/4 INCH PLASTIC TO METER BOX BACKFILLED AREA. JOB COMPLETE
201900006801 | 2019-01-03 | LEAD | 1801 | N TONTI | HAVANA | WMTLK | ML - METER LEAK MTR # A339790 ACCT # 131006-490137 EXAMINE INLET & OUTLET SERVICE INSIDE METER BOX METER BOX UNDER WATER /** 1) MN: A339790 SN: 0064292, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT TONTI N, *MB: CODE: ADHL LOC: SIDE ST CURB END OF HOUSE ON HAVANA 52' P.L. ****/ | 2019-01-30 | EXCAVATED IN GUTTER BOTTOM +REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900008301 | 2019-01-04 | LEAD | 2806 | N ROCHEBLAVE |  | WILK | INLET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-04 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900010901 | 2019-01-04 | LEAD | 1230 | ESPLANADE AV |  | WILK | LOCATION: 107862 MTR# A 248737 INSP D JOHNSON EXAMINE METER AND FOUND BAD LEAK COMING FROM CURB COCK BEHIND CASING. LEFT WATER OFF, CUSTOMER WAITING ON WATER. INLET SERVICE LEAK /** 1) MN: A248737 SN: 0010157, *TAP: SIZE: A LOC: 38 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: BEHK LOC: SIDE ST ON N RAMPART 88' FROM USPL ESPLANADE AVE ****/ | 2019-01-15 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900011301 | 2019-01-04 | LEAD | 2306 | ST BERNARD AV | N ROCHEBLAVE | WMTLK | MI- LEAK ON SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** 1) MN: A334748 SN: 0049182, *TAP: SIZE: A LOC: 203 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BFN LOC: ON ST. BERNARD AVE.,203' FROM U.R.P.L. NO. ****/ | 2019-01-23 | REPLACED 5/8 INCH WASHERS IN METER BOX
201900013701 | 2019-01-04 | LEAD | 2435 | DUMAINE | N ROCHEBLAVE | WILK | ML- METER LEAK METER #A331272 ACCT #116291-524293 INLET SERVICE LEAK IN SIDEWALK /** 1) MN: A331272 SN: 0021472, *TAP: SIZE: A LOC: 51 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BEN1 LOC: ON DUMAINE 52FT FROM ROCHEBLAVE N ****/ | 2019-01-23 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900014302 | 2019-01-05 | LEAD | 2514 | S DERBIGNY | 2ND | WMTLK | JOB REFERRE TO STAND-BY FOR CUSTOMER OUT OF WATER CUSTOMER AGREE TO WAIT TO TOMORROW FOR WATER 1ST AM /** 1) MN: A260278 SN: 0071868, *TAP: SIZE: B LOC: 145 FEET FROM P LINE AT SECOND, *MB: CODE: BD LOC: UNDER HEDGE COR 2516 ****/ | 2019-01-05 | EXAMINED JOB AT ABOVE LOCATION AND TURNED ON STOP - AND WASTE TO GIVE CUSTOMER WATER
201900014401 | 2019-01-04 | LEAD | 1622 | LOUISA | N CLAIBORNE AV | WILK | ML-METER LEAK CSM DOWN /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ INLET SERVICE LEAKING INTO METER BOX | 2019-01-10 | EXCAVATED IN CI=ONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESS UP AREA
201900017201 | 2019-01-05 | LEAD | 3000 | KANSAS | AMAZON | WMTLK | ML-METER LEAK METER#A334848 ACCT#230052-411572 *****************J.GILLIAM @ 20:17PM*************** EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER, GUTTER AND CUSTOMERS YARD FLOODED, CUSTOMER OUT OF WATER /** 1) MN: A334848 SN: 0139187, *TAP: SIZE: B LOC: 45 FEET FROM P LINE AT AMAZON, *MB: CODE: CDL1 LOC: ON KANSAS 45' FROM PL AMAZON 7' OUTSIDE PL ****/ | 2019-01-05 | EXCAVATED IN MUD PLOT AND MADE REPAIR ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201900017601 | 2019-01-06 | LEAD/PLASTIC | 3232 | JEFFERSON AV | S GALVEZ | WILK | WILK WATER LEAK-INLET SERVICE /** 1) MN: 000000 SN: 0089175, *TAP: SIZE: A LOC: 33 FEET FROM P LINE AT JEFFERSON AVE, *MB: CODE: BDH LOC: SIDE ST 2ND METER - 34' P.L. JEFFERSON AVE ****/ | 2019-01-05 | ARRIVED AT ABOVE LOCATION ,EXCAVTED BY HAND AND MADEE REPAIRS TO STOP LEAK ON 1"CONTROLLING LINE BACKFILLED , CLEANED UP AND WASHED DOWN WORK AREA TO COMPLETE JOB.
201900018101 | 2019-01-06 | LEAD | 4527 | MARK TWAIN DR | STEPHEN GIRARD AV | WILK | ****************PICKUP**************** INLET SERVICE LEAK IN ASPHALT STREET /** 1) MN: A317781 SN: 0113566, *TAP: SIZE: A LOC: 220 FEET FROM P LINE AT STEPHEN GIRARD AVE, *MB: CODE: __ LOC: ON MARK TWAIN DR 220' FROM PL STEPHEN GIRARD AVE 6 ****/ | 2019-01-28 | EXAMINE JOB. EXCAVATED STREET AND FOUND LEAD LEAK. ALSO DUG BY HAND IN MUDPLOT. FOUND TREE ROOTS. EXCAVAGED TREE ROOTS IN MUDPLOT. CONTINED TO DIG BY HAND IN STREET TO EXPOSE LEAK. REPLACING LEAD WITH 15 PVC TO METERBOX. INSTALL METERBOX COMPLETE AND RAISED TO GRADE. REMOVED LEAD FROM METERBOX TO PROPERTY WITH 6FT PVC. BACKFILLED EXCAVATION WITH RIVERSAND AND COALMILL.
201900019501 | 2019-01-07 | LEAD | 2858 | ALLEN |  | WILK | LOCATION: 174160 MTR# A 432392 INSP UDEBOR STATES INLET SERVICE IS LEAKING. PLEASE REPAIR. INLET SERVICE LEAK /** 1) MN: A213631 SN: 0102869, *TAP: SIZE: A LOC: 120 FEET FROM P LINE AT INDUSTRY, *MB: CODE: ADM5 LOC: ON ALLEN 120FT FROM PL INDUSTRY 9' OUTSIDE PL 9' I ****/ | 2019-01-10 | EXCAVATED IN MUD PLOT + REPLACED 5/8 I8NCH CURB COCK BACKFILLED + DRESSED UP AREA
201900019601 | 2019-01-07 | LEAD/PLASTIC | 6240 | DOVER PL |  | WILK | MI LEAK ON THE SIDEWALK CHANGED FROM 6270 DOVER PL INLET SERVICE LEAK IN MUDPLOT /** 1) MN: B019803 SN: 0153911, *TAP: SIZE: B LOC: 341 FEET FROM P LINE AT AURORA DR, *MB: CODE: CE LOC: ON DOVER PL 341' FROM PL AURORA DR 7' OUTSIDE PL ****/ | 2019-01-11 | EXAMINED AREA PUMPED DOWN METER BOX EXCAVTED ON INLET SERVICE OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK BACKFILLED CLEANED AREA ALSO RENEWED OUTLET AND RENEWED LEAD ON OUTLET SERVICE TO PROPERTY
201900019701 | 2019-01-07 | LEAD | 3601 | ST CLAUDE AV |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 114372-430143 METER NUMBER - A334942 INLET SERVICE LEAK IN BOX /** 1) MN: A334942 SN: 0017059, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: AFHM LOC: SIDE ST ON CONGRESS 74' P.L. ST CLAUDE AVE ****/ | 2019-01-11 | EXCAVATED 2 X 2 MUD PLOT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900020101 | 2019-01-07 | LEAD | 6026 | ST ANTHONY AV | ROSARY DR | WILK | ML- METER LEAK MTR # A220636 ACCT # 167107-718417 INLET SERVICE LEAK IN THE MUD PLOT LEAKING FROM BLEEDER VALVE SATURATION THE GRASS. CUSTOMER PARKING ON METER /** 1) MN: A220636 SN: 0108037, *TAP: SIZE: A LOC: 285 FEET FROM P LINE AT BURBANK DR, *MB: CODE: AFLK LOC: ON ST. ANTHONY, 285' FROM P.L. BURBANK DR., 3' OUT ****/ | 2019-01-14 | EXCV 4 X 4 CUT IN MUDPLOT FOUND LEAK INSIDE METER BOX ON BOX COCK CHANGED BOX COCK AND HAND WHEEL RAISED TO GRADE. FOUND LEAD ON INLET/ OUTLET SERVICE LINE BUT DID NOT REMOVE BACKFILLED AND DRESS CUT WITH SAND. (JOB COMPLETE)
201900022601 | 2019-01-07 | LEAD | 431 | ROYAL | ST LOUIS | WILK | ML METER LEAK METER# A409779 INLET SERVICE LEK IN BOX, IN SIDEWALK /** 1) MN: A219116 SN: 0000972, *TAP: SIZE: A LOC: 230 FEET FROM P LINE AT CONTI, *MB: CODE: CEN LOC: ON ROYAL ST 230.5' FROM PL CONTI ** 2) MN: A116021 SN: 0000972, *TAP: SIZE: B LOC: 25 FEET FROM P LINE AT ST LOUIS, *MB: CODE: OOO LOC: ON ROYAL 24FT FROM PL ST LOUIS 9FT OUTSD PL THERE ARE 7 MORE NOT LISTED. ****/ | 2019-02-14 | EXCAVATED 2 X 2 SIDEWALK CUT MADE REPAIR ON OUTLET SERVICE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900024401 | 2019-01-07 | LEAD | 2518 | PAUGER |  | SHRE | PLEASE LOCATE SEWER HOUSE CONNECTION. CUSTOMER UNABLE TO LOCATE WITH THE MEASUREMENTS GIVEN BY SWB. PLEASE CONTACT UPON COMPLETION: 504-473-6878 /** 1) MN: SN: 0056583, *TAP: SIZE: A LOC: 127 FEET FROM P LINE AT ROMAN N, *MB: CODE: BDM LOC: 127FT FROM LSPL N ROMAN ****/ | 2019-02-05 | EXCAVATED IN GUTTER BOTTOM UNABLE TO LOCATE 6 INCH SEWER HOUSE CONNECTION BACKFILLED + CLEANED UP AREA
201900025001 | 2019-01-07 | LEAD/PLASTIC | 423 | PACIFIC AV | ALIX | WMTLK | ML-METER LEAK ACCT#224215-401877 METER#A351833 EXAMINE INLET AND OUTLET SERVICE FOR LEAK INSIDE BOX, FLOODING SIDEWALK /** 1) MN: A285646 SN: 0018325, *TAP: SIZE: A LOC: 178 FEET FROM P LINE AT ALIX, *MB: CODE: CEL LOC: ON PACIFIC AVE., 178' FROM U.S.P.L. ALIX ****/ | 2019-01-23 | EXAMINED AREA PUMPED DOWN WATER BROKE OUT BRICK EXCAVATED ON INLET SERVICE OBSERVED LEAK ON INLET SERVICE REPAIRED LEAK LEAD ON INLET NEED TO BE REMOVED TO MAIN BACKFILLED CLEANED AREA LEFT CONE ON SITE NEED SAND COALMILL TO COMPLETE DRESS UP
201900025201 | 2019-01-07 | LEAD | 5616 | DAUPHINE |  | WMBK | UNABLE TO CHANGE METER. INSP J DESSELLE STATES THE CASING IS OBSTRUCTING THE WHEEL. PLEASE REPAIR AND CHANGE METER A361053 LOC 140704 BROKEN METER BOX CASING SHIFTED OVER HANDWHEEL, CUSTOMER HAS WATER /** 1) MN: A297635 SN: 0071328, *TAP: SIZE: A LOC: 170 FEET FROM P LINE AT CAFFIN AVE, *MB: CODE: CDL LOC: ON DAUPHINE 160' FROM PL OF CAFFIN AVE ****/ | 2019-01-09 | EXCAVATED 2 X 1 MUD PLOT ALIGNED METER BOX WITH METER BOTTOM AND REPLACED METER BACKFILLED AND CLEANED THE AREA *************OLD METER INFO********** METER:A361053 FAC:70508762 MAKE:SENSUS READ:0
201900026502 | 2019-01-07 | LEAD | 2629 | DEERS |  | WILK | MAKE REPAIRS ON LEAK HOUSE OUT OF WATER FRIST AM PR H RICHARD /** 1) MN: A157985 SN: 0097163, *TAP: SIZE: B LOC: 241 FEET FROM P LINE AT LAW, *MB: CODE: CDN1 LOC: ON DEERS 241FT FROM PL OF LAW 8FT OUTSIDE PL 3FT ****/ | 2019-01-08 | ARRIVED AT ABOVE LOCATION + FOUND CONTRATOR MAKING REPAIR CONTRACTOR DID NOT COMPLETE REPAIR MADE REPAIR IN METER BOX RESTOTING WATER BACK TO ABOVE LOCATION CUSTOMER HAS PROBLEM ON PROPERTY REFER TO PROPERTY OWNER FOR REPAIRS
201900026901 | 2019-01-07 | LEAD | 4205 | BURGUNDY | FRANCE | WILK | ML-METER LEAK ACCT# 138407-701475 METER# A121437 INLET SERVICE LEAK IN SIDEWALK, SIGNS OF PREVIOUS REPAIRS /** 1) MN: A121437 SN: 0068972, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT FRANCE, *MB: CODE: BDE LOC: ON BURGUNDY 47FT FROM PL FRANCE ****/ | 2019-01-14 | EXCAVATED IN EXISTING 4 X 4 SIDEWALK CUT AND REPLACED COCK AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201900028101 | 2019-01-08 | LEAD | 701 | CONGRESS |  | WILK | LOCATION ID-127295 MTR-A155026 MTR LEAKING AT CURB COCK /** 1) MN: A155026 SN: 0149573, *TAP: SIZE: A LOC: 50 FEET FROM P LINE AT CONGRESS, *MB: CODE: BEHO LOC: SIDE ST ON ROYAL ST 52' P.L. CONGRESS ****/ | 2019-01-11 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900029301 | 2019-01-08 | LEAD | 4214 | LOYOLA AV |  | WILK | ML--METER LEAK ACCOUNT#109670-533349 METER#A227204 INLET SERVICE LEAK IN GRASS FLOODING SIDEWALK AND GRASS /** 1) MN: A227204 SN: 0010929, *TAP: SIZE: B LOC: 93 FEET FROM P LINE AT MILAN, *MB: CODE: CFM1 LOC: IN GARDEN 92' P.L. MILAN ****/ DOTTIE READY 3/19/19 EXP 4/8/19 | 2019-03-27 | ARRIVED AT THE LOCATION MADE A 5 X 5 MUDPLOT CUT AROUND THE METER BOX ,MADE REPAIR ON INLET AND OUTLET ALSO RAISED TO GRADE. THEN BACKFILLED AND CLEANED AREA.
201900030601 | 2019-01-08 | LEAD | 1311 | FLOOD |  | WMTLK | LOCATIONID#143875-423357 METER#A398032 LEAK INSIDE METERBOX /** 1) MN: A226086 SN: 0089610, *TAP: SIZE: A LOC: 86 FEET FROM P LINE AT URQUHART, *MB: CODE: DL7 LOC: ON FLOOD 86' FROM PL OF URQUHART ****/ | 2019-01-18 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND
201900031101 | 2019-01-08 | LEAD | 2040 | PIETY | N GALVEZ | WMTLK | LOCATIONID#144551-433317 METER#B034546 LEAK INSIDE METERBOX /** 1) MN: B033178 SN: 0083951, *TAP: SIZE: B LOC: 37 FEET FROM P LINE AT GALVEZ N, *MB: CODE: BD4 LOC: METER ON PIETY 36.6 FT FROM PL N GALVEZ ****/ | 2019-01-14 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 3/4 INCH CURB COCK AND METER INSIDE METER BOX BACKFILLED AREA OLD METER INFO: B034546 FACT: 70698225 MAKE: SENUS READ: 118
201900031201 | 2019-01-08 | LEAD | 6011 | CHARTRES |  | WMTLK | LOCATIONID#165940-426026 METER#A404870 LEAK INSIDE METERBOX /** 1) MN: A249905 SN: 0106299, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT GORDON, *MB: CODE: CFL7 LOC: ON CHARTRES, 55' FROM P.L. GORDON, 1.5' OUTSIDE ****/ | 2019-01-18 | EXCAVATED AND MADE REPAIRS ON INLET SERVICE I MUD PLOT BACKFILLED JOB WITH RIVERSAND
201900033901 | 2019-01-08 | LEAD | 1545 | 6TH | ST CHARLES AV | WMTLK | WM-LEAK IN THE STREET EXAMINE INLET & OUTLET SERVICE FOR A LEAK IN THE SIDEWALK METER UNDER WATER FLOODING SIDEWALK /** 1) MN: A196114 SN: 0072638, *TAP: SIZE: A LOC: 88 FEET FROM P LINE AT ST CHARLES AVE, *MB: CODE: FM3 LOC: ON SIXTH 80FT FROM LRPL OF ST CHARLES AVE ****/ DOTTIE READY 1-15-19 EXP 2-4-19 | 2019-01-19 | REPLACED 5/8 CURB COCK TIED INTO LEAD.(SOC 3FT. X 3 FT .S/W)
201900034001 | 2019-01-08 | LEAD | 2109 | ST ANTHONY | N GALVEZ | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A335002 SN: 0053127, *TAP: SIZE: A LOC: 78 FEET FROM P LINE AT GALVEZ N, *MB: CODE: CD LOC: ON ST. ANTHONY,90.5' FROM L.S.P.L. NO. GALVEZ ****/ | 2019-01-22 | EXCAVATED 3 X 2 MUD PLOT REPLACED 5/8 INCH COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900034401 | 2019-01-08 | LEAD | 2715 | ST ANTHONY | HOPE | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A210774 SN: 0111439, *TAP: SIZE: A LOC: 115 FEET FROM P LINE AT HOPE, *MB: CODE: CDL LOC: 115FT FROM PL HOPE 7' OUTSIDE PL ****/ | 2019-01-22 | EXCAVATED 3 X 2 MUD PLOT REPLACED 5/8 INCH METER BOX COCK BACKFILLED AND CLEANED THE AREA
201900034601 | 2019-01-08 | LEAD | 2320 | ST ANTHONY | N TONTI | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. ***LEAK IS LOCATED IN FRONT OF OVERGROWN LOT*** /** 1) MN: SN: 0099629, *TAP: SIZE: B LOC: 133 FEET FROM P LINE AT TONTI N, *MB: CODE: AE LOC: ON ST. ANTHONY, 133' FROM P.L. NO. TONTI, 2' OUT- ****/ | 2019-01-22 | EXCAVATED 4 X 3 SIDEWALK CUT MADE REPAIRS ON INLET SERVICE AND REPLACED 5/8 INCH COCK BACKFILLED AND CLEANED THE AREA JOB COMPLETE
201900034901 | 2019-01-08 | LEAD | 1800 | N GALVEZ | NEW ORLEANS | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A276749 SN: 0163800, *TAP: SIZE: B LOC: 32 FEET FROM P LINE AT NEW ORLEANS, *MB: CODE: __ LOC: ON N GALVEZ 19FT FROM PL NEW ORLEANS 8FT OUTSD ****/ | 2019-01-24 | EXCAVATED 3 X 2 GUTTER BOTTOM REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA JOB COMPLETE
201900035101 | 2019-01-08 | LEAD | 1337 | CLOUET | N VILLERE | WMLK | WATER LEAK -MAIN. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-16 | MADE 8 X 8 CUT IN BLACK TOP STREET AND MADE REPAIR ON 5/8 INCH TAILPIECE ON 12 INCH WATER MAIN FOR ABANDON LOT BACKFILLED AREA JOB COMPLETE
201900035201 | 2019-01-08 | LEAD | 1318 | FRANCE | URQUHART | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A142465 SN: 0162244, *TAP: SIZE: B LOC: 186 FEET FROM P LINE AT URQUHART, *MB: CODE: CDN1 LOC: ON FRANCE 186'FROM P.L. URQUHART 6'OUTSIDE P.L. ****/ | 2019-01-16 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 INCH INLET SERVICE FOR ABANDON HOUSE BACKFILLED AREA JOB COMPLETE
201900035301 | 2019-01-08 | LEAD | 1852 | BURGUNDY | PAUGER | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: B029517 SN: 0050543, *TAP: SIZE: B LOC: 126 FEET FROM P LINE AT BOURBON, *MB: CODE: BFL LOC: ON BURGUNDY 1226FT FROM BOURBON ****/ | 2019-01-22 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 3/4 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900038101 | 2019-01-09 | LEAD | 2025 | N ROCHEBLAVE | ST ANTHONY | WMTLK | WM-LEAK IN SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR LEAK INSIDE BOX /** 1) MN: A261286 SN: 0073263, *TAP: SIZE: B LOC: 207 FEET FROM P LINE AT ALLEN, *MB: CODE: CD LOC: ON NO. ROCHEBLAVE, 207' FROM P.L. ALLEN ****/ | 2019-01-24 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900038201 | 2019-01-09 | LEAD | 1641 | N GALVEZ |  | WILK | LOCATION: 122996 MTR# A 432878 INSP L UDEBOR STATES OUTLET SERVICE LEAKING BEHIND WHEEL. PLEASE REPAIR. INLET SERVICE LEAK IN MUDPLOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-25 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH HANDWHEEL BACKFILLED + DRESSED UP AREA
201900038801 | 2019-01-09 | LEAD | 913 | N ROBERTSON |  | WMRE | INSP D JOHNSON STATES SERVICE IS BELOW GRADE. PLEASE RAISE TO GRADE AND SET 5/8 METER. LOC 306688 ***************B LEAVE IN SYSTEM**************** LOCATE, MARK, RAISE TO GRADE, SET 5/8 METER ALSO RENEW OUTLET SERVICE, CUSTOMER WAITING ON WATER, CUSTOMER WILL BE MOVING IN SOON /** 1) MN: 000000 SN: 0050040, *TAP: SIZE: A LOC: 87 FEET FROM P LINE AT DUMAINE, *MB: CODE: AFOK LOC: ON N ROBERTSON 87FT DUMAINE IN ALLEY ****/ | 2019-01-18 | LOCATED METER WITH MEASUREMENT GIVEN BURIED UNDER OLD SIDEWALK COVERED WITH GRESS RXCAVATED 4 X 3 CUT AND METER BOX UP TO GRADE ALSO LEFT WHIP OUT FOR CUSTOMER TO TIE INTO BACKFILLED AND CLEANED THE AREA (PET***) ********RESET DONE BY D. SMOTHERS, METER SHOP***
201900039101 | 2019-01-09 | LEAD | 2558 | N ROCHEBLAVE |  | WMRE | INSP L UDUEBOR STATES SERVICE IS BURIED UNDER ROCKS. PLEASE RAISE TO GRADE AND CHANGE METER A431044 LOC 140040 LOCATE, RAISE TO GRADE, MARK AND CHANGE METER /** 1) MN: A222961 SN: 0143468, *TAP: SIZE: A LOC: 108 FEET FROM P LINE AT MUSIC, *MB: CODE: CDL1 LOC: 107FT FROM URPL MUSIC ON N ROCHEBLAVE ****/ | 2019-01-24 | LOCATED METER AT ABOVE LOCATION REPLACED 5/8 INCH METER + MARKED WITH BLUE PAINT ************OLD METER INFO************** METER:A431044 FAC:16356633 MAKE:HERSEY READ:250
201900039301 | 2019-01-09 | LEAD | 2327 | PAULINE | N ROCHEBLAVE | WMTLK | ML METER LEAK METER# A141415 EXAMINE INLET AND OUTLET SERVICE FOR LEAK INSIDE BOX /** 1) MN: A343592 SN: 0095139, *TAP: SIZE: A LOC: 198 FEET FROM P LINE AT NO. TONTI, *MB: CODE: AD LOC: ON PAULINE, 196.5' FROM P.L. NO. TONTI, 8' OUTSIDE ****/ | 2019-01-19 | EXCVATED IN MUD PLOT THROUGH HEAVY TREE ROOTS + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900041001 | 2019-01-09 | LEAD | 2214 | TOURO | N MIRO | WILK | ML METER LEAK METER# A432463 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A181254 SN: 0071531, *TAP: SIZE: A LOC: 108 FEET FROM P LINE AT MIRO N, *MB: CODE: CDKM LOC: ON TOURO 107FT FROM USPL N MIRO ****/ | 2019-01-24 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA ALSO REPLACED DAMAGED 5/8 INCH WATER METER OLD METER INFO: A432463 FACT: 18137502 MAKE: HERSEY READ:100
201900041101 | 2019-01-09 | LEAD | 936 | LAMANCHE | N RAMPART | WOLK | MI- INSPECTOR FOUND CONS ON METER MTR#A253095 ACCT#145731-425453 /** 1) MN: A238776 SN: 0077496, *TAP: SIZE: A LOC: 46 FEET FROM P LINE AT LAMANCHE, *MB: CODE: CE LOC: ON SIDE BY POST - ON N RAMPART 46' P.L. LAMANCHE ****/ | 2019-01-18 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILLED WITH RIVERSAND
201900041301 | 2019-01-09 | LEAD/PLASTIC | 4529 | MAGAZINE | CADIZ | WILK | ML-METER LEAK ACCT# 111057-565614 METER # A428222 EXAMINE INLET SERVICE IN THE SIDEWALK /** 1) MN: A272563 SN: 0026207, *TAP: SIZE: B LOC: 74 FEET FROM P LINE AT CADIZ, *MB: CODE: CDL LOC: ON MAGAZINE 74FT FROM CADIZ ****/ DOTTIE READY 3/19/19 | 2019-05-11 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 5/8 HAND-WHEEL LEAKING ALSO 5/8 CURB COCK LEAKOING.REPLACED HANDWHEEL AND 5/8 CURB COCK TIED INTO LEAD.(SOC 4FT .X 4 FT.S/W)
201900041601 | 2019-01-09 | LEAD | 524 | ST LOUIS |  | WILK | WM-LEAK ON THE SIDEWALK INLET SERVICE LEAK IN BOX, GETTING INTO STORM DRAIN /** 1) MN: D002972 SN: 0004020, *TAP: SIZE: D LOC: 188 FEET FROM P LINE AT DECATUR, *MB: CODE: AEL1 LOC: 186FT FROM PL DECATUR IN MH ON ST LOUIS ** 2) MN: SN: 0000000, *TAP: SIZE: __ LOC: 158 FEET FROM P LINE AT CHARTRES, *MB: CODE: __ LOC: ****/ | 2019-01-15 | EXAMINE JOB + FOUND MTER COCK HALF WAY OFF TURNE METER COCK OFF TO STOP LEAK NO METER AT THIS LOCATION
201900042201 | 2019-01-09 | LEAD | 5630 | ROYAL | LAMANCHE | WILK | ML- METER LEAK METER #A245314 ACCT # 166024-425565 INLET LEAK INSIDE METER BOX (C) /** 1) MN: A245314 SN: 0106369, *TAP: SIZE: A LOC: 24 FEET FROM P LINE AT ROYAL, *MB: CODE: BEH LOC: ON LAMANCHE 24FT FROM PL ROYAL 6' OUTSIDE ****/ | 2019-01-25 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND
201900047201 | 2019-01-10 | LEAD | 2225 | ST BERNARD AV | N TONTI | WILK | WM LEAK IN STREET INLET SERVICE LEAK IN LARGE TREE ROOTS 01/11/19 LEAK HAS GOTTEN WORSE FLOWING FROM 2225 ST BERNARD AV TO 2233 ST BERNARD AV, PER INSPC C KENT (AJR) /** 1) MN: A214750 SN: 0074747, *TAP: SIZE: A LOC: 185 FEET FROM P LINE AT MIRO N, *MB: CODE: BD LOC: ON ST BERNARD 184' FROM PL OF MIRO N ****/ | 2019-01-19 | EXCAVATED IN LARGE TREE ROOTS AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201900047501 | 2019-01-10 | LEAD | 3631 | CLIO | S ROCHEBLAVE | WILK | INSP S BIBBINS STATES HE CANNOT CHANGE METER OR FIX LEAK BECAUSE CASING IS OBSTRUCTING WHEEL. CAN'T REMOVE METER TO CHANGE WASHERS. PLEASE REPAIR AS SOON AS POSSIBLE. METER A381513 LOC 222026 INLET SEVICE LEAK COMING FROM CURB COCK, ALSO SET METER BOX CASING /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ DOTTIE READY 3/26/19 EXP 4/15/19 | 2019-03-31 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK AND METER BOX CASING BACKFILLED AREA
201900047601 | 2019-01-10 | LEAD | 1410 | DAUPHINE | ESPLANADE AV | WOLK | ML-METER LEAK ACCT#124963-485538 METER#A417735 OUTLET SERVICE LEAK BEHIND HANDWHEEL, CON REG /** 1) MN: A197408 SN: 0047126, *TAP: SIZE: A LOC: 65 FEET FROM P LINE AT ESPLANADE, *MB: CODE: CDL LOC: ON DAUPHINE 65' FROM LRPL ESPLANADE AVE ****/ | 2019-01-24 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED HANDWHEEL TO STOP CONSTANT REGISTRATION BACKFILLED AND CLEANED THE AREA
201900048501 | 2019-01-10 | LEAD | 1729 | TERPSICHORE | BARONNE | WILK | ML: METER LEAK ACCT#100595-549700 MTR# A400454 BAD BLEEDER VALVE /** 1) MN: A328754 SN: 0003721, *TAP: SIZE: B LOC: 1788 FEET FROM P LINE AT BARONNE, *MB: CODE: BFKL LOC: ON TERPSICHORE 178.8' FROM BARONNE,2' INSIDE P.L. ****/ | 2019-01-19 | REPLACED 5/8 CURBCOCK TIED INTO LEAD.(SOC 3FT. X 3 FT .S/W)
201900048801 | 2019-01-10 | LEAD | 1222 | ST FERDINAND | URQUHART | WILK | ML- METER LEAK **ACCT#128065-479800**METER# INLET SERVICE LEAK IN BOX, CARS PARKING ON METER /** 1) MN: A283392 SN: 0056020, *TAP: SIZE: A LOC: 173 FEET FROM P LINE AT URQUHART, *MB: CODE: __ LOC: ON ST. FERDINAND,174.6' FROM U.S.P.L. URQUHART ****/ | 2019-01-25 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND
201900050901 | 2019-01-10 | LEAD | 2027 | FELICIANA | N GALVEZ | WMTLK | ML- METER LEAK METER #A393825 ACCT # 163057-591580 ** FLOODING AREA ** EXAMINE INLET AND OUTLET SERVICE FOR LEAK, METER UNDER WATER /** 1) MN: 000000 SN: 0102401, *TAP: SIZE: A LOC: 131 FEET FROM P LINE AT GALVEZ N, *MB: CODE: ADK LOC: ON FELICIANA, 131' FROM P.L. NO. GALVEZ, 7' OUT- ****/ | 2019-01-28 | MADE 4 X 6 CUT IN BLACK TOP STREET AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201900051001 | 2019-01-10 | LEAD | 4131 | N RAMPART | FRANCE | WOLK | MI- LEAK IN THE SIDEWALK EXAMINE OUTLET SERVICE FOR LEAK @ PROPERTY LINE, CON R EG /** 1) MN: 000000 SN: 0010019, *TAP: SIZE: B LOC: 60 FEET FROM P LINE AT RAMPART N, *MB: CODE: BEH LOC: ON SIDE ST ON FRANCE ST 60' P.L. N RAMPART ****/ | 2019-01-30 | EXCAVATED 3 X 2 SIDEWALK MADE REPAIR ON OUTLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201900052601 | 2019-01-10 | LEAD | 1224 | N VILLERE | GOV NICHOLLS | WILK | WM-LEAK ON THE SIDEWALK INLET SERVICE LEAK IN THE SIDEWALK LEAKING FROM CURB COCK. ***NO METER IN BOX*** /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-17 | EXCAVATED AND MADE REPIAR ON ABANDON 5/8 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND COLDMILL
201900053301 | 2019-01-10 | LEAD | 800 | ANDRY | DAUPHINE | WILK | WM-LEAK IN THE STREET /** 1) MN: B028985 SN: 0121500, *TAP: SIZE: B LOC: 18 FEET FROM P LINE AT ANDRY, *MB: CODE: BDH7 LOC: ON DAUPHINE ST 16' FROM UPL ANDRY ****/ INLET LEAK IN THE MUD PLOT. | 2019-02-12 | MADE 4 X 4 CUT IN BLACK TOP STRET IN HEAVY RAIN AND MADE REPAIRS ON 3/4 INCH PLASTIC INLET SERVICE BACKFILLED AREA
201900053901 | 2019-01-11 | LEAD | 9330 | OLD GENTILLY RD |  | WILK | /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-10 | PLACED 3/4 STOP COCK ON 3/4 LEAD SERVICE. ABANDONED SERVICES. JOB COMPLETE
201900054601 | 2019-01-11 | LEAD | 1819 | ESPLANADE AV | N PRIEUR | WOLK | MI-INSPECTOR FOUND CONS ON METER MTR#E008286 ACCT#223092-487969 /** 1) MN: C019694 SN: 0061476, *TAP: SIZE: D LOC: 170 FEET FROM P LINE AT ROMAN N, *MB: CODE: AE2 LOC: ON ESPLANADE 170FT FROM PL ROMAN ****/ | 2019-01-29 | REPLACED CNI AND UNION TO STOP LEAK
201900054701 | 2019-01-11 | LEAD | 5227 | DAUPHINE |  | WMTLK | LOCATIONID#106217-424771 METER#B034290 LEAK INSIDE METERBOX /** 1) MN: B025941 SN: 0020647, *TAP: SIZE: A LOC: 65 FEET FROM P LINE AT DAUPHINE, *MB: CODE: CEH4 LOC: SIDE ST ON EGANIA 65' FROM USP LINE DAUPHINE ****/ | 2019-02-01 | EXCAVTED IN CONCRETE SIDEWALK + REPLACED 3/4 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900054801 | 2019-01-11 | LEAD | 717 | INDEPENDENCE |  | WOLK | LOCATIONID#145566-428118 METER#A268787 LEAK INSIDE METERBOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-30 | REPLACED 5/8 HANDWHEEL + GUTS IN METER BOX
201900055501 | 2019-01-11 | LEAD | 2500 | D"ABADIE |  | WOLK | INSP L UDUEBOR STATES HE IS UNABLE TO SET METER. INLET AND OUTLET TOO CLOSE. PLEASE REPAIR AND SET 5/8 METER. LOC 306678 BROKEN HANDWHEEL NOT LINING UP ALSO RENEW SERVICE AND SET 5/8 METER, HOUSE UNDER RENOVATION /** 1) MN: A153550 SN: 0043263, *TAP: SIZE: A LOC: 60 FEET FROM P LINE AT D'ABADIE, *MB: CODE: ADHM LOC: ON N DORGNEOIS ST 58.5' FROM USPL D'ABADIE ****/ | 2019-01-28 | EXCAVATED IN MUD PLOT + REPLACED BROKEN 5/8 INCH METER BOX BOTTOM + ALSO SET 5/8 INCH WATER METER BACKFILLED + DRESSED UP AREA
201900056201 | 2019-01-11 | LEAD | 1338 | GALLIER |  | WOLK | INSP L UDUEBOR STATES SERVICE IS LEAKING FROM BEHIND THE CURB COCK. PLEASE REPAIR AND CHANGE METER A426715 LOC 128264 OUTLET SERVICE LEAK INSIDE BO, CON REG ALSO CHANGE METER /** 1) MN: A125585 SN: 0055245, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT VILLERE N, *MB: CODE: CDK4 LOC: IN WLKWAY CURB 47'FROM N VILLERE ****/ | 2019-01-30 | EXCAVATED 2 X 2 MUD PLOT REPLACED HANDWHEEL TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900056401 | 2019-01-11 | LEAD | 2415 | LAMANCHE | ROCHEBLAVE | WILK | ML: METER LEAK ACCT#207923-421693 MTR# A393737 INLET SERVICE LEAK INSIDE BOX IN MUDPLOT /** 1) MN: A325137 SN: 0168731, *TAP: SIZE: B LOC: 5 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: OOOO LOC: ON LAMANCHE 4FT FROM PL N ROCHEBLAVE 4FT OUTSD ****/ | 2019-01-25 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND
201900058001 | 2019-01-11 | LEAD | 1910 | FRANCE | N PRIEUR | WILK | ***********************PICKUP******************* INLET SERVICE LEAK IN ASPHALT STREET, FLOODING STREET /** 1) MN: A289986 SN: 0111472, *TAP: SIZE: A LOC: 77 FEET FROM P LINE AT PRIEUR N, *MB: CODE: CDL6 LOC: 77'FROM P L N PRIEUR 7' OUTSIDE PL ****/ | 2019-01-19 | MADE 8 X 8 CUT IN BLACK TOP STREET AND MADE REPAIRS ON 2 INCH SERVICE FOR ABANDON BUILDING BACKFILLED AREA JOB COMPLETE
201900060001 | 2019-01-11 | LEAD | 4905 | DAUPHINE | DESLONDE | WILK | ML: METER LEAK, MTR # B042752, ACCOUNT # 175533-716790 INLET SERVICE LEAK IN MUDPLOT, FLOODING AREA /** 1) MN: B032486 SN: 0088862, *TAP: SIZE: B LOC: 62 FEET FROM P LINE AT DESLONDE, *MB: CODE: CEHK LOC: ON DAUPHINE 62FT FROM PL DESLONDE 7FT OUTSD PL ****/ | 2019-01-25 | EXCAVATED AND MADE REPIAR ON 5/8 INCH INLET SERVICE BACKFILLD JOB WITH RIVERSAND
201900061501 | 2019-01-11 | LEAD | 1905 | URSULINES AV | N ROMAN | WILK | WM- LEAK INTHE SIDEWALK INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A333715 SN: 0045826, *TAP: SIZE: A LOC: 50 FEET FROM P LINE AT ROMAN N, *MB: CODE: ADM4 LOC: METER ON URSULINES AVE 50 FT FROM PL N ROMAN ****/ | 2019-01-17 | EXCAVATED AND MADE REPAIR ON 5/8 INCH INLET SERVICE BACKFILLED WITH RIVERSAND
201900061601 | 2019-01-11 | LEAD | 2800 | CONTI |  | WMRE | LOCATION: 306770 INSP M. FRAZIER STATES METER BOX IS BELOW GRADE. PLEASE LOCATE AND SET A 5/8 METER. NEW CONSTRUCTION LOCATE, RAISE RO GRADE AND SET 5/8 METER /** 1) MN: A312707 SN: 0024549, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT CONTI, *MB: CODE: AFHN LOC: 64FT FROM USPL CONTI SIDE ST ON N WHITE NEAR FENCE ****/ | 2019-01-23 | EXCAVATED 3 X 2 MUD P-LOT WITH MEASUREMENT GIVEN + FOUND METER BOX UPGRADE SET 5/8 INCH METER AND LEFT WHIP OUT FOR CUSTOMER TO TIE INTO BACKFILLED AND CLEANED THE AREA
201900061701 | 2019-01-11 | LEAD | 2626 | GOV NICHOLLS | N DORGENOIS | WILK | ML- METER LEAK METER# A241894 ACCT# 104572-523622 INLET SERVICE LEAK IN SIDEWALK /** 1) MN: A241894 SN: 0002732, *TAP: SIZE: B LOC: 276 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CE LOC: ****/ | 2019-01-25 | EXCAVATED IN PREVIOUS CUT + MADE REPAIRS ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201900061901 | 2019-01-11 | LEAD | 2654 | URSULINES AV | N DORGENOIS | WILK | ML-METER LEAK METER#A400579 ACCT#183402-524002 BAD BLEEDER VALVE LEAKING IN SIDEWALK /** 1) MN: A336415 SN: 0010217, *TAP: SIZE: A LOC: 434 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: FM LOC: MTR ON URSULINES 436FT FRM PL N DORGENOIS 5FT OUT- ****/ | 2019-01-23 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK + RAISED 5/8 INCH METER BOX BOTTON TO GRADE BAKFILLED + DRESSED UP AREA
201900062101 | 2019-01-11 | LEAD | 1671 | PAUL MORPHY | ONZAGA | WILK | ML-METER LEAK ACCT#140111-479041 MTR# A422197 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A209438 SN: 0073141, *TAP: SIZE: A LOC: 213 FEET FROM P LINE AT ONZAGA, *MB: CODE: CDLM LOC: 213FT FROM PL ONZAGA 2FT FROM CURB ****/ | 2019-01-25 | EXCVATED IN MUD PLOT + REPLACED 5/8 INCH HANDWHEEL BACKFILLED + DRESSED UP AREA
201900062501 | 2019-01-11 | LEAD/PLASTIC | 900 | VALLETTE |  | WMTLK | ML-METER LEAK ACCT#224400-401059 MTR#A426781 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER BOX UNDER WATER & HOLE IS EXPOSED 01/17/19 PER S/R 12864155 CHANGE LEAD WHIP (KSW) /** 1) MN: A234387 SN: 0035949, *TAP: SIZE: A LOC: 74 FEET FROM P LINE AT VALLETTE, *MB: CODE: AF LOC: ON HOMER 74' FROM LSPL VALLETTE RES ****/ | 2019-02-01 | WE ARRIVED AND EXAM AND FOUND TWO LEAKS ONE ON THE BOX COCK AND ONE ON THE STOP AN WASTE ON THE HOME OWNER ALSO WHEN WE EXAM THE JOB THE OUTLET DAG OUT I DID SEND A VIDEO TO MY SUP S SLACK WAHT I FOUND WE DID MADE THE REPAIRS TO THE BOX COCK BY CUTTING OUT THE SIDEWALK
201900062601 | 2019-01-11 | LEAD | 2227 | N PRIEUR | ELYSIAN FIELDS AV | WILK | ML METER LEAK MTR#A354563 LOC#140362 INLET SERVICE LEAK INSIDE BOX /** 1) MN: A118991 SN: 0068414, *TAP: SIZE: A LOC: 202 FEET FROM P LINE AT ELYSIAN FIELDS, *MB: CODE: AD LOC: ON N PRIEUR 202' FROM PL OF ELYSIAN FIELDS ****/ | 2019-01-24 | REPLACED WASHERS TO STOP LEAK
201900063301 | 2019-01-12 | LEAD | 1208 | DESIRE | MARAIS | WILK | MI- LEAK ON THE SIDEWALK ***CHANGED FROM 1204 DESIRE** INLET IN THE METER BOX. /** 1) MN: A327633 SN: 0049401, *TAP: SIZE: A LOC: 55 FEET FROM P LINE AT MARAIS, *MB: CODE: ADM5 LOC: ON DESIRE 56FT FROM PL OF MARAIS ****/ | 2019-01-28 | EXCAVATED 8 X 6 STREET CUT MADE REPAIRS ON INLET SERCVICE LINE THE STREET BACKFILLED AND CLEANED THE AREA JOB COMPLETE
201900063701 | 2019-01-12 | LEAD | 947 | PICHELOUP PL | DELGADO DR | WMLK | MI- LEAK IN THE STREET LEAK ON THE MAIN IN THE STREET... GETTING OFF IN DCB (C) /** 1) MN: A282045 SN: 0069976, *TAP: SIZE: A LOC: 378 FEET FROM P LINE AT DUMAINE, *MB: CODE: D LOC: 377FT FROM LSPL DUMAINE ****/ | 2019-01-29 | EXCAVATED 8 X 6 STREET CUT MADE REPAIRS ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201900064101 | 2019-01-12 | LEAD | 2436 | N MIRO | SPAIN | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-20 | EXAMINED JOB FIND NO EAK AT ADDRESS JOB COMPLETE
201900064501 | 2019-01-12 | LEAD | 1417 | GOV NICHOLLS | N VILLERE | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A127963 SN: 0005958, *TAP: SIZE: CC LOC: 172 FEET FROM P LINE AT MARAIS, *MB: CODE: BDLM LOC: XXX IN BOARD FENCE GUTTER EDGE 127' P.L. N VILLERE ** 2) MN: A326893 SN: 0005958, *TAP: SIZE: CC LOC: 119 FEET FROM P LINE AT MARAIS, *MB: CODE: BDLM LOC: ON GOV. NICHOLLS, 120' FROM P.L. MARAIS, 10' OUT- ****/ | 2019-01-30 | REPLACED 2 INCH UNION IN MANHOLE ON OUTLET SIDE AT ABOVE LOCATION
201900065001 | 2019-01-12 | LEAD | 1503 | TOURO | N ROBERTSON | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-11 | EXCAVATED AND MADE REPAIRS ON ABANDON 5/8 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND JOB COMPLETE
201900067201 | 2019-01-14 | LEAD | 3618 | N VILLERE |  | WMTLK | LOCATION ID-184578 MTR-A396155 UNDERGROUND LEAK AROUND MTR/AREA FLOODED /** 1) MN: A321688 SN: 0137662, *TAP: SIZE: A LOC: 57 FEET FROM P LINE AT VILLERE N, *MB: CODE: ADHO LOC: ON INDEPENDENCE 57' P/L NO VILLERE 7' OUTSIDE ** 2) MN: A250733 SN: 0137662, *TAP: SIZE: A LOC: 57 FEET FROM P LINE AT VILLERE N, *MB: CODE: ADHO LOC: ON INDEPENDENCE 58' P/L NO VILLERE 2ND METER THERE ARE 2 MORE NOT LISTED. ****/ | 2019-01-30 | EXCAVATED 3 X 3 MUD PLOT REPLACE METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900067801 | 2019-01-14 | LEAD | 1932 | LAPEYROUSE |  | WMRE | WM - LEAK ON THE SIDEWALK METER IS TURNED OFF LOCATE METER, BRING TO GRADE, ALSO EXAMINE INLET SERVICE. *****HOUSE UNDER RENOVATIONS***** /** 1) MN: B024224 SN: 0045388, *TAP: SIZE: B LOC: 51 FEET FROM P LINE AT JOHNSON N, *MB: CODE: BFK LOC: 51FT FROM URPL JOHNSON ****/ | 2019-01-28 | EXCAVATED IN PREVIOUS CUT + RAISED 5/8 INCH METER BOX BOTTOM TO GRADE BACKFILLED + DRESSED UP AREA
201900069401 | 2019-01-14 | LEAD | 912 | 3RD | CONSTANCE | WILK | WM-LEAK BEWTWEEN SIDEWALK AND STREET INLET SERVICE LEAK IN GRASS FLOODING GRASSY AREA /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-02 | ARRIVED ON JOB SITE EXAMINED AREA FOR LEAK FOUND NO LEAK
201900073101 | 2019-01-14 | LEAD | 2853 | RAMSEY DR | HUDSON PL | WILK | WM: LEAK BETWEEN THE SIDEWALK AND THE STREET LOCATED ON THE HUDSON PL EXAMINE INLET SERVICE LEAK /** 1) MN: C008963 SN: 0134253, *TAP: SIZE: C LOC: 61 FEET FROM P LINE AT RAMSEY DR, *MB: CODE: AL LOC: ON HUDSON, 59' FROM P.L. RAMSEY DR., 7' OUTSIDE, ****/ | 2019-02-02 | EXAMINED AREA EXCVATED ON INLET SERVICE REPAIRED LEAK ON INLET SERVICE BACKFILLED CLEANED AREA
201900073501 | 2019-01-14 | LEAD | 1137 | CHARTRES | GOV NICHOLLS | WMTLK | LOCATION#203917-600768. METER#D008366. THE METER HAS A VERY BAD LEAK PER THE INSPECTOR AT THE TIME OF INSPECTION /** 1) MN: D006141 SN: 0006128, *TAP: SIZE: D LOC: 40 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: OOO LOC: MTR ON CHARTRES 41FT FRM GOV NICHOLLS 4FT INSD CRB ** 2) MN: SN: 0006128, *TAP: SIZE: B LOC: 42 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: __ LOC: ON CHARTRES 42FT FROM URPL OF GOVERN NICHOLLS ****/ | 2019-01-22 | PUMPED DOWN MANHOLE + REPLACED 1 1/2 INCH STOP COCK + TWO 1 1/2 INCH UNION IN MANHOLE AT ABOVE LOCATION
201900074801 | 2019-01-15 | LEAD | 2238 | LIZARDI | N TONTI | WILK | INLET SERVICE LEAK /** 1) MN: A251472 SN: 0127321, *TAP: SIZE: A LOC: 293 FEET FROM P LINE AT MIRO N, *MB: CODE: CDL1 LOC: RES ON LIZARDI 293FT P/L N MIRO 6' OUTSIDE 4' ****/ | 2018-12-27 | EXCAVATED 3 X 2 DRIVWAY CUT REPLACED 5/8 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900075301 | 2019-01-15 | LEAD | 1022 | BURGUNDY |  | WMTLK | LOCATIONID#106975-529452 METER#A238813 LEAK INSIDE METERBOX /** 1) MN: A238813 SN: 0008943, *TAP: SIZE: B LOC: 153 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: CEL LOC: INSIDE 151' P.L. URSULINES AV ****/ | 2019-02-12 | REPLACED WASHERS TO STOP LEAK
201900075601 | 2019-01-15 | LEAD | 840 | GOV NICHOLLS |  | WMTLK | LOCATIONID#116008-529191 METER#A237083 LEAK INSIDE METERBOX /** 1) MN: A237083 SN: 0029537, *TAP: SIZE: A LOC: 49 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: CD LOC: ON DAUPHINE 45FT FROM GOV NICHOLLS ** 2) MN: SN: 0029537, *TAP: SIZE: A LOC: 49 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: __ LOC: ON DAUPHINE 50FT FROM P.L. GOV. NICHOLLS ****/ | 2019-02-12 | EXCAVATED 3 X 2 SIDEWALK CUT MADE REPAIR ON INLET SERVICE LINE AND REPLACED 5/8 INCH METER COCK BACKFILLED AND CLEANED THE AREA
201900075801 | 2019-01-15 | LEAD | 1109 | BOURBON |  | WMTLK | LOCATIONID#117393-529205 METER#A295761 LEAK INSIDE METERBOX /** 1) MN: A295761 SN: 0023644, *TAP: SIZE: A LOC: 56 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: AF6 LOC: RES ****/ | 2019-02-07 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND COLDMILL
201900075901 | 2019-01-15 | LEAD | 1035 | BOURBON |  | WMTLK | LOCATIONID#105787-529047 METER#A301615 LEAK INSIDE METERBOX /** 1) MN: A290682 SN: 0025342, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: AE6 LOC: RES 63' P.L. URSULINES AV ****/ | 2019-02-07 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILLED JOB ITH RIVERSAND COLDMILL
201900076001 | 2019-01-15 | LEAD | 1000 | ROYAL |  | WMTLK | LOCATIONID#119448-528955 METER#A346834 LEAK INSIDE METERBOX /** 1) MN: A230268 SN: 0032252, *TAP: SIZE: A LOC: 83 FEET FROM P LINE AT ROYAL, *MB: CODE: BFH5 LOC: APTS AND GROCERY SIDE ST 83' P.L. ROYAL ****/ | 2019-02-07 | EXCAVATED AND MADE REPAIRS ON 5/8 INLET SERVICE BACKFILLED JOB WITH RIVRSAND COLDMILL
201900076101 | 2019-01-15 | LEAD | 1018 | ROYAL |  | WMTLK | LOCATIONID#106403-529078 METER#A312039 LEAK INSIDE METERBOX /** 1) MN: A223488 SN: 0025179, *TAP: SIZE: B LOC: 15 FEET FROM P LINE AT URSULINES, *MB: CODE: AEM2 LOC: ON ROYAL ST. 16FT. FROM DIV. PL OF ST. PHILIP ST. ** 2) MN: A264967 SN: 0025179, *TAP: SIZE: D LOC: 15 FEET FROM P LINE AT URSULINES, *MB: CODE: AEM2 LOC: ON ROYAL ST. FROM DIV. PL OF ST. PHILIP ST. 9FT. F THERE ARE 9 MORE NOT LISTED. ****/ | 2019-02-07 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND,COLDMILL
201900076201 | 2019-01-15 | LEAD | 726 | GOV NICHOLLS |  | WMTLK | LOCATIONID#103375-529005 METER#A240845 LEAK INSIDE METERBOX /** 1) MN: A240845 SN: 0005974, *TAP: SIZE: A LOC: 127 FEET FROM P LINE AT ROYAL, *MB: CODE: AE LOC: ON GOVERN NICHOLLS 127FT FROM URPL OF ROYAL ****/ | 2019-02-12 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900076401 | 2019-01-15 | LEAD | 1310 | ROYAL |  | WMTLK | LOCATIONID#134828-529233 METER#A144024 LEAK INSIDE METERBOX /** 1) MN: A144024 SN: 0065611, *TAP: SIZE: A LOC: 105 FEET FROM P LINE AT BARRACKS, *MB: CODE: CD LOC: 2 APTS - 100' P.L. BARRACKS ****/ | 2019-02-06 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER COCK TO STOP LEAK ALSO REPLACED METER BOTTOM FROM EXCAVATING BACKFILLED AND CLEANE DTHE AREA
201900076701 | 2019-01-15 | LEAD | 3143 | N ROCHEBLAVE | CLOUET | WILK | ML-METER LEAK INLET SERVICE LEAK INSIDE METER BOX CAUSING METER BOX TO OVERFLOW. **NO 1 LIVE @ LOCATION /** 1) MN: A242329 SN: 0106126, *TAP: SIZE: B LOC: 238 FEET FROM P LINE AT LOUISA, *MB: CODE: ADM2 LOC: 239FT FROM PL LOUISA 8FT OUTSIDE PL 2FT INSD CURB ** 2) MN: A113211 SN: 0106126, *TAP: SIZE: A LOC: 295 FEET FROM P LINE AT CLOUET, *MB: CODE: AEM2 LOC: ON N ROCHEBLAVE 294' FROM PL CLOUET 7' OUTSIDE PL ****/ | 2019-01-29 | EXCAVATED IN EXISTING SIDEWALK CUT AND MADE REPAIR ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201900078101 | 2019-01-15 | LEAD | 4935 | EVANGELINE DR |  | WILK | MI-- CUT SERVICE UNKN IF CUSTOMER W/O WATER SERVICES CUT BY: COMMAND CONSTRUCTION 3206 N TURNBULL DR METAIRIE, LA. 7002 504-887-8795 *******DAMAGE CLAIM******* (C.ROSS @ 12:05AM) CUT INLET ON ABANDON SERVICE INFRONT VACANT LOT BY COMMAND CONSTRUCTION INTERFERING WITH CONTRACTORS WORK /** 1) MN: A128524 SN: 0128448, *TAP: SIZE: B LOC: 110 FEET FROM P LINE AT GABRIEL DR, *MB: CODE: A LOC: ON EVANGLINE DR 112' FROM PL GABRIEL DR 7.6' OUTSI ****/ | 2019-01-15 | EXCAVATED IN A STREET CUT FOUND LEAD LINE CUT DO TO CONTRACTOR HITTING INLET SERVICE RPAIR LEAD LINE WITH 5/8 STOP COCK AND RUN 8FT OF 3/4 WATER TUBING TO A NEW 5/8 METER BOX COMPLETE RAISE METER TO GRADE BACKFILL. (JOB COMPLETE) (FORCE ACCOUNT COMMAND CONSTRUCTION)
201900079501 | 2019-01-15 | LEAD | 1414 | EGANIA |  | WMTLK | WM - LEAK IN THE STREET **********1ST AM********** EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER AREA FLOODED. ***FOUND STAGNATED & FRESH WATER @ SITE*** /** 1) MN: SN: 0116168, *TAP: SIZE: B LOC: 100 FEET FROM P LINE AT VILLERE N, *MB: CODE: ADK LOC: RES 100FT FROM P.L. N.VILLERE 7' OUTSIDE PL ON EGA ****/ | 2019-01-16 | EXAMINED JOB PUMPED METER BOX DOWN AND FOUND CURB COCK IN ON POSITION WITH NO METER SHUT OFF CURB COCK TO STOP LEAK FOR VACANT HOUSE JOB COMPLETE
201900079601 | 2019-01-15 | LEAD | 2708 | CHARTRES | PORT | WILK | ML- METER LEAK METER # A314704 ACCT#128634-426905 **FLOODING AREA*** INLET SERVICE LEAK @ THE CURB /** 1) MN: A141872 SN: 0056024, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT PORT, *MB: CODE: ADN LOC: 73FT FROM LRPL PORT ****/ | 2019-02-08 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900079901 | 2019-01-15 | LEAD | 2343 | N MIRO | SPAIN | WILK | ML- METER LEAK MTR# A407360 ACCT# 162869-484239 INLET SERVICE LEAKING INSIDE METER BOX /** 1) MN: A143923 SN: 0102403, *TAP: SIZE: B LOC: 94 FEET FROM P LINE AT SPAIN, *MB: CODE: CDKL LOC: ON NO. MIRO, 94' FROM P.L SPAIN, 8' OUTSIDE P.L. ****/ | 2019-02-11 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900080001 | 2019-01-15 | LEAD | 1433 | N CLAIBORNE AV |  | WMBK | LOCATION ID-304615 MTR-B041691 CASING SHIFTED OVER CURB COCK AND METER TILTED METER BOX CASING SHIFTED OVER CURB COCK /** 1) MN: B032397 SN: 0015385, *TAP: SIZE: B LOC: 87 FEET FROM P LINE AT , *MB: CODE: AFK LOC: ****/ | 2019-01-30 | EXCAVATED IN BRICK SIDEWALK + RESET 5/8 INCH METER BOX CASING PROPERTY BACKFILLED + DRESSED UP AREA
201900080601 | 2019-01-15 | LEAD | 1709 | N MIRO |  | WOLK | ML--METER LEAK ACCOUNT#134845-488796 METER#A416127 ***********LEAKING AGAIN********************************* /** 1) MN: A330777 SN: 0056567, *TAP: SIZE: A LOC: 84 FEET FROM P LINE AT ST BERNARD AVE, *MB: CODE: CDLM LOC: ON N MIRO ST 84' FROM PL D'ABADIE ST ****/ | 2019-01-30 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201900082701 | 2019-01-16 | LEAD | 904 | ROYAL |  | WMTLK | LOCATIONID#112593-527972 METER#C012984 LEAK INSIDE METERBOX /** 1) MN: C012984 SN: 0014472, *TAP: SIZE: A LOC: 34 FEET FROM P LINE AT DUMAINE, *MB: CODE: BF1 LOC: ON ROYAL 36FT FR PL DUMAINE 6FT OUTSD PL ROYAL ****/ | 2019-02-08 | EXCAVATED 3 X 2 SIDEWALK CUT MADE REPAIR ON INLET SERVICE MADE REPAIR ON INLET SERVICE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900083001 | 2019-01-16 | LEAD/PLASTIC | 1000 | DUBLIN | FRERET | WMTLK | LOCATIONID#111563-564452 METER#A417477 LEAK INSIDE METERBOX /** 1) MN: A281099 SN: 0013027, *TAP: SIZE: B LOC: 56 FEET FROM P LINE AT DUBLIN, *MB: CODE: CDH1 LOC: SIDE ON FRERET ST 58' P.L. DUBLIN ****/ | 2019-02-06 | MADE A 4 X 8 MUDCUT INTREE ROOTS EXCAVATED AND MADE REPAIRS ON A 3/4 INLET SERVICE LEAK' LEAD LINE. PLASTIC OUTLET. [RENEWED THE OUT LET ]
201900088101 | 2019-01-16 | LEAD/PLASTIC | 4431 | LOYOLA AV | JENA | WILK | ML- METER LEAK METER# A228794 ACCT# 104339-571938 INLET SERVICFE LEAKING FROM BLEEDER VALVE IN SIDEWALK 03/12/19 LEAK HAS GOTEN WORSE PER SR#12869498 (AJR) /** 1) MN: A228794 SN: 0006692, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT JENA LSPL, *MB: CODE: BE LOC: 82' FROM LSPL JENA ****/ DOTTIE READY 3/19/19 EXP4/8/19 | 2019-03-27 | ARRIVED AT THE ABOVE LOCATION MADE A 3 X 3 SIDEWALK CUT AROUND THE METER BOX AND MADE REPAIRS ON THE INLET AND ALSO RAN A NEW 3/4 OUTLET LEFT SERVICE .THEN BACKFILLED AND CLEANED AREA.
201900089501 | 2019-01-16 | LEAD/PLASTIC | 720 | ST MARY | CHIPPEWA | WMTLK | WM-LEAK ON THE SIDEWALK ************************1ST AM************************* EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-17 | ARRIVED ON JOB SITE EXAMINE LEAK IN MUD PLOT BROKE OUT SIDEWALK BY HAND EXCAVATED IN MUD PLOT MADE REPAIRS ON A 2" CONTROLLING LINE ON 2" WATER MAIN BACKFILLED DRESS UP WORK SITE. JOB COMPLETE
201900090001 | 2019-01-17 | LEAD/PLASTIC | 147 | ALVIN CALLENDER | PRYTANIA | WOLK | ML- METER LEAK MTR # A412978 LOC/CUST # 145599-704116 CONS ON METER /** 1) MN: A114370 SN: 0041249, *TAP: SIZE: B LOC: 246 FEET FROM P LINE AT PRYTANIA, *MB: CODE: ADL LOC: ON ALVIN CALENDER, 246' FROM P.L. PRYTANIA ****/ | 2019-02-23 | MADE A 4 X 8 MUD CUT. EXCAVATED AND MADE REPAIRS ON A 3/4 INLET SERVICE LEAK. LEAD LINE. RAISED THE METER TO GRADE AND RENEWED THE OUTLET WITH PLASTIC.
201900094301 | 2019-01-17 | LEAD | 1527 | ST ROCH AV | N CLAIBORNE AV | WILK | ML: METER LEAK ACCT#122016-482222 MTR#A386468 INLET SERVICE LEAK /** 1) MN: SN: 0057667, *TAP: SIZE: A LOC: 90 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: CFL LOC: ON ST. ROCH AVE.,90' FROM L.R.P.L. NO. CLAIBORNE ****/ | 2019-02-11 | EXCAVATED AND MADE REPAIRS ON 5/8INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND
201900095001 | 2019-01-17 | LEAD | 3210 | DAUPHINE | LOUISA | WDSM | DECREASE EXISTING SERVICE AND METER FROM 1 INCH TO 5/8 INCH SERVICE AND METER AT 3210 DAUPHINE STREET, IN THE SAME LOCATION FOR THE FLAT SUM OF $100.00. NOTE: ESTIMATED TIME OF INSTALLATION FOR SEWER, WATER & DRAIN SERVICE MAY TAKE 4-6 WEEKS. WFA JOB #2756 APP.: #123584 /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-29 | REDUCE 1 INCH METER DOWN TO 5/8 INCH AND REPLACED WASHERS OLD METER INFO: HERSEY #C035912 FACT#15551498 RD-0005
201900095501 | 2019-01-17 | LEAD | 3214 | DAUPHINE | LOUISA | WDSM | DECREASE EXISTING SERVICE AND METER FROM 1 INCH TO 5/8 INCH SERVICE AND METER AT 3214 DAUPHINE STREET, IN SAME LOCATION FOR THE FLAT SUM OF $100.00. NOTE: ESTIMATED TIME OF INSTALLATION FOR SEWER, WATER AND DRAIN SERVICES MAY TAKE 4-6 WEEKS. WFA JOB #2757 APP.: #123585 /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-29 | REDUCE 1 INCH METER TO 5/8 INCH METER AND REPLACED WASHERS OLD METER INFO: HERSEY #C035895 FACT#015551481 RD-0
201900095801 | 2019-01-17 | LEAD | 1434 | ELYSIAN FIELDS AV |  | WMTLK | LOCATIONID#150025-520424 METER#A430388 METERBOX OVERFLOWING /** 1) MN: A335511 SN: 0082839, *TAP: SIZE: B LOC: 237 FEET FROM P LINE AT VILLERE N, *MB: CODE: BDK LOC: ON ELYSIAN FIELDS 237 FT FROM PL N VILLERE ****/ | 2019-02-12 | EXAMINED JOB + FOUND NO LEAK PRESENT
201900095901 | 2019-01-17 | LEAD | 2311 | ST ROCH AV |  | WMTLK | LOCATIONID#142482-703639 METER#A400096 METERBOX OVERFLOWING /** 1) MN: SN: 0071469, *TAP: SIZE: A LOC: 74 FEET FROM P LINE AT NO. TONTI, *MB: CODE: CDLM LOC: ON ST. ROCH AVE., 76' FROM P.L. NO. TONTI ****/ | 2019-02-11 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH OUTLET SERVICE BACKFILLED JOB WITH RIVERSAND
201900096201 | 2019-01-17 | LEAD | 1500 | ELYSIAN FIELDS AV |  | WMTLK | LOCATION ID-302188 MTR-B042119 CASING SHIFTED OVER CURB COCK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-11 | REPLACE UPPER METER BOX CASING AT ABOVE LOCATION
201900096501 | 2019-01-17 | LEAD/PLASTIC | 801 | ODEON AV |  | WMTLK | LOCATION ID-227239 MTR-A373830 UNDERGROUND LEAK AROUND MTR/AREA FLOODED /** 1) MN: SN: 0124038, *TAP: SIZE: A LOC: 53 FEET FROM P LINE AT ODEON AVE, *MB: CODE: BFH LOC: ON PATTERSON 53'FRM PL ODEON 2'OUTSIDE PL ****/ | 2019-02-11 | WE EXCAVATED BY HAND IN TREE ROOTS TO MAKE REPAIRS TO 3/4 INLET REPAIRSA OR COMPLETE WE BACKFILL PLUS CLEAN UP
201900096901 | 2019-01-17 | LEAD | 1416 | ST ANTHONY AV | N ROBERTSON | WILK | ML-METER LEAK INLET LEAK IN SIDEWALK (C) /** 1) MN: A258651 SN: 0018273, *TAP: SIZE: A LOC: 159 FEET FROM P LINE AT VILLERE N, *MB: CODE: BFK1 LOC: 159' P.L. N VILLERE ****/ | 2019-02-11 | REPLACE BOTH INELT AND OUTLET WASHERS AT ABOVE LOCATION
201900097001 | 2019-01-17 | LEAD | 830 | N GALVEZ | DUMAINE | WILK | ML-METER LEAK METER #A426270 ACCT # 121842-721505 INLET LEAK IN THE MUDPLOT BY VACANT LOT )C) /** 1) MN: A243593 SN: 0039774, *TAP: SIZE: A LOC: 92 FEET FROM P LINE AT DUMAINE, *MB: CODE: FL1 LOC: ON NO. GALVEZ,92' FROM U.R.P.L. DUMAINE ****/ | 2019-01-31 | EXCAVATED 4 X 4 SIDEWALK CUT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA JOB COMPLETE
201900097301 | 2019-01-17 | LEAD | 415 | ATLANTIC AV | ALIX | WILK | ML-METER LEAK METER#A360500 ACCT#2247517-401958 INLET SERVICE LEAK IN THE SIDEWALK COMING OUT OF OLD PATC, FLOODING THE SIDEWALK /** 1) MN: A323557 SN: 0040103, *TAP: SIZE: __ LOC: 142 FEET FROM P LINE AT ALIX, *MB: CODE: CEL LOC: ON ATLANTIC AVE., 142' FROM U.S.P.L. ALIX ****/ | 2019-02-02 | EXAMINED AREA BROKED OUT CONCRETE EXCAVATED ON OUTELT SERVICE TO PROPRERTY REPAIRED LEAK ON OUTLET SERVICE BACKFILLED AREA
201900100001 | 2019-01-18 | LEAD | 2441 | CHARTRES |  | WMRE | UNABLE TO CHANGE METER. WHEEL IS BELOW THE CASING. PLEASE REPAIR AND CHANGE METER A283031. SR 111103 METER BOX HAS SHIFTED OVER HANDWHEEL /** 1) MN: A283031 SN: 0044131, *TAP: SIZE: A LOC: 38 FEET FROM P LINE AT CHARTRES, *MB: CODE: BDHN LOC: SIDE ST/SPAIN 38 FT FROM PL CHARTRES ****/ | 2019-02-08 | EXCAVATED 2 X 2 EXPOSED SIDEWALK CUT REPLACED METER AND PLACED METER BOX CASING CORRECT ABOVE METER BOTTOM BAKFILLED AND CLEANED THE AREA **************OLD METER INFO ****************** METER:A283031 FAC:47144925 MAKE:SENSUS READ:35
201900105401 | 2019-01-20 | LEAD | 2032 | PIETY | N GALVEZ | WILK | ML-METER LEAK ACCT#134338-433256 METER#A391670 INLET SERVICE LEAK INSIDE METER BOX 01/22/19 LEAK NOW CAUSING POOR PRESURE PER SR#12864457 (AJR) 1/28/19 CUSTOMER NOW OUT OF WATER, PER P. DAVENPORT (PET) *****J GILLIAM 11:42***** /** 1) MN: A191330 SN: 0084803, *TAP: SIZE: A LOC: 192 FEET FROM P LINE AT GALVEZ N, *MB: CODE: AE5 LOC: R.S. 192' P.L. N GALVEZ ****/ | 2019-01-29 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH BOTTOM BACKFILLED AREA
201900106101 | 2019-01-21 | LEAD | 2600 | N ROBERTSON |  | WMTLK | LOCATIONID#176617-703649 METER#D005709 LEAK INSIDE METERBOX /** 1) MN: D005709 SN: 0120514, *TAP: SIZE: D LOC: 84 FEET FROM P LINE AT FRANKLIN AVE, *MB: CODE: AFK2 LOC: ON N ROBERTSON ****/ | 2019-02-15 | EXAMINED JOB + FOUND NO LEAK
201900106601 | 2019-01-21 | LEAD/PLASTIC | 1624 | SOUTHLAWN BL | MAGELLAN | WOLK | ML- METER LEAK MTR # C017811 LOC/CUST 231410-424650 CONS REG ON METER /** 1) MN: C020381 SN: 0142096, *TAP: SIZE: __ LOC: 0 FEET FROM P LINE AT SOUTHLINE DR, *MB: CODE: BDM1 LOC: ON SOUTHLAWN BLVD., 25' FROM D.P.L. MAGELLAN, 2.5' ****/ | 2019-01-28 | ARRIVED ON JOB SITE EXAMINED CONS REG ON METER EXCAVATED IN M,UD PLOT BY HAND RENEWED OUTLET MADE REPAIRS ON INLET AND SET UP NEW METER BOX COMPLETE BACKFILLED DRESS UP WORK SITE
201900108301 | 2019-01-21 | LEAD | 2019 | BURGUNDY | FRENCHMEN | WILK | ML- METER LEAK ACCT# 116232-485871 MTR# A255776 EXAMINE INLET SERVICE FOR LEAK IN BOX, IN SIDEWALK /** 1) MN: A255776 SN: 0048657, *TAP: SIZE: A LOC: 137 FEET FROM P LINE AT TOURO, *MB: CODE: CFLN LOC: ON BURGUNDY 172FT FROM PL OF FRENCHMEN ****/ | 2019-02-06 | ARRIVED AT ABOVE LOCATIONEXCAVATED IN 2 X 2 SIDEWALK CUT + REPAIRED 5/8 INCH CURB COCK
201900109401 | 2019-01-21 | LEAD | 822 | PHILIP | LAUREL | WILK | MI- LEAK IN THE STREET CHANGED FROM 816 PHILIP INLET SERVICE LEAK IN ASPHALT STREET /** 1) MN: A324791 SN: 0012100, *TAP: SIZE: B LOC: 150 FEET FROM P LINE AT LAUREL, *MB: CODE: CELM LOC: 150FT FROM PL LAUREL M/BOX ON PHILIP ST ****/ | 2019-02-02 | ARRIVED ON JOB SITE EXAMIND LEAK IN MUD PLOT EXCAVATED IN MUD PLOT BY HAND MADE REPAIRS ON INLET SERVICE BACKFILLED DRESSED UP WORK SITE
201900110501 | 2019-01-22 | LEAD | 1709 | N MIRO | D"ABADIE | WOLK | OUTLET SERVICE LEAK /** 1) MN: A330777 SN: 0056567, *TAP: SIZE: A LOC: 84 FEET FROM P LINE AT ST BERNARD AVE, *MB: CODE: CDLM LOC: ON N MIRO ST 84' FROM PL D'ABADIE ST ****/ | 2019-01-20 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900110601 | 2019-01-22 | LEAD | 1528 | PIETY | N CLAIBORNE AV | WILK | INLET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-20 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA (NO METER) (JOB COMPLETE)
201900110701 | 2019-01-22 | LEAD | 5920 | N VILLERE | GORDON | WILK | MI- LEAK BETWEEN SIDEWALK AND CURB INLET SERVICE LEAK IN BOX, NO METER IN BOX, CARS ROLLING OVER METER, HOUSE UNDER RENOVATION /** 1) MN: A250054 SN: 0090790, *TAP: SIZE: C LOC: 9 FEET FROM P LINE AT VILLERE N, *MB: CODE: ADZ LOC: ON GORDON ST 9' OUT FROM PL N VILLERE ****/ | 2019-02-01 | EXCAVATED AND MADE REPAIRS ON 5/8 NCH SERVICE IN MUD PLOT BACKFILLED JOB WITH RIVERSAND. JOB COMPLETE
201900110801 | 2019-01-22 | LEAD | 5914 | N VILLERE | GORDON | WMTAG | ML- METER LEAK METER# A416861 ACCT# 305186-722097 LOWER METER BOX TO PROPER GRADE, NO LEAK FOUND /** 1) MN: SN: 0089776, *TAP: SIZE: C LOC: 9 FEET FROM P LINE AT VILLERE N, *MB: CODE: OOO LOC: ON GORDON 9FT FROM VILLERE ****/ | 2019-02-01 | LOWER METER BXO TO GRADE
201900111001 | 2019-01-22 | LEAD | 1227 | ANNETTE | ST ANTHONY | WILK | INLET SERVICE LEAK /** 1) MN: SN: 0069880, *TAP: SIZE: A LOC: 215 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: ADL LOC: ON ANNETTE, 215' FROM P.L. ST. CLAUDE AVE. ****/ | 2019-01-20 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCHCURB COCK + 5/8INCH HANDWHEEL BACKFILLED + DRESSED UP AREA
201900111401 | 2019-01-22 | LEAD | 1512 | CAFFIN AV | N CLAIBORNE AV | WILK | INLET SERVICE LEAK /** 1) MN: A268673 SN: 0108837, *TAP: SIZE: B LOC: 143 FEET FROM P LINE AT NO. ROBERTSON, *MB: CODE: AD LOC: ON CAFFIN AVE., 135' FROM P.L. NO. ROBERTSON, 7' ****/ | 2019-01-17 | ARRIVED AT ABOVE LOCATION EXCAVATED IN 8 X 11 CONCRETE CUT FOUND 3/4 INCH BEND ADAPTER LEAKING ON 6 INCH WATER MAIN + MADE REPAIRS ON 3/4 INCH PLASTIC
201900112101 | 2019-01-22 | LEAD | 2677 | N ROCHEBLAVE | PAINTERS | WMTLK | ML: METER LEAK, MTR # A371004, ACCT # 148445-485018 CHANGED FROM 2677 N ROCHEBLAVE EXAMINE INLET AND OUTLET SERVICE FOR LEAK /** 1) MN: A330767 SN: 0080648, *TAP: SIZE: B LOC: 234 FEET FROM P LINE AT ARTS, *MB: CODE: CDN1 LOC: ON N ROCHEBLAVE ST 235' FROM PL ARTS ****/ | 2019-02-04 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900112301 | 2019-01-22 | LEAD/PLASTIC | 300 | MOUTON | MILNE BL | WILK | MI-LEAK IN STREET INLET SERVICE LEAK IN ASPHALT STREET ON MILNE BL, FLOODING AREA 01/30/19 PER INSP L HEBERT UPGRD TO AN ***B 1ST AM*** LEAK HAS GOTTEN WORSE CAUSING A DEPRESSION IN AN ASPHALT STREET. NEED 1 BARREL & FLAG (KSW) /** 1) MN: A274703 SN: 0131641, *TAP: SIZE: B LOC: 8 FEET FROM P LINE AT MOUTON, *MB: CODE: ADH LOC: ON MILNE 10' FROM PL MOUTON 6' OUTSIDE PL 2' INSI ****/ | 2019-01-31 | EXCAVATED IN STREET TO REPAIR A INLET SERVICE LEAK HAD TO MAKE A 8 X 8 ASPHALT STREET CUT FOUND ON INLET
201900112401 | 2019-01-22 | LEAD | 1508 | BASIN | N VILLERE | WILK | MI- LEAK IN THE SIDEWALK CHANGED FROM 1508 BASIN INLET ON ABANDON SERVICE IN SIDEWALK /** 1) MN: A326018 SN: 0045948, *TAP: SIZE: D LOC: 64 FEET FROM P LINE AT NO. VILLERE, *MB: CODE: __ LOC: ON ST. PETER, 64' FROM P.L. NO. VILLERE ****/ | 2019-02-04 | EXAMINED METER INSIDE MANHOLE AND FOUND NO LEAK
201900112701 | 2019-01-22 | LEAD | 1481 | N GALVEZ |  | WMTLK | LOCATIONID#126081-488197 METER#A422315 METERBOX OVERFLOWING /** 1) MN: A125513 SN: 0049123, *TAP: SIZE: A LOC: 69 FEET FROM P LINE AT GALVEZ N, *MB: CODE: BDH LOC: ON COLUMBUS,70' FROM U.S.P.L. NO. GALVEZ ****/ | 2019-02-04 | REPLACE WASHERS TO STOP LEAK
201900112901 | 2019-01-22 | LEAD | 2415 | COLUMBUS |  | WMTLK | LOCATIONID#104201-708174 METER#B022762 LEAK INSIDE METERBOX /** 1) MN: B022762 SN: 0006632, *TAP: SIZE: B LOC: 83 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BEH5 LOC: 85FT FROM LSPL ROCHEBLAVE ****/ | 2019-02-15 | ARRIVED AT ABOVE LOCATION EXCAVATED IN DRIVEWAY FOUND 3/4 INCH METER BOX COCK + HANDWHEEL WAS LEAKING REPAIRED + RAISED TO GRADE
201900114101 | 2019-01-22 | LEAD | 2713-15 | N ROMAN |  | WILK | ML METER LEAK ACCOUNT 156234-403759 METER #A340776 EXAMINE INLET SERVICE FOR LEAK /** AT 2713: 1) MN: A340776 SN: 0162809, *TAP: SIZE: A LOC: 103 FEET FROM P LINE AT PORT, *MB: CODE: BDLM LOC: ON ROMAN 102.5FT FROM PORT 8FT OUTSIDE 2FT INSIDE ** AT 2715: 2) MN: A288475 SN: 0093217, *TAP: SIZE: B LOC: 102 FEET FROM P LINE AT PORT, *MB: CODE: CD LOC: ON ROMAN 104FT FROM PORT ****/ | 2019-01-31 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900114201 | 2019-01-22 | LEAD | 2709-11 | N ROMAN | PORT | WILK | ********************PICKUP******************** EXAMINE INLET SERVICE FOR LEAK /** AT 2709: 1) MN: A141327 SN: 0075322, *TAP: SIZE: B LOC: 71 FEET FROM P LINE AT PORT, *MB: CODE: CELN LOC: ON ROMAN 70.FT FROM PORT ****/ | 2019-01-31 | EXCAVATED IN ASPHALT STREET REPLACED 3/4 INCH BEND ADAPTER + 3/4 INCH OUTLET SERVICE LINE FROM WATER MAIN TO METER BOX COMPACTED BACKFILLED + DRESSED UP AREA
201900117201 | 2019-01-22 | LEAD | 722 | ST MARY | CHIPPEWA | WILK | MI- LEAK IN THE SIDEWALK INLET SERVICE LEAK IN MUDPLOT,....LEAKING FROM CURB COCK FLOODING CURB....NO METER IN BOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-02 | ARRIVED ON JOB SITE EXAMINED LEAK IN MUD PLOT EXCAVATED IN MUD PLOT BY HAND MADE REPAIRS ON INLET SERVICE BACKFILLED DRESSED UP WORK SITE
201900117601 | 2019-01-22 | LEAD | 1116 | THAYER | DE ARMAS | WILK | ML:METER LEAK ACCT#238386-404096 MTR#C027455 EXAMINE INLET SERVICE LEAK IN SIDEWALK FOR A LEAK /** 1) MN: C027455 SN: 0176555, *TAP: SIZE: C LOC: 35 FEET FROM P LINE AT DE ARMAS, *MB: CODE: BEK LOC: ON THAYER 35FT FROM DIV P/L DE ARMAS 8' OUTSIDE ****/ | 2019-02-02 | EXAMINED AREA BROKE OUT CONCRETE EXCAVATED ON OUTLET SERVICE ODSERVED LEAK ON OUTLET SERVICE REPAIRED LEAK ON PROOPERTY BACKFILLED CLEANED AREA
201900117901 | 2019-01-22 | LEAD | 3201 | DUMAINE | RENDON | WILK | ML-METER LEAK METER#C023077 ACCT#152255-521769 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: C023077 SN: 0034416, *TAP: SIZE: C LOC: 68 FEET FROM P LINE AT DUMAINE, *MB: CODE: CDHM LOC: ON RENDON 68' FROM PL DUAMINE 8' OUTSIDE PL 2' INS ****/ | 2019-02-04 | EXCAVATED 3 X 2 MUD PLOT THROUGH TREE ROOTS MADE REPAIRS ON OUTLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201900118701 | 2019-01-23 | LEAD | 2701 | PARIS AV |  | WILK | LOCATIONID#128422-492149 METER#A416596 BLEEDER LEAK /** 1) MN: A154767 SN: 0055490, *TAP: SIZE: A LOC: 42 FEET FROM P LINE AT PARIS AVE, *MB: CODE: CDH LOC: ON DUELS GUY WIRE 46FT FROM PL PAINTERS ****/ | 2019-01-31 | REPLACED WASHERS TO STOP LEAK
201900119501 | 2019-01-23 | LEAD | 1737 | N RAMPART |  | WOLK | LOCATION: 109935 MTR# A 433145 INSP L UDEUBOR STATES METER IS NOT CONNECTED AND WHEEL IS BROKEN. WATER OFF, LEFT TAG PLEASE REPAIR HOUSE UNDER CONSTRUCTION AND VACANT INLET & OUTLET SERVICE NOT LINING UP. BROKEN HANDWHEEL, ***HOUSE UNDER RENOVATIONS*** /** 1) MN: A335125 SN: 0011074, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT ST ANTHONY, *MB: CODE: ADM3 LOC: ON RAMPART 70FT FROM ST ANTHONY ****/ | 2019-01-31 | EXCAVATED 3 X 2 SIDEWALK CUT RAISED METER BOX UP TO GRADE AND REPLACED HANDWHEEL BACKFILLED AND CLEANED THE AREA
201900120601 | 2019-01-23 | LEAD | 1404 | FRENCHMEN | N VILLERE | WILK | MI- LEAK ON SIDEWALK CHANGED FROM 1408 FRENCHMEN INLET ON ABANDON SERVICE BY PARKING LOT /** 1) MN: SN: 0055923, *TAP: SIZE: A LOC: 43 FEET FROM P LINE AT VILLERE N, *MB: CODE: AFK LOC: ON FRENCHMEN ST 42' FROM USPL N VILLERE ****/ | 2019-01-31 | EXCAVATED 3 X 2 SIDEWALK CUT RAISED METER UP TO GRADE AND REPLACED HANDWHEEL BACKFILLED AND CLEANED THE AREA
201900121701 | 2019-01-23 | LEAD | 722 | ADELE |  | WILK | ML--METER LEAK ACCOUNT#216423-724941 METER#A354429 INLET SERVICE LEAKING BEHIND CURB COCK FLOODNIG GRASSY AREA /** 1) MN: A351620 SN: 0177002, *TAP: SIZE: A LOC: 542 FEET FROM P LINE AT LAUREL, *MB: CODE: CD LOC: ON ADELE 174FT FROM ANNUNCAITON 8FT OUTSIDE ****/ | 2019-02-02 | ARRIVED ON JOB SITE EXAMINED LEAK IN MUD PLOT EXCAVATED IN MUD PLOT BY HAND MADE REPAIRS ON INLET SERVICE BACKFILLED DRESS UP WORK SITE
201900124801 | 2019-01-23 | LEAD | 1028 | JOSEPHINE |  | WILK | ************PICKUP JOB************ INLET SERVICE LEAK IN MUDPLOT IN TREE ROOTS, FLOODING CURB GETTING OFF IN DCB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-03 | ARRIVED ON JOB SITE EXAMINED LEAK MADE REPAIRS INSIDE METER BOX BACKFILLED DRESS UP WIRH SITE
201900125901 | 2019-01-24 | LEAD | 2265 | MARAIS | MANDEVILLE | WMTLK | METER LEAK ACCT#125558-481390 A-309916 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METERS UNDER WATER /** 1) MN: A309916 SN: 0047786, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: AE6 LOC: ON MARAIS,114.6' FROM U.S.P.L. MANDEVILLE ****/ | 2019-02-05 | PUMPED WATER OUT OF METER BOX AN EXAMINED INELT AND OUTLET FIND NO LEAK RAIN WATER IN BOX
201900126401 | 2019-01-24 | LEAD | 1830 | LAPEYROUSE | N PRIEUR | WILK | INLET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-23 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE NEAR CURB BACKFILLED + DRESSED UP AREA ALSO RAISED 5/8 INCH METER BOX BOTTOM TO GRADE. JOB COMPLETE
201900126501 | 2019-01-24 | LEAD | 1518 | N ROBERTSON | COLUMBUS | WILK | INLET SERVICE LEAK /** 1) MN: A242805 SN: 0043242, *TAP: SIZE: B LOC: 10 FEET FROM P LINE AT COLUMBUS, *MB: CODE: ANF1 LOC: ON N. ROBERTSON 10' FROM DIV. PL OF COLUMBUS ST. ** 2) MN: A345283 SN: 0043242, *TAP: SIZE: B LOC: 9 FEET FROM P LINE AT COLUMBUS, *MB: CODE: ANF1 LOC: ON N. ROBERTSON 9FT. FROM DIV. PL OF COLUMBUS ST. THERE IS 1 MORE NOT LISTED. ****/ | 2019-01-23 | EXCAVATED IN BRICK SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA ALSO REPLACED 5/8 INCH METER BOX BOTTOM (NO METER) (JOB COMPLETE)
201900126701 | 2019-01-24 | LEAD | 837 | N BROAD | DUMAINE | WILK | INLET SERVICE LEAK /** 1) MN: B028387 SN: 0021645, *TAP: SIZE: B LOC: 65 FEET FROM P LINE AT DUMAINE, *MB: CODE: CDL4 LOC: ON NO. BROAD,65' FROM U.S.P.L. DUMAINE ****/ | 2019-01-23 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER COCK BACKFILLED AND CLEANED THE AREA. . JOB COMPLETE
201900127001 | 2019-01-24 | LEAD | 2222 | MARAIS |  | WOLK | MI--- CHECK FOR LEAK AT METER OUTLET SERVICE LEDAK @ PROPERY LINE, FLOODING SIDEWALK /** 1) MN: A312523 SN: 0048921, *TAP: SIZE: B LOC: 11 FEET FROM P LINE AT ELYSIAN FIELDS AVE, *MB: CODE: OOO LOC: ON MARAIS 11' FROM DIV PL ELYSIAN FIELDS AVE 9' OU ****/ | 2019-02-08 | MADE REPAIRS ON 5/8 INCH OUTLET SERVICE REQUEST CUSTOMER TO DROP COPPER LINE AND BURIED IT
201900128301 | 2019-01-24 | LEAD | 1321 | EGANIA | URQUHART | WMTLK | MI- LEAK BETWEEN THE SIDEWALK AND THE STREET EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN GRAVEL, METER UNDER WATER, UNABLE TO PUMP OUT /** 1) MN: A214191 SN: 0111231, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT URQUHART, *MB: CODE: ADK LOC: MTR ON EGANIA 150FT FROM PL URQUHART 9FT OUTSIDE ****/ | 2019-02-11 | EXCAVATED IN GRAVEL AND FOUND 5/8 INCH CURB COCK LEAKING MADE REPAIRS BACKFILLED AREA
201900128401 | 2019-01-24 | LEAD | 1405 | SHEPARD | THAYER | WILK | ML- METER LEAK METER # C033035 ACCT # 239196-405909 **FLOODING AREA*** INLET SERVICE LEAK IN BOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-02 | EXAMINED AREA EXCAVATED ON OUTLET SERVICE EXPOSED LEAK ON OUTLET SERVICE REPAIRED LEAK BACKFILLED CLEANED AREA
201900128601 | 2019-01-24 | LEAD | 1522 | GOV NICHOLLS |  | WOLK | LOCATION ID-209499 MTR-A125706 METER LEAK OUTLET SERVICE LEAK IN GARDEN /** 1) MN: A125706 SN: 0027220, *TAP: SIZE: B LOC: 6 FEET FROM P LINE AT NROBERTSON, *MB: CODE: CD LOC: ON GOV NICHOLLS 6' FROM N ROBERTSON 9'OUTSIDE 3'IN ****/ | 2019-02-05 | EXCAVATED IN GARDEN MUD PLOT AND MADE REPAIRS ON 3/4 INCH OUTLET BEHIND METER BOX BACKFILLED AREA
201900128701 | 2019-01-24 | LEAD | 1943 | L B LANDRY AV | SHEPARD | WILK | ML- METER LEAK METER # C030209 ACCT # 239188-405922 INLET SERVICE LEAK IN MUDPLOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-03 | EXAMINED AREA EXCVATED ON INLET + OUTLET SERVICE EXCAVATED THROUGH ROOTS REPAIRED LEAK BACKFILLED LCEANED AREA
201900130501 | 2019-01-24 | LEAD | 2233 | GEN COLLINS AV |  | WILK | ML--METER LEAK ACCOUNT#229839-408688 METER#A298742 INLET SERVICE LEAK IN CONCRETE DRIVEWAY FLOODING CURB GETTING OFF IN THE DCB /** 1) MN: A298742 SN: 0132735, *TAP: SIZE: B LOC: 231 FEET FROM P LINE AT COPERNICUS, *MB: CODE: CD23 LOC: ON GEN COLLINS 232FT FROM P.L. COPERNICUS ****/ | 2019-02-03 | EXAMINED AREA BROKE OUT CONCRETE EXCAVATED ON INLET + OUTLET SRVICE REPAIRED LEAK OM N INLET SERVICE REPLACED BROKEN HANDWHEEL BACKFILLED CLEANED AREA
201900131101 | 2019-01-25 | LEAD | 1318 | DAUPHINE |  | WILK | LOCATION: 114134 MTR# A 417574 INSP D. JOHNSON STATES BAD LEAK COMING FROM CURB COCK. PLEASE REPAIR. INLET AND OUTLET SERVICE NOT LINING UP /** 1) MN: A266941 SN: 0018871, *TAP: SIZE: A LOC: 36 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: AEL LOC: 37' P.L. ESPLANADE AVE ****/ | 2019-02-08 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACE 5/8 INCH METER COCK BACKFILLED AND CLEANED THE AREA
201900131201 | 2019-01-25 | LEAD | 2112 | ST ROCH AV |  | WILK | LOCATION: 306009 INSP D. JOHNSON UNABLE TO SET A METER, CURB COCK SIDE IS A 3/4 SIZE. PLEASE REPAIR CURB COCK SIDE AND SET A 5/8 METER. CUSTOMER WAITING ON WATER INLET AND OUTLET SERVICE NOT THE SAME SIZE, REPAIR AND SET 5/8 METER, HOUSE UNDER CONSTRUCTION /** 1) MN: 000000 SN: 0056447, *TAP: SIZE: C LOC: 104 FEET FROM P LINE AT GALVEZ N, *MB: CODE: BDNK LOC: 92' P.L. GALVEZ N ****/ | 2019-02-06 | REPLACED 3/4 INCH CURB COCK PUT IN 5/8 INCH CURB COCK WHEEL HAD LEAK ON IT REPLACED IT WITH A 5/8 INCH WHEEL
201900134001 | 2019-01-25 | LEAD/PLASTIC | 3724 | BRUXELLES | MILTON | WOLK | MI- CHANGE LEAD WHIP METER # A375897 HOLE IS EXPOSED **********A.PARKER @ 11:51AM*************** OUTLET TIE IN,CUSTOMER OUT OF WATER /** 1) MN: A276218 SN: 0097529, *TAP: SIZE: A LOC: 168 FEET FROM P LINE AT ST DENIS, *MB: CODE: BDM4 LOC: ON BRUXELLES, 168' FROM P.L. ST. DENIS,7' OUTSIDE ****/ | 2019-01-25 | EXCAVATED A 3 X 4 MUD CUT AND RENEW THE OUTLET SERVICE FROM METER TO PROPERTY . LEAD ON THE INLET SERVICE BACKFILL AND CLEAN UP
201900134101 | 2019-01-25 | LEAD | 6025 | DOVER PL | WESTCHESTER PL | WOLK | ML-METER LEAK METER #B034240 ACCT#228433-419649 CHECK FOR LEAK @ PROPERTY LINE /** 1) MN: B032380 SN: 0121679, *TAP: SIZE: B LOC: 171 FEET FROM P LINE AT WESTCHESTER, *MB: CODE: BD LOC: ON DOVER PL., 171' FROM P.L. WESTCHESTER, 8' OUT- ****/ | 2019-02-03 | EXAMINED AREA OBSERVED AREA EXCAVATED TO PROERTY OBSERVED NO LEAK BACKFILLED CLEANED AREA ALSO REPLACED METER BOX COCK
201900136001 | 2019-01-25 | LEAD | 2305 | CHOCTAW | N TONTI | WILK | MI- LEAK IN STREET **FLOODING CUST YARD*** CHANGED FROM 2300BLK CHOCTAW EXAMINE INLET SERVICE FOR A LEAK ON AN ABANDON SERVICE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-11 | EXCAVATED IN GUTTER BOTOOM FOUND NO LEAK MADE ADDITIONAL 6 X 6 CUT IN ASPHALT STREET FOUND LEAK ON 3/4 INCH TAIL PIECE FOR ABANDON LOT MADE REPAIRS BACKFILLED AREA
201900136701 | 2019-01-25 | LEAD | 968 | WILSON DR | DELGADO DR | WOLK | WM LEAK IS SIDEWALK OUTLET LEAK ON THE SIDEWALK (C) /** 1) MN: A295089 SN: 0069095, *TAP: SIZE: B LOC: 502 FEET FROM P LINE AT DUMAINE, *MB: CODE: ADK2 LOC: 154' P.L. DELGADO ****/ | 2019-02-08 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH OUTLET SERVICE BACKFILLED JOB WITH RIVERSAND
201900137301 | 2019-01-25 | LEAD | 711 | KERLEREC | ROYAL | WILK | ML-METER LEAK ACCT #103056-485278 METER# B032986 "EXAMINE INLET FOR A LEAK UNDERGROUND ON THE SIDEWALK" (C) /** 1) MN: B023357 SN: 0005690, *TAP: SIZE: B LOC: 84 FEET FROM P LINE AT ROYAL, *MB: CODE: CDN2 LOC: ON KERLEREC 84FT FROM LSPL OF ROYAL ****/ | 2019-02-17 | EXCAVATED 5 X 5 SIDEWALK MADE REPAIR ON INLET SERVICE LEAK BACKFILLED AND CLEANED THE AREA
201900138801 | 2019-01-26 | LEAD | 5348 | CAMP | JEFFERSON AV | WILK | ML-METER LEAK ACCT#120940-559653 METER#A255057 INLET SERVICE LEAK IN MUDPLOT BAD CURBCOCK /** 1) MN: A255057 SN: 0037213, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT LEONTINE, *MB: CODE: CEL1 LOC: ON CAMP ST 83' FROM UPL LEONTINE ST ****/ DOTTIE READY 2-25-19 EXP 3-17-19 | 2019-03-16 | REPLACED 5/8 CURB COCK TIED INTO LEAD.
201900139101 | 2019-01-26 | LEAD/PLASTIC | 8 | VIVIAN CT | HUNTLEE DR | WILK | ML-METER LEAK ACCT#227066-415957 METER#A147175 INLET SERVICE LEAK FLOODING SIDEWALK SPOKE WITH CUSTOMER /** 1) MN: A147175 SN: 0115927, *TAP: SIZE: A LOC: 123 FEET FROM P LINE AT HUNTLEE DR, *MB: CODE: BFK LOC: ON VIVIAN CT., 123' FROM P.L. HUNTLEE DR., 4' OUT- ****/ | 2019-02-06 | EXAMINED AREA EXCAVATED ON INLET AND OUTLET SERVICE OBSERVED LEAK ON OUTLET SERVICE TRACED TO PROPERTY RENEWED OUTLET WITH PLASTIC REMOVED LEAD LEAD FOUND ON INLET BACKFILLED DRESSED CUT CLEANED AREA
201900140302 | 2019-03-16 | LEAD | 2230 | S GAYOSO | FONTAINEBLEAU DR | WILK | INLET SERVICE LEAK ON SIDEWALK /** 1) MN: A318929 SN: 0073718, *TAP: SIZE: B LOC: 225 FEET FROM P LINE AT JENA, *MB: CODE: CEL LOC: ON GAYOSO 230FT FROM JENA ****/ DOTTIE READY 3/21/19 EXP 4/10/19 | 2019-03-27 | REPLACED 5/8 CURB COCK AND TWO UPPER METER CASTING.TIED INTO LEAD.(SOC 2FT. X 2 T .S/W)
201900140501 | 2019-01-26 | LEAD | 5571 | MILNE BL | HOMEDALE | WILK | WM-LEAK IN STREET SIDEWALK NEAR SERVICE ALLEY INLET SERVICE LEAK IN MUDPLOT, FLOODING NEIGHBOR'S PROPERTY. CUSTOMER ALSO HAVE VERY POOR PRESSURE (JOB GIVEN TO J. MORGAN) /** 1) MN: A279302 SN: 0086897, *TAP: SIZE: A LOC: 216 FEET FROM P LINE AT HOMEDALE AVE, *MB: CODE: AGJ LOC: ON MELROSE ALLEY, 216' FROM P.L. HOMEDALE AVE. ****/ | 2019-01-26 | ARRIVED ON JOB SITE EXAMINED LEAK AND CUSTOMER OUT OF WATER EXCAVATED IN MUD PLOT BY HAND MADE REPAIRS ON SERVICE AND SET UP NEW METER BOX COMPLETE BACKFILLED DRESSED UP WORK SITE
201900142001 | 2019-01-27 | LEAD | 3719 | BLAIR |  | WILK | ML-METER LEAK ACCT#229914-420562 MTR#A297150 INLET SERVICE LEAK INSIDE METER BOX. ***SPOKE WITH CUSTOMER*** /** 1) MN: A297150 SN: 0133384, *TAP: SIZE: B LOC: 698 FEET FROM P LINE AT BERKLEY DR, *MB: CODE: BD LOC: 699FT FROM P.L. BERKLEY ****/ | 2019-02-03 | EXAMINED AREA EXCAVATED ON ILET + OUTLET SERVICE TRACED TO PROPERTY OBSERED LEAK ON OUTLET SERVICE REPAIRED LEAK BACKFILLED CLEANED AREA
201900143901 | 2019-01-28 | LEAD | 614 | TOULOUSE |  | UNKN | INSP D JOHNSON STATES HE IS UNABLE TO CHANGE METER. METER IS CEMENTED INTO BOX AND ISN'T OPERATING. PLEASE REPAIR AND CHANGE METER C035219 LOC 188709 METER BOX FILLED WITH CEMENT, METER UNABLE TO BE MOVE /** 1) MN: C026949 SN: 0145786, *TAP: SIZE: C LOC: 119 FEET FROM P LINE AT CHARTRES, *MB: CODE: BENM LOC: ON TOULOUSE 118FT FROM PL CHARTRES 5FT OUTSIDE PL ****/ | 2019-02-14 | REMOVED ALL CONCRETE AND DEBRIS OUT OF METER BOX REPLACE 1 INCH METER WITH NEW METER OLD METER INFO: HERSEY #C035219, FACT#015509181 RD:0
201900147501 | 2019-01-28 | LEAD | 2018 | URSULINES AV |  | WILK | INSP D JOHNSON STATES SERVICE IS LEAKING BEHIND CURBCOCK. PLEASE REPAIR AS SOON AS POSSIBLE. METER A309290 LOC 117823 INLET SERVICE LAEK NEAR CURB COCK /** 1) MN: A309290 SN: 0048763, *TAP: SIZE: A LOC: 149 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CFL4 LOC: 149' P.L. N JOHNSON ****/ | 2019-02-13 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE IN SIDEWALK BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900149801 | 2019-01-28 | LEAD | 2500 | TRICOU | N DORGENOIS | WILK | ML: METER LEAK ACCT #181629-421977 MTR#A418213 INLET SERVICE LEAK INSIDE METER BOX, HOLE IS OPEN INTERFERRING WITH CONTRACTORS WORK 01/29/19 CUST NOW HAS POOR PRESSURE (KSW) /** 1) MN: A307245 SN: 0129717, *TAP: SIZE: B LOC: 9 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: ADN1 LOC: RES ON TRICOU 9FT P.L. N DORGENOIS 7' OUTSIDE ****/ | 2019-01-31 | REPLACED METER CASING AND TEST PRESSURE AT FAUCAT AT 55 PSI ALSO CHANGE OUT WASHERS
201900150401 | 2019-01-28 | LEAD | 1721 | ALVAR |  | WILK | ML-METER LEAK ACCT#153509-432553 MTR#A417867 INLET SERVICE LEAK IN SIDEWALK, FLOODING SIDEWALK 02/06/19 LEAK GETTING WORST (KSW) /** 1) MN: A241663 SN: 0089409, *TAP: SIZE: A LOC: 174 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BDM5 LOC: ON ALVAR, 145.5' FROM P.L. NO. DERBIGNY,7.5' OUT- ****/ | 2019-02-17 | FOUND OUTLET WASHERS LEAK
201900150701 | 2019-01-28 | LEAD | 1212 | ST ANTHONY AV | ST CLAUDE AV | WILK | MI : LEAK IN THE STREET EXAMINE INLET SERVICE BETWEEN CURB AND STREET FOR A LEAK /** 1) MN: A246674 SN: 0015402, *TAP: SIZE: B LOC: 5 FEET FROM P LINE AT ST CLAUDE, *MB: CODE: CD LOC: ON ST ANTHONY 5' FROM DIV. P.L. ST ANTHONY 6' OUT- ****/ | 2019-02-12 | EXAMINED JOB AT ABOVE LOCATION FOUND NO LEAK ON INLET OR OUTLET
201900152701 | 2019-01-29 | LEAD | 511 | ST LOUIS |  | WOLK | LOCATION ID-110428 MTR-A418613 UNDERGROUND LEAK BETWEEN MTR AND STOP & WASTE/CONS REG ON MTR /** 1) MN: A258790 SN: 0011734, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT DECATUR, *MB: CODE: AEL1 LOC: RES AND STORE 95' P.L. DECATUR ****/ | 2019-02-14 | EXAMINE JOB + FOUND NO CONSTANT REGISTRATION
201900153201 | 2019-01-29 | LEAD | 2125 | PAUGER |  | WMBK | INSP D JOHNSON STATES HE IS UNABLE TO SET METER BECAUSE METERBOX IS FILLED WITH CEMENT. PLEASE REPAIR AND SET 5/8 METER. LOC 205996 UPPER METER BOX CASING BROKEN NOT STAYING ON PROPERLY /** 1) MN: A158768 SN: 0051440, *TAP: SIZE: A LOC: 55 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: __ LOC: ON PAUGER 56FT FROM PL N ROBERTSON 9' OUTSIDE PL 3 ****/ | 2019-02-13 | ARRIVED AT ABOVE LOCATION FOUND CEMENT IN METER BOX CLEANED IT ALL + SET 5/8 INCH METER
201900159501 | 2019-01-29 | LEAD | 2438 | DESIRE | N ROCHEBLAVE | WILK | ML- METER LEAK METER #A420480 ACCT # 151319-433865 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A338965 SN: 0109025, *TAP: SIZE: A LOC: 272 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: ADK2 LOC: 262' P.L. N ROCHEBLAVE BETWEEN POST & DRIVE ****/ | 2019-02-15 | EXCAVATED 5 X 2 MUD PLOT MADE REPAIR ON 1 INCH INLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900160101 | 2019-01-29 | LEAD/PLASTIC | 3000 | KANSAS | AMAZON | WMTLK | ML - METER LEAK MTR#A334848 ACCT# 166655-506341 EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER IN MUDPLOT 01/31/19 PER INSP L HEBERT UPGRD TO A **** ( B ) 1ST AM***** CUSTOMER HAS VERY LOW PRESSURE, ALSO INSP L HEBERT STATED HE SPOKE WITH S SLACK /** 1) MN: A334848 SN: 0139187, *TAP: SIZE: B LOC: 45 FEET FROM P LINE AT AMAZON, *MB: CODE: CDL1 LOC: ON KANSAS 45' FROM PL AMAZON 7' OUTSIDE PL ****/ | 2019-02-01 | ARRIVED ON JOB SITE EXAMINE LEAK AND CUSTOMER HAD LOW PRESSURE EXCAVATED IN MUD PLOT BY HAND MADE REPAIRS ON SERVICE CUSTOMER HAVE GOOD PRESSURE BACKFILLED DRESS UP WORK SITE
201900161501 | 2019-01-30 | LEAD | 2302 | ORLEANS |  | WOLK | LOCATION# 220350 CUSTOMER# 526812 METER# B035293 INSPECTOR DID AN OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION ON METER, PUMPED WATER OUT METER FILLS BACK UP ALSO METER NEEDS TO BE RAISED TO GRADE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-15 | ARRIVED AT ABOVE LOCATION EXAMINED OUTLET FOR CONSTANT REGISTRATION + FOUND NO LEAK OR WATER IN METER BOX
201900163101 | 2019-01-30 | LEAD | 1641 | BARTHOLOMEW | N DERBIGNY | WMTLK | MI: LEAK ON SIDEWALK, MTR # A419279, ACCT # 304746-719957 EXAMINE INLET & OUTLET SERVICE FOR A LEAK ON THE SIDEWALK METER UNDER WATER /** 1) MN: A305213 SN: 0084033, *TAP: SIZE: A LOC: 11 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: __ LOC: ON BARTHOLOMEW 14FT FROM DERBIGNY ****/ | 2019-02-17 | EXCAVATED 4 X 5 MUD PLOT MADE REPAIR ON INLET SERVICE LEAK BACKFILED AND CLEANED THE AREA
201900163301 | 2019-01-30 | LEAD/PLASTIC | 2366 | ST THOMAS | 1ST | WOLK | INSP S BIBBINS STATES SERVICE NEEDS WHIP TIED IN AND NEW CASING. PLEASE REPAIR AND SET 5/8 METER. LOC 306741 OUTLET TIE IN HOLE EXPOSED, NEW CONSTRUCTION /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-01-31 | ARRIVED ON JOB SITE EXCAVATED IN MUD PLOT SET UP NEW METER BOX COMPLETE AND SET 5/8 METER ALSO TIED OUTLET IN BACKFILLED DRESS UP WORK SITE LEFT METER OFF
201900164501 | 2019-01-30 | LEAD | 1549 | N DERBIGNY | LAPEYROUSE | WMTLK | CUSTOMER WAITING ON WATER. INLET AND OUTLET NOT LINING UP CORRECTLY. PLEASE REPAIR METER A433108 ASAP. LOC 124010 *****************J.GILLIAM @ 10:55 10:24AM**************** BROKEN INLET SERVICE UNABE TO CLOSE, ALSO BROKEN OUTLET SERVICE, CON REG /** 1) MN: SN: 0044486, *TAP: SIZE: A LOC: 90 FEET FROM P LINE AT LAHARPE, *MB: CODE: D LOC: ON DERBIGNY 89FT FROM LSPL LAHARPE ****/ | 2019-01-30 | ARRIVED AT ABOVE LOCATION + FOUND CUSTOMER OUT OF WATER EXCAVATED IN CONCRETE SIDEWALK + MUD PLOT + FOUND INLET + OUTLET REVERSED MADE REPAIR ON 3/4 INCH INLET SERVICE LINE + REPLACED 3/4 INCH OUTLET SERVICE LIEN FROM METER BOX TO PROPERTY RESTORING WATER BACK TO ABOVE LOCATION BACKFILLED + DRESSED UP AREA
201900166201 | 2019-01-30 | LEAD | 1430 | N DORGENOIS | KERLEREC | WILK | MI- LEAK BETWEEN S/WALK & STREET CHANGED FROM 1430-34 N DORGENOIS EXAMINE INLET SERVICE FOR A LEAK METER LOCATED IN LARGE TREE ROOTS /** 1) MN: A283909 SN: 0098421, *TAP: SIZE: A LOC: 24 FEET FROM P LINE AT KERLEREC, *MB: CODE: ADM LOC: 23FT FROM PL KERLEREC ****/ | 2019-02-19 | EXCAVATED 7 X 2 MUD PLOT TRENCH THROUGH TREE ROOTS MADE ON INLET SERVICE LINE AND REPLACED METER COCK ALSO METER WAS REPLACED DUE TO MAKING REPAIR BACKFILLED AND CLEANED THE AREA
201900166901 | 2019-01-30 | LEAD | 1805 | MILAN | BARONNE | WILK | WM LEAK IN SIDEWALK INLET SERVICE LEAKING FROM CURB COCK /** 1) MN: A256909 SN: 0017031, *TAP: SIZE: A LOC: 70 FEET FROM P LINE AT MILAN, *MB: CODE: BDHM LOC: ON SIDE CRB ON BARONNE 67.7' FROM LPL MILAN ****/ DOTTIE READY 3/21/19 EXP 4/10/19 | 2019-03-31 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK WITH NEW ONE BACKFILLED AREA
201900167401 | 2019-01-30 | LEAD | 1720 | INDEPENDENCE | N ROMAN | WILK | MI- LEAK BETWEEN THE SIDEWALK AND THE STREET INLET SERVICE LEAK IN MUDPLOT BETWEEN SIDEWALK & STREET /** 1) MN: A264886 SN: 0092931, *TAP: SIZE: A LOC: 162 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: ADK LOC: 160'PL N DERBIGNY ON INDEPENDENCE ****/ | 2019-02-26 | EXAMINED AND PUMPED INSIDE METER BOX AND FOUND HANDWHEEL BROKE REPLACED WHEEL INSIDE METER BOX TO STOP LEAK CARS ROLL OVER METER
201900167801 | 2019-01-30 | LEAD | 4510 | N DERBIGNY |  | WMTLK | MI LEAK ON THE SIDEWALK EXAMINE INLET & OUTLET SERVICE INSIDE MANHOLE FOR A LEAK /** 1) MN: SN: 0161694, *TAP: SIZE: B LOC: 130 FEET FROM P LINE AT KENTUCKY, *MB: CODE: OOO LOC: ON N DERBIGNY 130FT FROM PL KENTUCKY 2FT OUTSD ****/ | 2019-03-21 | EXAMINE JOB AT ABOVE LOCATION FOUND LEAK ON 2 INCH INLET SERVICE INSIDE OF MANHOLE MADE REPAIRS ON 2 INCH INSIDE OF MANHOLE JOB COMPLETE
201900170001 | 2019-01-31 | LEAD | 2528 | AUBRY |  | WMTLK | LOCATION#140082-479376. THE METER HAS A BAD LEAK. THE INSPECTOR COULD NOT TELL WHERE THE LEAK WAS COMING FROM. /** 1) MN: A294449 SN: 0070823, *TAP: SIZE: A LOC: 52 FEET FROM P LINE AT ROUSSELIN, *MB: CODE: CD LOC: 52FT FROM PL ROUSSELIN ****/ | 2019-02-22 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR INLET SERVICE LIEN AND REPLACED METER COCK BACKFILLED AND CLEANED THE AREA
201900170401 | 2019-01-31 | LEAD | 1436 | N TONTI | KERLEREC | WMTLK | LOCATION 132887-718848. METER#A380439. THE METER BOX IS OVERFLOWING WITH WATER PER THE INSPECTORS FINDINGS. /** 1) MN: A293158 SN: 0063736, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT KERLEREC, *MB: CODE: BDK LOC: 64FT FROM PL KERLEREC ****/ | 2019-02-22 | REPLACED WASHER TO STOP LEAK
201900170601 | 2019-01-31 | LEAD | 2301 | CONGRESS |  | WMTBG | LOCATIONID#174501-434231 METER#A327747 CASING ABOVE GRADE,RAISE /** 1) MN: A231315 SN: 0118032, *TAP: SIZE: A LOC: 35 FEET FROM P LINE AT NO. TONTI, *MB: CODE: AD LOC: ON CONGRESS, 33' FROM P.L. NO. TONTI, 7' OUTSIDE ****/ | 2019-02-20 | FOUND METER BOX 3 CASES DEEP EXCAVATED 4 X 3 MUD PLOT RAISED METER BOX TO CORRECT GRADE LEVEL BACKFILLED AND CLEANED THE AREA
201900171701 | 2019-01-31 | LEAD | 2222 | ONZAGA | N MIRO | WILK | ML- METER LEAK METER # A407505 ACCT# 137689-702221 CHANGED FROM 2220 ONZAGA EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX, METER BOX LOCATED ON SIDEWALK IN A CONCRETE STREET /** 1) MN: A177570 SN: 0068330, *TAP: SIZE: A LOC: 166 FEET FROM P LINE AT MIRO S, *MB: CODE: CEMN LOC: 164' FROM PL OF MIRO S ****/ | 2019-02-22 | EXCAVATED 2 X 2 SIDWALK CUT REPLACED METER COCK TO STOP LEAK BACKFILED AND CLEANED THE AREA
201900173401 | 2019-01-31 | LEAD | 2267-69 | N PRIEUR |  | WMTLK | WM-- LEAK IN THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER /** AT 2267: 1) MN: A118629 SN: 0093536, *TAP: SIZE: A LOC: 59 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: CD LOC: ON NO. PRIEUR,60' FROM U.S.P.L. MANDEVILLE ****/ | 2019-02-20 | EXCAVATED 3 X 2 SIDWALK CUT AND 5 X 2 MUD PLOT RELOCATION METER BOX FROM MUD PLOT TO SIDEWALK ALSO RENEWED OUTLET SERVICE LINE
201900173501 | 2019-01-31 | LEAD | 1227 | ST FERDINAND | URQUHART | WILK | ML: METER LEAK ACCT#126445-479906 MTR# A335064 INLET SERVICE LEAK INSIDE BOX IN SIDEWALK /** 1) MN: A335064 SN: 0050238, *TAP: SIZE: A LOC: 124 FEET FROM P LINE AT URQUHART, *MB: CODE: ADMN LOC: ON ST FERDINAND 123.5' FROM LRPL URQUHART ****/ | 2019-02-20 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED YHE AREA
201900174801 | 2019-01-31 | LEAD | 2721 | DUMAINE | N BROAD | WMTLK | ML- METER LEAK METER# A422601 ACCT# 102174-520775 EXAMINE INLET & OUTLET SERVICE FOR A LEAK, METER BOX UNDER WATER /** 1) MN: A308773 SN: 0004901, *TAP: SIZE: B LOC: 189 FEET FROM P LINE AT BROAD N, *MB: CODE: AFK LOC: ON DUMAINE 189FT FROM LSPL OF N BROAD ****/ | 2019-02-16 | EXCAVATED 4 X 4 MUD POT TO MAKE REPAIR ON A OUTLET SERVICE LEAK BACKFILLED AND CLEANED THE AREA
201900175101 | 2019-01-31 | LEAD | 2615 | A P TUREAUD AV | LAW | WILK | WM- LEAK IN THE STREET INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A338981 SN: 0071229, *TAP: SIZE: C LOC: 90 FEET FROM P LINE AT LAW, *MB: CODE: CDL LOC: ON A.P. TUREAUD AVE., 90' FROM P.L. LAW, 9'OUTSIDE ****/ | 2019-02-16 | EXCAVATED 4 X 3 MUD MADE REPAIR ON INLET SERVICE LEAK BACKFILLED AND CLEAND THE AREA
201900175801 | 2019-01-31 | LEAD/PLASTIC | 237 | BROADWAY | COLISEUM | WILK | MI METER LEAK MTR #A406639 ACCT# 110112-566560 INLET SERVICE LEAK AT CURBCOCK FLOODING SIDEWALK /** 1) MN: A239243 SN: 0054803, *TAP: SIZE: A LOC: 34 FEET FROM P LINE AT COLISEUM, *MB: CODE: BDKL LOC: ON BROADWAY, 26' FROM P.L. COLISEUM, 10' OUTSIDE, ** 2) MN: A330599 SN: 0061960, *TAP: SIZE: C LOC: 66 FEET FROM P LINE AT BROADWAY, *MB: CODE: __ LOC: ON SIDE STREET ON COLISEUM 66' FROM LRPL BROADWAY ****/ | 2019-02-07 | EXCAVATED IN MUD PLOT TO REPAIRE A BAD METER BOX COCK HAD TO MAKE A 2X4 SIDEWALK CUT FOUND LEAD ON INLET
201900175901 | 2019-01-31 | LEAD/PLASTIC | 7420 | ZIMPEL | CHEROKEE | WMTLK | MI- LEAK IN STREET EXAMINE INLET/OUTLET SERVICE FOR LEAK FLOODING SIDEWALK ON CHEROKEE METER BOX UNDER WATER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-23 | MADE REPAIRS ON A 3/4 INLET LEAK LEAK LEAD LINE. RENEWED A 5/8 OUTLET FROM THE METER TO PROPERTY
201900178301 | 2019-02-01 | LEAD | 2618-16 | LEPAGE | N BROAD | WILK | PP-POOR PRESSURE ACCT#301123-703158 METER#A429422 **********J GILLIAM 11:37********** INLET SERVICE LEAK UNDERGROUND CAUSING VERY LOW PRESSURE ***16 PSI @ OUTSIDE FAUCET /** AT 2616: 1) MN: SN: 0023307, *TAP: SIZE: A LOC: 174 FEET FROM P LINE AT BROAD N, *MB: CODE: CFLT LOC: ON LEPAGE,174' FROM S.P.L. NO. BROAD ** AT 2618: 2) MN: A249199 SN: 0023307, *TAP: SIZE: B LOC: 19 FEET FROM P LINE AT CRETE, *MB: CODE: __ LOC: ON LEPAGE 21' FROM DIV PL CRETE 2' OUTSIDE PL 12' ****/ | 2019-02-04 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE THAT WAS CAUSING POOR PRESSURE BACKFILLED + DRESSED UP AREA
201900179601 | 2019-02-01 | LEAD | 1803 | A P TUREAUD AV |  | WILK | ML- METER LEAK METER# A406862 ACCT #122903-528181 EXAMINE INLET SERVICE FOR A LEAK @ PROPERTY LINE WITH CONSTANT REGISTRATION ON THE METER /** 1) MN: SN: 0060031, *TAP: SIZE: __ LOC: 0 FEET FROM P LINE AT , *MB: CODE: AEN1 LOC: 81FT FROM PL N ROMAN ON LONDON ****/ | 2019-02-20 | EXAMINED JOB FIND LEAK ON PROPERTY BACKFILLED AND CLEANED UP AREA
201900180701 | 2019-02-01 | LEAD | 1522 | MANDEVILLE |  | WMRE | METER BOX BURIED CUSTOMER STATES NEED WATER PLEASE RAISE TO GRADE AND SET A 5/8 METER LOCATION #306888 LOCATE, MARK BRING APT A TO GRADE /** 1) MN: A340912 SN: 0022928, *TAP: SIZE: A LOC: 163 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: AE LOC: 162FT FROM USPL ROBERTSON ON MANDEVILLE ****/ | 2019-02-17 | EXCAVATED IN THE 4 X 8 DRIVEWAY OVER 3/4 INCH INLET SERVICE PUT A 3/4 TEE AND SET 5/8 INCH METER BOX COMPLETE AND SET 5/8 METER AND 2 FT OF 3/4 INCH WATER TUBING ON THE OUTLET SERVICE BACKFILLED
201900180901 | 2019-02-01 | LEAD | 5801 | ABBEY DR | WOODLAND | WILK | ML- METER LEAK METER # A145256 ACCT # 231640-418057 **********1ST AM********** INLET SERVICE LEAK INSIDE METER BOX FLOODING AREA /** 1) MN: A145256 SN: 0142762, *TAP: SIZE: B LOC: 32 FEET FROM P LINE AT WOODLAND, *MB: CODE: ADM7 LOC: RES. 32' FROM DPL WOODLAND DR 3' INSIDE CURB ****/ | 2019-02-02 | EXAMINED AREA EXCAVATED OM INLET + OUTLET SERVICE ODSERVED LEAK ON INLET SERVICE REPAIRED LEAK REPLACED VROKEN HAND WHEEL BACKFILLED CLEANED AREA
201900184101 | 2019-02-02 | LEAD | 1897 | CRETE | TRAFALGAR | WILK | WM-LEAK IN SIDEWALK *********CHANGED FROM 3100 TRAFALGAR************ INLET LEAK IN THE METER BOX CAUSING THE METER BOX TO OVERFLOW. THE METER OI ON TRAFALGAR ST (C) /** 1) MN: B029668 SN: 0160851, *TAP: SIZE: B LOC: 33 FEET FROM P LINE AT ST BERNARD AVE, *MB: CODE: OOO LOC: ****/ | 2019-02-18 | ARRIVED AT ABOVE LOCATION EXCAVATED IN MUD PLOT FOUND 3/4 INCH METER BOX COCK LEAKING + MADE REPAIRS
201900184701 | 2019-02-02 | LEAD | 3334 | N DERBIGNY | DESIRE | WMTLK | ML- METER LEAK METER # A-409707 ACCT# 143973-431642 /** 1) MN: A336322 SN: 0086180, *TAP: SIZE: B LOC: 198 FEET FROM P LINE AT PIETY, *MB: CODE: CD LOC: 198' P.L. PIETY ****/ | 2019-02-17 | EXCAVATED 9 X 3 SIDEWALK MADE REPAIR ON OUTLET SERVICE LEAK BACKFILLED AND CLEANED THE AREA
201900185601 | 2019-02-02 | LEAD | 68 | FLAMINGO | GERANIUM LN | WILK | MI-C Y NO WATER METER#035963 ACCT#167401-513619 NO WATER ON THE INLET... CUSTOMER OUT OF WATER. JOB GIVEN TO A. LAGARDE /** 1) MN: B025224 SN: 0111344, *TAP: SIZE: B LOC: 83 FEET FROM P LINE AT CIRCLE, *MB: CODE: AGKY LOC: SIDE OF HOUSE 83FT FROM PL CIRCLE 3FT OUTSD PL ** 2) MN: C026397 SN: 0000000, *TAP: SIZE: C LOC: 5 FEET FROM P LINE AT FIRE HYDRANT, *MB: CODE: C LOC: ON FLAMINGO 5FT FROM DIV P/L FIRE HYDRANT 11FT ****/ | 2019-02-02 | ARRIVED ON JOB SITE EXAMINED CUSTOMER OUT OF WATER HOLE WAS ALREADY EXCAVATED FOUND COCK OFF GIVE CUSTOMER WATER LEFT JOB SAFE
201900187001 | 2019-02-03 | LEAD | 2318 | N ROBERTSON | SPAIN | WILK | ML- METER LEAK METER# A425496 ACCT# 120779-482205 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A313873 SN: 0053089, *TAP: SIZE: A LOC: 145 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: AFE2 LOC: ON NO. ROBERTSON,145' FROM L.R.P.L. MANDEVILLE ****/ | 2019-02-20 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING AN MADE REPIR MADE A 3 X 3 CONCRETE CUT BACKFILLED + DRESSED UP AREA
201900188801 | 2019-02-03 | LEAD/PLASTIC | 5972 | GEN DIAZ |  | WMTBG | LOCATIONID#168739-510629 METER#C027400 METER BELOW GRADE,RAISE /** 1) MN: C027400 SN: 0110633, *TAP: SIZE: C LOC: 56 FEET FROM P LINE AT POLK AVE, *MB: CODE: BDK LOC: 65FT FROM PL POLK IN LINE WITH S&W 5FT FRM CURB ****/ | 2019-02-12 | EXCAVATED IN MUD PLOT THROUGH TREE ROOOTS TO RAISE A 1" SERVICE UP TO GRADE BACKFILLED AND DRESS UP WITH RIVER SAND PLASTIC INLET & LEAD OUTLET
201900190001 | 2019-02-03 | LEAD | 731 | BARTHOLOMEW | DAUPHINE | WILK | WATER LEAK -INLET SERVICE. LEAK IS NOT VISIBLE (NON-SURFACING). LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. ***FOR HELP LOCATING THE LEAK CALL KEITH AT ECHOLOGICS: 504-722-3942*** /** 1) MN: A302175 SN: 0063646, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT DAUPHINE, *MB: CODE: AELO LOC: ON BARTHOLOMEW 75FT FROM LRPL DAUPHINE ****/ | 2019-06-15 | EXCAVATED IN THE STREET CUT 4 X 16 OVER 3/4 INCH INLET SERVICE FOUND LEAD LINE LEAKING REPLACE TAILPIECE 3/4 INCH 17 FT OF 3/4 INCH WATER TUBING BACKFILL
201900190101 | 2019-02-03 | LEAD | 724 | BARTHOLOMEW | DAUPHINE | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A219331 SN: 0012111, *TAP: SIZE: B LOC: 178 FEET FROM P LINE AT ROYAL, *MB: CODE: BELM LOC: ON BARTHOLOMEW 179FT FROM USPL OF ROYAL ****/ | 2019-04-24 | EXCAVATED INJ CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA ALSO REPLACED BROKEN 5/8 INCH METER BOX BOTTOM. JOB COMPLETE
201900190501 | 2019-02-03 | LEAD | 1714 | INDEPENDENCE | N DERBIGNY | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A327762 SN: 0084568, *TAP: SIZE: B LOC: 128 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: CDL LOC: ON INDEPENDENCE 127FT FROM DERBINGY N ****/ | 2019-03-04 | MADE 4 X 4 CUT IN SIDEWALK AND RELOCATED METER FROM GUTTER BOTTOM TO SIDEWALK RE[PLACED 5/8 CURB COCK AND 5/8 INCH WHEEL BACKFILLED AREA
201900190701 | 2019-02-03 | LEAD | 1742 | CLOUET | N ROMAN | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A274881 SN: 0084292, *TAP: SIZE: A LOC: 18 FEET FROM P LINE AT ROMAN N, *MB: CODE: CDLM LOC: ON CLOUET 18' FROM PL N ROMAN 7.5' OUTSIDE PL ****/ | 2019-03-05 | EXCAVATED IN MUD PLOT AND MADE REPAIR ON 3/4 INCH INLET SERVICE UNDERNEATH CURB AND REPLACED 5/8 INCH COCK COCK BACKFILLED AREA
201900190801 | 2019-02-03 | LEAD | 3135 | BURGUNDY | CLOUET | WILK | WATER LEAK -INLET SERVICE. LEAK IS NOT VISIBLE (NON-SURFACING). LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: A151888 SN: 0055665, *TAP: SIZE: B LOC: 262 FEET FROM P LINE AT CLOUET ISPL, *MB: CODE: ADN LOC: 262FT FROM ISPL CLOUET ****/ | 2019-04-09 | MADE 4 X 6 CUT IN BLACK TOP STREET AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BACKFILL AREA
201900191001 | 2019-02-03 | LEAD | 3501 | N RAMPART | GALLIER | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-03-08 | MADE 4 X 6 STREET CUT AND MADE REPAIRS ON 4 INCH WATER MAIN WITH REPAIR CLAMP BACKFILLED AREA
201900191601 | 2019-02-03 | LEAD | 2224 | PORT | N MIRO | WMTLK | WATER LEAK -METER. LEAK IS NOT VISIBLE (NON-SURFACING). LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: SN: 0093761, *TAP: SIZE: A LOC: 195 FEET FROM P LINE AT MIRO N, *MB: CODE: BEN2 LOC: ON PORT 200FT FROM PL OF N MIRO 7.5FT OUTSIDE PL ****/ | 2019-03-11 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900191701 | 2019-02-03 | LEAD | 3725 | DAUPHINE | PAULINE | WILK | WATER LEAK -INLET SERVICE. LEAK IS NOT VISIBLE (NON-SURFACING). LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: E003946 SN: 0159758, *TAP: SIZE: E LOC: 64 FEET FROM P LINE AT BURGUNDY, *MB: CODE: BDIP LOC: ON PAULINE 64FT FROM PL BURGUNDY 4FT. OUTSIDE PL ** 2) MN: E004810 SN: 0159758, *TAP: SIZE: CCCC LOC: 132 FEET FROM P LINE AT DAUPHINE, *MB: CODE: __ LOC: ON PAULINE 131' FROM PL DAUPHINE 6' OUTSIDE PL 3' THERE IS 1 MORE NOT LISTED. ****/ | 2019-06-16 | EXCAVTED IN THE 4 X 8 CUT IN THE SIDEWALK DUG BY HAND OVER 1 INCH INLET SERVICE PUT A STOP COCK ON INLET SERVICE IN HAD NO METER IN MANHOLE BACKFILL
201900193301 | 2019-02-04 | LEAD/PLASTIC | 126 | HARRISON AV | CATINA | WMBK | UNABLE TO CHANGE METER, CASING OVER CURB COCK. PLEASE REPAIR AND CHANGE METER A399220 LOC 156380 INSTALL NEW METER BOX CASING AND COVER ALSO CHANGE METER IN BRICK WALKWAY /** 1) MN: A292610 SN: 0093556, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT CATINA, *MB: CODE: CDL1 LOC: ON HARRISON AVE 62.5FT FROM PL OF CATINA 14FT OUT- ****/ | 2019-02-22 | EXCAVATED A 6 X 6 MUD PLOT / LIMESTONT CUT & RAISED METER BOX UP TO GRADE . ALSO CHANGED AND WATER METER . FOUND OUTLET SERVICE AS LEAD PIPE & INLET SERVICE AS PVC BACKFILLED JOB SITE *************OLD METER INFO************** METER:A399220 FAC:14104981 MAKE:HERSEY READ:855
201900197101 | 2019-02-04 | LEAD | 1476 | N GALVEZ | COLUMBUS | WMTLK | ML - METER LEAK MTR # B042761 ACCT # 130360-524161 *** METER IS LOCATED AT 2024 COLUMBUS*** EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER IN LOWLINE AREA /** 1) MN: B033214 SN: 0060053, *TAP: SIZE: B LOC: 86 FEET FROM P LINE AT GALVEZ N, *MB: CODE: BDH LOC: RES FRONT OF 2024 COLUMBUS 84FT FROM PL GALVEZ ****/ | 2019-02-16 | EXAMINE FOUND INLET WASHERS LEAK
201900197701 | 2019-02-04 | LEAD/PLASTIC | 6077 | WILDAIR DR | ROSARY DR | WILK | ML: METER LEAK ACCT#183491-504918 MTR#C029221 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: C025334 SN: 0134708, *TAP: SIZE: C LOC: 150 FEET FROM P LINE AT ROSARY DR, *MB: CODE: CD LOC: ON WILDAIR 150' FROM PL ROSARY DR 8' OUTSIDE PL 2' ****/ | 2019-02-25 | EXCAVATED IN MUD PLOT TO REPAIR INLET SERVICE LEAK BEHINE THE METER BOX FOUND PLASTIC ON OUTLET LEAD ON INLET DRES UP WITH RIVER SAND AND CLEAN UP
201900198001 | 2019-02-04 | LEAD/PLASTIC | 325 | BROADWAY | PRYTANIA | WILK | WM- LEAK BETWEEN SIDEWALK AND CURB INLET SERVICE LEAK BAD BLEEDER VALVE /** 1) MN: A158812 SN: 0014946, *TAP: SIZE: A LOC: 40 FEET FROM P LINE AT PRYTANIA, *MB: CODE: CD LOC: 43FT FROM RPL PRYTANIA ****/ | 2019-02-23 | MADE A 4 X 4 SIDEWALK CUT. EXCAVATED AND MADE REPAIS ON A 3/4 LEAD LINE INLET SERVICE LEAK. ALSO RAISED THE METER TO GRADE AND RENEWED THE OUTLET WITH PLASTIC.
201900198101 | 2019-02-04 | LEAD | 831 | MAZANT | DAUPHINE | WILK | ML-METER LEAK ACCT# 134504-428393 METER# A311634 INLET SERVICE LEAK /** 1) MN: A311634 SN: 0065272, *TAP: SIZE: A LOC: 239 FEET FROM P LINE AT DAUPHINE, *MB: CODE: BD LOC: ON MAZANT 239FT FROM PL DAUPHINE ****/ | 2019-02-17 | EXCAVATED 3 X 3 MUD PLOT MADE REPAIR ON INLET SERVICE LEAK BACKFILLED AND CLEANED THE AREA
201900198301 | 2019-02-04 | LEAD | 423 | ALABO | DOUGLAS | WMLK | MI- LEAK ON SIDEWALK EXAMINE WATER MAIN FOR LEAK ON SIDEWALK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-03-06 | EXCAVATED IN CONCRETE SIDEWALK BY HAND + MADE REPAIR ON ABANDONED 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201900200901 | 2019-02-04 | LEAD/PLASTIC | 8219 | APPLE | DUBLIN | WILK | ML-METER LEAK METER#A288049 ACCT#135166-591441 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A315161 SN: 0067907, *TAP: SIZE: A LOC: 133 FEET FROM P LINE AT DUBLIN, *MB: CODE: CDN LOC: 132FT FROM PL DUBLIN ****/ | 2019-02-22 | MADE A 2 X8 MUD CUT EXCAVATED AND MADE REPAIRS ON A 5/8" INLET SERVICE LEAK LEAD LINE PLASTIC OUTLET
201900201401 | 2019-02-04 | LEAD | 1817 | ST ROCH AV |  | WILK | ML METER LEAK ACCOUNT #130880-482863 METER #A367288 INLET SERVICE LEAK IN BOX /** 1) MN: A336057 SN: 0061095, *TAP: SIZE: A LOC: 140 FEET FROM P LINE AT ROMAN N, *MB: CODE: CDM1 LOC: ON ST. ROCH AVE.,137' FROM S.P.L. NO. ROMAN ****/ | 2019-02-20 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING AN MADE REPAIR .MADE 3 X 3 MUD CUT BACKFILLED DRESSED UP AREA UP ****************OLD METER INFO************* METER:A367288 FAC:70696503 MAKE:SENSUS READ:75136
201900204201 | 2019-02-05 | LEAD | 851 | TAFT PL | DUMAINE | WMTLK | ML-METER LEAK ACCT#140719-514213 METER#A314175 EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN MUDPLOT NEAR LARGE TREE, METER UNDER WATER /** 1) MN: A251532 SN: 0075878, *TAP: SIZE: B LOC: 197 FEET FROM P LINE AT DUMAINE, *MB: CODE: BD LOC: ON TAFT 200' FROM PL OF DUMAINE ****/ | 2019-02-18 | EXCAVATED 3 X 3 MUD PLOT THROUGH ROOTS REPLACED HANDWHEEL AND MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201900209401 | 2019-02-06 | LEAD | 600 | DUMAINE | CHARTRES | WMTLK | ML- METER LEAK MTR#A419693 ACCT#119120-528834 /** 1) MN: SN: 0000000, *TAP: SIZE: __ LOC: 15 FEET FROM P LINE AT CHARTRES, *MB: CODE: AEV LOC: ON DUMAINE, 11' FROM P.L. CHARTRES, 6' OUTSIDE,1' ** 2) MN: A254523 SN: 0030211, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT CHARTRES, *MB: CODE: BFR4 LOC: 3 APTS ON DUMAINE ST 54' USPL CHARTRES ST ****/ | 2019-02-14 | REPLACED WASHERS TO STOP LEAK
201900209901 | 2019-02-06 | LEAD | 1401 | LAFITTE |  | WMTLK | LOCATIONID#140966-525788 METER#A407432 LEAK INSIDE METERBOX /** 1) MN: A237958 SN: 0137995, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT MARAIS, *MB: CODE: AFK4 LOC: ON LAFITTE ST 63' FROM PL MARAIS ** 2) MN: SN: 0137995, *TAP: SIZE: B LOC: 35 FEET FROM P LINE AT ST PETER ON MARAIS, *MB: CODE: __ LOC: ON MARAIS 35' P.L. ST PETER ****/ | 2019-02-16 | EXCAVATED 3 X 2 SIDEWALK CUT MADE REPAIR ON INLET SERVICE LEAK BACKFILLED AND CLEANED THE AREA
201900210001 | 2019-02-06 | LEAD | 1511 | URSULINES AV |  | WMTLK | LOCATIONID#106934-485903 METER#A391253 LEAK INSIDE METERBOX /** 1) MN: A122815 SN: 0038958, *TAP: SIZE: A LOC: 80 FEET FROM P LINE AT VILLERE N, *MB: CODE: BELM LOC: ON URSULINES AVE 79.6' FROM PL N VILLERE ****/ | 2019-02-19 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900210101 | 2019-02-06 | LEAD | 1216 | N VILLERE |  | WMTLK | LOCATIONID#128021-526214 METER#A316909 METERBOX OVERFLOWING /** 1) MN: A128076 SN: 0041221, *TAP: SIZE: A LOC: 166 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: AFLM LOC: ON NO. VILLERE,165' FROM L.R.P.L. GOV. NICHOLLS ****/ | 2019-02-16 | EXCAVATED 3 X 3 MUD PLOT MADE REPAIR ON INLET SERVICE LEAK BACKFILLED AND CLEANED THE AREA
201900212801 | 2019-02-06 | LEAD | 636 | LIZARDI | ROYAL | WMTLK | WM-LEAK IN SIDEWALK **************DAMAGE CLAIM*************** CHANGED FROM 640 LIZARDI CRUSHED SERVICE BY AVANTAGADE CONSTRUCTION, CUSTOMER HAS WATER, HOUSE UNDER RENOVATION **JEFF WILLIAMS (504)914-4903 /** 1) MN: SN: 0062637, *TAP: SIZE: A LOC: 272 FEET FROM P LINE AT CHARTRES, *MB: CODE: ADK2 LOC: ON LIZARDI,270.7' FROM S.P.L. CHARTRES ****/ | 2019-04-18 | EXAMINED JOB AT ABOVE LOCATION AND FOUND NEW POURED SIDEWALK AND PLACE GRASS ON LAWN FOUND NO DAMAGED OR LEAK ALREADY COMPLETED. JOB COMPLETE
201900213001 | 2019-02-06 | LEAD | 432 | S RENDON |  | WMTLK | ML METER LEAK ACCOUNT #135112-532421 METER #A381252 EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN BOX /** 1) MN: A142532 SN: 0065906, *TAP: SIZE: B LOC: 157 FEET FROM P LINE AT BANKS, *MB: CODE: CDLM LOC: ON S RENDON,156.5' FROM U.P.L. BANKS ****/ | 2019-02-16 | EXCAVATED 2 X 4 CUT MADE REPAIR ON INLET SERVICE LEAK BACKFILLED AND CLEANE THE AREA
201900213401 | 2019-02-06 | LEAD | 2549 | COLUMBUS | N BROAD | WOLK | ML-METER LEAK***ACCT#124308-515320 ****METER NUMBER#A381228 OUTLET SERVICE LEAKING BEHIND HANDWHEEL IN SIDEWALK /** 1) MN: A215488 SN: 0044980, *TAP: SIZE: B LOC: 129 FEET FROM P LINE AT BROAD N, *MB: CODE: BDK5 LOC: 127FT FROM LRPL N BROAD ****/ | 2019-02-16 | EXCAVATED 4 X 2 SIDEWALK CUT MADE REPAIR ON OUTLET SERVICE LEAK BACKFILLED AND CLEANED THE AREA
201900213601 | 2019-02-06 | LEAD | 1011 | N ROCHEBLAVE | ST PHILIP | WILK | ML -METER LEAK***ACCT#114572-523750***METER#A371852 BAD BLEEDER VALVE INSIDE BOX ON SIDEWALK /** 1) MN: A133746 SN: 0016977, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT ST PHILIP, *MB: CODE: BFL LOC: 116' P.L. ST PHILIP ****/ | 2019-02-12 | EXCAVATED AND MADE REPAIRS ON 5/8 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND
201900213901 | 2019-02-06 | LEAD | 1309 | FRANKLIN AV |  | WOLK | ML-METER LEAK ACCT#145572-449595 METER#A254136 EXAMINE OUTLET SERVICE FOR LEAK NO VISIBLE STOP AND WASTE, CON REG /** 1) MN: A254136 SN: 0045137, *TAP: SIZE: C LOC: 117 FEET FROM P LINE AT URQUHART, *MB: CODE: ADNM LOC: ON ALMONASTER AVE., 85' FROM P.L. URQUHART ****/ | 2019-02-17 | EXCAVATED 3 X 3 MUD PLOT MADE REPAIR ON OUTLET SERVICE LEAK BACKFILLED AND CLEANED THE AREA
201900217401 | 2019-02-06 | LEAD/PLASTIC | 5509 | WILTON DR | RAPIDES DR | WMTBG | LOCATIONID#161718-719046 METER#A283332 METER BELOW GRADE,RAISE /** 1) MN: A259157 SN: 0100532, *TAP: SIZE: A LOC: 234 FEET FROM P LINE AT RAPIDES DR, *MB: CODE: BN2 LOC: 234FT FROM PL RAPIDES DR 10' OUTSIDE PL 3' INSIDE ****/ | 2019-02-26 | EXCAVATED A 3 X 6 MUDPLOT CUT AND RAISED 5/8" METER BOX TO GRADE . FOUND PVC OUTLET SERVICE & LEAD INLET SERVICE BACKFILLED JOB SITE
201900218301 | 2019-02-06 | LEAD | 940 | PICHELOUP PL |  | WMTLK | ML METER LEAK ACCT#146393-514944 METER#B036064 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: B020654 SN: 0078239, *TAP: SIZE: B LOC: 305 FEET FROM P LINE AT DUMAINE, *MB: CODE: BD LOC: ON PICHELOUP 305FT FROM PL OF DUMAINE ****/ | 2019-02-18 | EXCAVATED 5 X 2 MUD PLOT SET 3/4 INCH METER BOX COMPLETE ALSO RAISED METER TO GRADE METER WAS MOVED CLOSER TO SIDEWALK TO OREVENT CUSTOMER FROM ROLLING ON TOP AND PARKING ON IT BACKFILLED AND CLEANEDTHE AREA
201900218401 | 2019-02-06 | LEAD | 1530 | MANDEVILLE | N CLAIBORNE AV | WILK | MI: LEAK IN THE STREET INLET SERVICE LEAK IN STREET /** 1) MN: A329137 SN: 0062095, *TAP: SIZE: A LOC: 102 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: AE3 LOC: 102 FT FROM PL OF N CLAIBORNE AVE. ****/ | 2019-02-25 | MADE 8 X 8 CUT IN CONCRETE STREET AND REPLACED 5/8 INCH TAILPIECE BACKFILLED AREA OVER 6 INCH WATER MAIN JOB COMPLETE
201900219201 | 2019-02-06 | LEAD | 1500 | FLOOD | ROBERTSON | WMLK | WM - LEAK IN THE STREET BROKEN WATER MAIN IN THE STREET FLOODING STREET, GETTING OFF IN THE DCB. ***PER INS J HILL ( B ) LEAVE IN SYSTEM /** 1) MN: A232457 SN: 0100317, *TAP: SIZE: B LOC: 20 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: CD LOC: ON FLOOD 20FT FROM ROBERTSON N ****/ | 2019-02-07 | MADE REPAIR ON 4 INCH WATER MINE FIXED WITH 4 INCH CLAMP BACKFILLED + CLEANED UP AREA 10X20 STREET CUT BACK HOLE (JOB COMPLETE)
201900220401 | 2019-02-06 | LEAD | 1915 | ARTS | N JOHNSON | WILK | ML-METER LEAK ACCT # 138807-483476 **METER #A360299 INLET SERVICE LEAK IN METER BOX /** 1) MN: A269211 SN: 0069373, *TAP: SIZE: A LOC: 127 FEET FROM P LINE AT PRIEUR N, *MB: CODE: AE LOC: ON ARTS, 127' FROM P.L. NO. PRIEUR ****/ | 2019-02-25 | EXAMINED AND PUMPED INSIDE METER BOX DOWN AND REPLACED 5/8 WASHERS ON INLET AND OUTLET
201900220501 | 2019-02-06 | LEAD | 2624 | DAUPHINE | PORT | WOLK | **********PICK UP********** OUTLET SERVICE LEAK IN A CONCRETE SIDEWAK, WITH CONSTANT REGISTRATION ON THE METER /** 1) MN: A272770 SN: 0047689, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT PORT, *MB: CODE: BEN LOC: 76FT FROM URPL PORT ****/ | 2019-02-25 | MADE 4 X6 SIDEWALK CUT AND MADE REPAIRS ON 3/4 INCH OUTLET SERVICE BACKFILLED AREA
201900221501 | 2019-02-07 | LEAD/PLASTIC | 4722 | CLEVELAND AV | S BERNADOTTE | WILK | LEAK IN STREET /** 1) MN: A284555 SN: 0045317, *TAP: SIZE: B LOC: 146 FEET FROM P LINE AT BERNADOTTE S, *MB: CODE: CELM LOC: 146FT FROM URPL BERNADOTTE S ****/ | 2019-02-06 | EXCAVATED A 9 X 11 CONCRETE STREET CUT AND MADE REPAIRS ON THE INLET SERVICE. PLASTIC ON THE OUTLET SERVICE BACKFILL AND CLEAN UP.
201900224501 | 2019-02-07 | LEAD | 820 | ANDRY |  | WMRE | LOCATION: 306896 INSP UDUEBOR UNABLE TO LOCATE METER BOX. PLEASE LOCATE, RAISE AND SET A METER. NEW CONSTRUCTION LOCATE, MARK, AND SET METER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-22 | ARRIVED AT ABOVE LOCATION TO LOCATED A 5/8 INCH METER AND RASIED TO GRADE AND LEFT A 3/4 INCH OUTLET WHIP METER WAS FOUND AT 142 FT FROM DAUPHINE ST
201900224601 | 2019-02-07 | LEAD | 1726 | TRICOU | N DERBIGNY | WMTLK | ML: METER LEAK ACCT#168223-724027 MTR# A428160 EXAMINE INLET AND OUTLET SERVICE FOR LEAK, METER UNDER WATER /** 1) MN: A114173 SN: 0125579, *TAP: SIZE: A LOC: 198 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: DLM LOC: RES ON TRICOU 198FT FROM PL DERBIGNY 7' OUTSIDE PL ****/ | 2019-02-22 | ARRIVED AT ABOVE LOCATION PUMP DOWN GUTTER BOTTOM TO LOCATE AT 5/8 INCH METER FIND A 5/8 INCH INLET SERVICE WASHER LEAKING MADE REPAIR CARS ROLLING OVER METER BACKFILLED + CLEAN UP AREA
201900225101 | 2019-02-07 | LEAD | 1630 | ST ROCH AV | N CLAIBORNE AV | WILK | MI- LEAK ON SIDEWALK INLET SERIVCE LEAK IN THE SIDEWALK /** 1) MN: 000000 SN: 0070863, *TAP: SIZE: A LOC: 251 FEET FROM P LINE AT CLAIBORNE AV N, *MB: CODE: BDN2 LOC: 251' P.L. N CLAIBORNE AV ****/ | 2019-03-08 | MADE 4 X 4 CUT IN SIDEWALK AND MADE REPAIRS ON 3/4 INCH INLET SERVICE AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201900229801 | 2019-02-08 | LEAD | 835-37 | ELYSIAN FIELDS AV |  | WILK | ML- MEATER LEAK METER# C018988 ACCT# 168609-581624 CHANGED FROM 2222 BURGUNDY INLET ON ABANDON SERVICE ON SIDEWALK /** AT 837: 1) MN: SN: 0046450, *TAP: SIZE: A LOC: 49 FEET FROM P LINE AT BURGUNDY, *MB: CODE: __ LOC: 49' P.L. BURGUNDY ****/ | 2019-02-18 | EXCAVATED 3 X 2 DRIVEWAY CUT MADE REPAIR ON INLET SERVICE LINE + REPLACED METER COCK BACKFILED AND CLEANED THE AREA
201900230101 | 2019-02-08 | LEAD | 1401 | ANNETTE |  | WILK | LOCATION: 124789 MTR# A-436870 INSP UDUEBOR STATES INLET SERVICE NEED REPAIRS, BAD BLEEDER VALVE. EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A299086 SN: 0046929, *TAP: SIZE: A LOC: 59 FEET FROM P LINE AT ANNETTE, *MB: CODE: BDH3 LOC: ON NO. VILLERE,56.6' FROM L.S.P.L. ANNETTE ****/ | 2019-02-28 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201900230801 | 2019-02-08 | LEAD | 1561 | N MIRO | LAHARPE | WILK | ML: METER LEAK ACFT#153458-488918 MTR#A345047 EXAMINE INLET SERVICE FOR LEAK IN MUDPLOT NEAR METER /** 1) MN: A117081 SN: 0069866, *TAP: SIZE: A LOC: 138 FEET FROM P LINE AT LAHARPE, *MB: CODE: ADMN LOC: ON NO. MIRO,140.4' FROM P.L. LAHARPE,11' OUTSIDE ****/ | 2019-02-25 | EXCAVATED 3 X 2 MUD PLOT REPLACE METER BOX COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900230901 | 2019-02-08 | LEAD | 3012 | GRAND RTE ST JOHN | SAUVAGE | WILK | ML-METER LEAK MTR#A266600 ACC#121065-490782 INLET SERVICE LEAK IN BOX IN CONCRETE SIDEWALK /** 1) MN: A266600 SN: 0037689, *TAP: SIZE: A LOC: 242 FEET FROM P LINE AT DUPRE N, *MB: CODE: AFK2 LOC: ON GRAND ROUTE ST. JOHN,242' FROM U.S.P.L. ****/ | 2019-02-26 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900231001 | 2019-02-08 | LEAD | 2222 | PAINTERS |  | WILK | LOCATION: 179141 INSP UDUEBOR STATES AREA IS FLOODED, METER UNDER WATER. PLEASE REPAIR AND CHANGE MTR# A 404690 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A284490 SN: 0059181, *TAP: SIZE: A LOC: 178 FEET FROM P LINE AT MIRO N, *MB: CODE: CDM2 LOC: ON PAINTERS 177' FROM PL N MIRO 7' OUTSIDE PL ****/ | 2019-03-06 | MADE 4 X 4 SIDEWALK CUT AND MADE REPAIRS ON 3/4 INCH INLET SERVICE ALSO REPLACED 5/8 INCH METER THAT WAS IN BACKWARDS SET NEW 5/8 INCH METER BAKFILLED AREA OLD METER INFO: A404690 FACT: 14110452 MAKE: HERSEY READ: 960
201900231901 | 2019-02-08 | LEAD | 1614 | REYNES |  | WILK | LOCATION: 172900 INSP UDUEBOR STATES INLET SERVICE LEAKING BEHIND CURB COCK. PLEASE REPAIR AND CHANGE MTR# A 359058 INLET SERVICE LEAK IN BOX ON SIDEWALK /** 1) MN: A151110 SN: 0116365, *TAP: SIZE: A LOC: 97 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: AEL LOC: RES ON REYNES 97' PL N CLAIBORNE AV IN LINE WITH ****/ | 2019-02-21 | EXCAVATED 3 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900232001 | 2019-02-08 | LEAD | 1240 | REYNES |  | WOLK | LOCATION: 163336 INSP UDUEBOR STATES WHEEL IS BROKEN. PLEASE REPAIR AND CHANGE MTR# A 259515 BROKEN HANDWHEEL ALSO CHANGE METER /** 1) MN: A259515 SN: 0102747, *TAP: SIZE: A LOC: 18 FEET FROM P LINE AT REYNES, *MB: CODE: ADH LOC: ON URQUHART, 18' FROM P.L. REYNES, 6' OUTSIDE P.L. ****/ | 2019-02-21 | EXCAVATED 3 X 2 MUD PLOT REPLACE BROKEN HANDWHEEL AND METER BACKFILLED AND CLEANED THE AREA OLD METER INFO: A259515 FACT:38395258 MAKE: ROCKWELL READ: 139
201900232301 | 2019-02-08 | LEAD | 2619 | N VILLERE | ALMONASTER AV | WILK | MI- LEAK ON SIDEWALK **FLOODING AREA** EXAMINE INLET SERVICE FOR LEAK ON SIDEWALK /** 1) MN: SN: 0059529, *TAP: SIZE: A LOC: 136 FEET FROM P LINE AT ALMONASTER AV, *MB: CODE: CDLN LOC: 136' P.L. ALMONASTER AV ****/ | 2019-03-06 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201900232401 | 2019-02-08 | LEAD | 1931 | MARIGNY | N JOHNSON | WILK | ML- METER LEAK METER# A329318 ACCT # 124723-483328 ***FLOODING AREA*** BAD BLEEDER VALVE IN BOX /** 1) MN: A345550 SN: 0046127, *TAP: SIZE: A LOC: 90 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CD LOC: ON MARIGNY 88.5' FROM LRPL N JOHNSON ****/ | 2019-02-28 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA
201900237901 | 2019-02-08 | LEAD | 8000 | BERG |  | WMTBG | LOCATIONID#164463-465993 METER#A156197 METER BELOW GRADE,RAISE /** 1) MN: A156197 SN: 0137517, *TAP: SIZE: B LOC: 12 FEET FROM P LINE AT HYDT #2, *MB: CODE: CDL LOC: FRONT 12FT FROM PL HYDT 2 7FT OUTSIDE ****/ | 2019-03-01 | EXCAVATED IN MUDPLOT RIASE METETRBOX TO GRADE OUTLET PLASTIC AND INLET LEAD BACKFILL DRESS UP WITH SAND.
201900240701 | 2019-02-08 | LEAD | 4320 | BURGUNDY |  | WOLK | ML- METER LEAK METER # A232913 ACCT #140753-428878 INLET LEAK IN SIDEWALK FLOODING SIDEWALK /** 1) MN: A270817 SN: 0062299, *TAP: SIZE: A LOC: 160 FEET FROM P LINE AT LESSEPS, *MB: CODE: CFL LOC: ON BURGUNDY 160' FROM PL OF LESSEPS ****/ | 2019-04-22 | EXAMINE JOB AT ABOVE LOCATION FOUND NO LEAK ON INLET OR OUTLET WASHERS
201900242201 | 2019-02-08 | LEAD | 4998 | MONTEGUT |  | WMTBG | LOCATIONID#169124-468898 METER#A234138 CASING BELOW GRADE,RAISE /** 1) MN: A234138 SN: 0111450, *TAP: SIZE: A LOC: 750 FEET FROM P LINE AT MIRABEAU AVE, *MB: CODE: ADL LOC: 750FT MIRABEAU AV 6' OUTSIDE 7' INSIDE CURB ****/ | 2019-02-27 | EXCAVATED IN MUDPLOT ALSO RAISE TO GRADE LEAD ON INLET AND PLASTIC ON OUTLET BACKFILL JOB COMPLETE
201900247101 | 2019-02-10 | LEAD | 1665 | PAUL MORPHY | ONZAGA | WOLK | WM-LEAK IN SIDEWALK ***********1ST AM*********** EXAMINE OUTLET SERVICE LEAK IN SERVICE CUT, AREA FLOODED.....FOUND ONE ( 1 ) BARREL UPON ARRIVAL /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-11 | EXCAVATED AND MADE REPAIRS ON PUTLET SERVICE AT PROPERTY BACKFILLED JOB WITH RIVERSAND COLDMILL JOB COMPLETE
201900250001 | 2019-02-11 | LEAD | 4343 | WERNER DR | CHEF MENTEUR HW | WILK | PP-POOR PRESSURE ACCT#177656-444607 METER#B037646 INLET SERVICE LEAKING FROM BLEEDER VALVE IN BOX IN MUDPLOT /** 1) MN: B021174 SN: 0132350, *TAP: SIZE: B LOC: 345 FEET FROM P LINE AT CHEF MENTEUR HWY, *MB: CODE: ADN LOC: RES ON WERNER 345FT PL CHEF MENTEUR HW 9' OUTSIDED ****/ | 2019-02-26 | HAND DUG IN MUDPLOT FOUND LEAD ON INLET AND OUTLET. RENEWED OUTLET WITH 6FEET OF PLASTIC. CUT LEAD TO CURB WITH 4FEET OF PLASTIC WITH PACK JOINT AND STOP COCK ON INLET. ALSO RAISED TO GRDE WITH 3/4 METER BOX COMPLETE. BACKFILLED WITH 1 YARD OF RIVER SAND.
201900252401 | 2019-02-11 | LEAD | 924 | PICHELOUP PL | DUMAINE | WILK | **********PICK UP********** INLET SERVICE LEAK IN THE MUD PLOT CARS ROLLING OVER METER /** 1) MN: A304157 SN: 0072468, *TAP: SIZE: B LOC: 177 FEET FROM P LINE AT DUMAINE, *MB: CODE: CD LOC: ON PICHELOUP PL 177' FROM PL OF DUMAINE ****/ | 2019-02-26 | EXCAVATED 4 X 4 SIDEWALK CUT RELOCATED FROM MUD PLOT TO SIDEWALK BACKFILLED AND CLEANED THE AREA
201900254001 | 2019-02-11 | LEAD | 2855 | ALLEN | AGRICULTURE | WOLK | WM: LEAK ON SIDEWALK CUSTOMER STATES LEAK HAS GOTTEN WORSE EXAMINE OUTLET SERVICE FOR LEAK, PREVIOUS REPAIRED /** 1) MN: A244891 SN: 0104999, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT INDUSTRY, *MB: CODE: CDN1 LOC: ON ALLEN 130FT PL INDUSTRY 7' OUTSIDE ****/ | 2019-03-04 | EXAMINE JOB AT ABOVE LOCATION FOUND LEAK COMING FUTHER BACK ON PROOERTY REFER TO CUSTOMER FOR (P.O.P) TO HAVE PLUMMER
201900254101 | 2019-02-11 | LEAD | 3113 | ST ANN |  | WILK | PP POOR PRESSURE ACCOUNT #304609-588210 METER #A428006 EXAMINE INLET SERVICE FOR LEAK, HOUSE UNDER RENOVATION 02/19/19 LEAK CAUSING POOR PRESSURE PER SR#12867635 (AJR) /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-21 | EXAMINE AND FOUND NO LEAK CLEAN UP AREA
201900254801 | 2019-02-11 | LEAD | 1841 | GENTILLY BL |  | WILK | ML-- METER LEAK METER# A210855 ACCT# 147209-492852 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A296586 SN: 0061001, *TAP: SIZE: A LOC: 16 FEET FROM P LINE AT CASTIGLIONE, *MB: CODE: OOO LOC: 33' P.L. CASTIGLIONE ****/ | 2019-02-25 | EXCAVATED 5 X 3 MUD PLOT MADE REPAIR ON INLET SERVICE LINE AND REPLACED METER COCK BACKFILLED AND CLEANED THE AREA
201900256201 | 2019-02-11 | LEAD | 200 | N JEFFERSON DAVIS PK | IBERVILLE | WILK | ML- METER LEAK MTR # A387693 ACCT # 103598-519066 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A268316 SN: 0006420, *TAP: SIZE: A LOC: 14 FEET FROM P LINE AT IBERVILLE LRPL, *MB: CODE: M6 LOC: 14' FROM LRPL IBERVILLE ****/ | 2019-02-25 | EXCAVATED 3 X 2 MUD PLOT MADE ON INLET SERVICE LINE ON SECOND METER BOX BACKFILLED AND CLEANED THE AREA *NO METER INSIDE 2ND METER BOX* JOB COMPLETE
201900256801 | 2019-02-11 | LEAD | 2744 | ORCHID | CRETE | WILK | ML-METER LEAK METER#A323841 ACCT3141478-727527 INLET SERVICE LEAK /** 1) MN: A323841 SN: 0072517, *TAP: SIZE: B LOC: 86 FEET FROM P LINE AT CRETE, *MB: CODE: BDN6 LOC: ON ORCHARD, 87' FROM L.P.L. CRETE ****/ | 2019-02-18 | EXCAVATED 4 X 2 SIDEWALK CUT REPLACED METER COCK TO STOP LEAK BACKFILLED ND CLEANED THE AREA
201900258402 | 2019-03-07 | LEAD | 1421 | GALLIER | VILLERE | WOLK | EXAMINED JOB AT ABOVE LOCATION AND FOUND AREA FLOOD UNABLE TO GET BLACK GMC YUKON AND BLACK INPALA MOVE TO CHECK JOB SITE /** 1) MN: A217045 SN: 0065815, *TAP: SIZE: A LOC: 166 FEET FROM P LINE AT VILLERE N, *MB: CODE: BDK5 LOC: ON GALLIER 166'FROM L S P L VILLERE ****/ | 2019-03-12 | EXAMINED JOB AT ABOVE LOCATION FOUND NO LEAK ON INLET OR OUTLET
201900260501 | 2019-02-12 | LEAD | 2455 | DESLONDE |  | WMTBG | LOCATIONID#184210-422980 METER#A289232 METER BURIED,LOCATE & RAISE /** 1) MN: A251122 SN: 0136428, *TAP: SIZE: B LOC: 24 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: AD LOC: RES 24FT P/L N.DORGENOIS 7' OUTSIDE ****/ | 2019-02-21 | EXCAVATED 4 X 3 MUD PLOT RAISED METER BOX TO GRADE BACKFILLED AND CLEANED THE AREA METER WAS REPLACED DUE TO IT NOT REGISTERING ***********OLD METER INFO********** METER:A289232 FAC:49138826 MAKE:SENSE READING:914
201900260801 | 2019-02-12 | LEAD | 2528 | CONTI |  | WMTBG | LOCATIONID#174502-523474 METER#A374723 METER BURIED,LOCATE & RAISE /** 1) MN: SN: 0055505, *TAP: SIZE: A LOC: 229 FEET FROM P LINE AT NO. ROCHEBLAVE, *MB: CODE: BDKL LOC: ON CONTI, 228' FROM P.L. NO. ROCHEBLAVE, 9' OUT- ****/ | 2019-02-23 | EXCAVATED TO FIND A 3/4 INCH INLET SERVICE MADE REPAIRS WHERE THE LEAK WAS FOUND AND RAISED TO GRADE
201900261801 | 2019-02-12 | LEAD | 1227 | ST ANTHONY AV |  | WMTLK | ML METER LEAK ACCOUNT #118856-486649 METER #A409988 EXAMINE INLET & OUTLET SERVICE FOR A LEAK UNABLE TO VERIFY LEAK METER UNDER WATER DUE TO RAIN /** 1) MN: A273497 SN: 0049514, *TAP: SIZE: A LOC: 145 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: BF25 LOC: 145' P.L. ST CLAUDE AVE ****/ | 2019-03-08 | EXCAVATED 3 X 2 MUD PLOT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900263101 | 2019-02-12 | LEAD | 2009 | PORT |  | WOLK | ML METERLEAK MTR#A431725 LOC/CUST#207987-705544 CONS REG ON METER /** 1) MN: A296853 SN: 0073471, *TAP: SIZE: A LOC: 3 FEET FROM P LINE AT NO. GALVEZ, *MB: CODE: OOO LOC: ON PORT, 4' FROM D.P.L. NO. GALVEZ, 8' OUTSIDE, 4' ****/ | 2019-03-11 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX AT ABOVE LOCATION
201900263601 | 2019-02-12 | LEAD | 3708 | LOUISIANA AV PK | S DORGENOIS | WILK | ML METER LEAK ACCOUNT #147071-552060 METER #C034299 EXAMINE INLET SERVICE FOR LEAK BEHIND CURB COCIK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ DOTTIE READY 4-10-19 EXP 4-30-19 | 2019-04-27 | CHANGED 1"METER BOX COCK.
201900264601 | 2019-02-12 | LEAD | 2129 | GORDON | N MIRO | WILK | WM- LEAK IN THE STREET INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A327579 SN: 0128584, *TAP: SIZE: A LOC: 211 FEET FROM P LINE AT NO. GALVEZ, *MB: CODE: CDMN LOC: ON GORDON, 211' FROM P.L. NO. GALVEZ, 8' OUTSIDE ****/ | 2019-04-01 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA (NO METER) JOB COMPLETE
201900265401 | 2019-02-12 | LEAD | 809 | DUMAINE |  | WILK | PP- POOR PRESSURE ACCT# 133072-529232 MTR# A372758 INLET SERVICE LEAKING UNDERGROUND CAUSING POOR PRESSURE /** 1) MN: A234855 SN: 0008519, *TAP: SIZE: B LOC: 57 FEET FROM P LINE AT BOURBON, *MB: CODE: CE5 LOC: ON DUMAINE ST 60' FROM PL BOURBON ****/ | 2019-03-07 | EXCAVATED 5 X 2 SIDEWALK BRICK TILE MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201900267701 | 2019-02-13 | LEAD | 353 | BARONNE |  | WMTBG | ACCOUNT #170600 METER #D4997 PLEASE LOCATE AND RAISE METER TO GRADE /** 1) MN: SN: 0000000, *TAP: SIZE: H LOC: 85 FEET FROM P LINE AT BARONNE, *MB: CODE: AERH LOC: ON PERDIDO 86' FROM LSPL OF BARONNE ** 2) MN: SN: 0002333, *TAP: SIZE: B LOC: 32 FEET FROM P LINE AT PERDIDO, *MB: CODE: __ LOC: THERE IS 1 MORE NOT LISTED. ****/ | 2019-03-18 | EXCAVATED 4 X 1 SIDEWALK CUT UNABLE TO LOCATE METER AT THIS LOCATION BACKFILLED AND CLEANED THE AREA JOB CONTINUED
201900268001 | 2019-02-13 | LEAD | 2302 | ORLEANS AV |  | WMTBG | ACCOUNT #220350-526812 METER #B35293 PLEASE LOCATE AND RAISE METER TO GRADE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-24 | LOCATED METER ON BACK ST PETER STREET COURT BACK OF ABOVE ADDRESS MARK METER WITH BLUE PAINT. JOB COMPLETE
201900269001 | 2019-02-13 | LEAD | 2804 | CONTI | WHITE | WMTLK | ML MTR# A281823 LOC & CUST# 126050-427815 SERVICE ADDRESS: 2804 CONTI ST. INSP COMM: F/ON-L/ON (OCC) NO CONS REG. NO LKS AT OR AROUND METER, UNABLE TO TELL IF MTR REG PROP. NO VISIBLE FAUCET RD. 6002 /** 1) MN: A281823 SN: 0050912, *TAP: SIZE: A LOC: 46 FEET FROM P LINE AT WHITE N, *MB: CODE: CDLM LOC: 45FT FROM PL N WHITE ****/ | 2019-03-08 | EXCAVATED 4 X 4 MUD PLOT FOUND NO LEAK ON INLET OR OUTLET RAISE METER BOX UP TO GRADE BACKFILLED JOB WITH RIVERSAND
201900269302 | 2019-03-26 | LEAD | 1436 | ARTS | N ROBERTSON | WILK | INLET SERVICE LEAK IN THE MUD PLOT EXCAVATED 2 X 4 GUTTER BOTTOM MUD PLOT FOUND LEAK COMING FUTHER BACK UNDER ABANDON CAR BACKFILL JOB WITH RIVERSAND REFER TO ZONE 4 FOR A MACHINE /** 1) MN: A341279 SN: 0052991, *TAP: SIZE: A LOC: 274 FEET FROM P LINE AT VILLERE N, *MB: CODE: AD1 LOC: ON ARTS ST 273.5' FROM PL N VILLERE ****/ | 2019-03-30 | EXCAVATED 3 X 2 MUD PLOT REPLACED 5;/8 INCH COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900270101 | 2019-02-13 | LEAD | 1919 | FRENCHMEN | N JOHNSON | WILK | ML-METER LEAK ACCT#118506-494493 METER#A145450 INLET SERVICE LEAK IN THE SIDEWALK /** 1) MN: A145450 SN: 0002812, *TAP: SIZE: A LOC: 139 FEET FROM P LINE AT PRIEUR N, *MB: CODE: BFK5 LOC: 142' P.L. N PRIEUR ****/ | 2019-03-04 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900271001 | 2019-02-13 | LEAD | 1725 | LESSEPS |  | WILK | ML--METER LEAK METER # B032832 ACCT# 178940-719796 EXAMINE INLET SERVICE FOR ALEAK CARS ROLLING OVER METER /** 1) MN: B032832 SN: 0124973, *TAP: SIZE: B LOC: 194 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: CDK7 LOC: ON LESSEPS 194'P L N DERBIGNY 6' OUTSIDE ****/ | 2019-03-22 | EXCAVATED IN MUD PLOT + REPLACED 3/4 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900272001 | 2019-02-13 | LEAD | 2760 | ST ANN | N WHITE | WILK | WM-LEAK IN SIDEWALK EXAMINE INLET SERVICE FOR LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-03-08 | EXAMINED JOB AT ABOVE LOCATION FOUND NO LEAK
201900272101 | 2019-02-13 | LEAD | 0 | FORSTALL | N TONTI | WOLK | PER LEWIS UDUEBOR METER BOX IS BURIED PLEASE RAISE TO GRADE AND CHANGE METER C-24503 LOCATION#177894 ********METER LOCATION*****(SWB PUMBING STATION) ON FORSTALL 2FT PL OF N TONTI 6FT OUTSIDE PL *************B LEAVE IN SYSTEM************ INSTALL HANDWHEEL AND SET METER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-03-05 | EXCAVATED IN MUD PLOT + LOCATED METER BOX RE-PLACED BROKEN 5/8 INCH HANDWHEEL + SET 5/8 INCH METER
201900273101 | 2019-02-13 | LEAD | 3325 | IBERVILLE |  | WILK | ML-- METER LEAK METER# A399631 ACCT# 125317-519245 INLET SERVICE LEAK IN METER BOX IN THE MUD PLOT NEAR UTILITY POLE /** 1) MN: A335781 SN: 0050962, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT JEFF DAVIS PKWY N, *MB: CODE: ADN3 LOC: ON IBERVILLE,95' FROM L.R.P.L. HAGAN AVE. ****/ | 2019-02-23 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO AMKE THE REPAIRS JOB COMPLETE
201900273201 | 2019-02-13 | LEAD | 3301 | IBERVILLE | N RENDON | WMLK | **********PICK UP********** LEAK ON WATER MAIN IN THE SIDEWALK ON THE CONTROLLING LINE NEAR UTILITY POLE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-23 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO MAKE THE REPAIRS
201900274901 | 2019-02-13 | LEAD | 1545 | DESIRE | N CLAIBORNE AV | WOLK | MI- CONS ON METER METER # A-419766 ACCT # 221705-713523 /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-03-06 | EXCAVATED IN MUD PLOT AND REPLACED BROKEN 5/8 BOTTOM WITH NEW ONE BACKFILLED AREA
201900275101 | 2019-02-13 | LEAD | 921 | FLOOD | BURGUNDY | WMTLK | MI- METER LEAK MTR # A-431360 ACCT #304238-503229 /** 1) MN: A243802 SN: 0120994, *TAP: SIZE: A LOC: 161 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CD LOC: ON FLOOD 159FT FROM PL BURGUNDY 7' OUTSIDE PL ****/ | 2019-02-27 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 ICH CURB COCK BACKFILLED AREA
201900276701 | 2019-02-14 | LEAD | 3016 | GRAND RTE ST JOHN |  | WILK | ML METER LEAK ACCOUNT #103906-522241 METER #A406187 EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX METER BEHIND FENCE /** 1) MN: A221771 SN: 0056728, *TAP: SIZE: A LOC: 269 FEET FROM P LINE AT GRAND RTE ST JOHN, *MB: CODE: CFLM LOC: 269FT FROM LSPL OF GRAND RTE ST JOHN ****/ | 2019-03-26 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INJLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900276901 | 2019-02-14 | LEAD | 1524 | BASIN | PHILIP | WILK | WM- LEAK IN THE STREET EXAMINE INLET SERVICE FOR A LEAK ON AN ABANDON SERVICE IN THE SIDEWALK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-03-13 | EXCAVATED 5 X 3 SIDEWALK CUT ALSO REMOVED 2 FT OF THE CURB MADE REPAIR ON 1 INCH ABANDONED INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA *NO METER AT THIS ADDRESS* JOB COMPLETE
201900277601 | 2019-02-14 | LEAD | 1437 | PORT |  | WILK | LOCATION: 118218 METER WAS REMOVED 2/13/19 INSP D. JOHNSON STATES THERE IS A LEAK COMING FROM CURB COCK. PLEASE REPAIR. INLET SERVICE LEAK IN THE MUD PLOT INSIDE METER BOX /** 1) MN: A303486 SN: 0056043, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: CFLM LOC: 63' P.L. N ROBERTSON ****/ | 2019-02-28 | MADE 4 X 4 CUT IN SIDEWALK AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA
201900277701 | 2019-02-14 | LEAD | 1458 | MARAIS |  | UNKN | LOCATION: 116044 INSP D. JOHNSON STATES THERE IS CEMENT IN METER BOX. PLEASE REMOVE CEMENT AND METER A-412756 REMOVE CONCRETE OUT OF METER BOX /** 1) MN: A313765 SN: 0020765, *TAP: SIZE: A LOC: 123 FEET FROM P LINE AT KERLEREC, *MB: CODE: CFLM LOC: 123' P.L. KERLEREC ****/ | 2019-03-13 | REMOVE CEMENT FROM INSIDE OF METER BOX
201900278001 | 2019-02-14 | LEAD/PLASTIC | 3318 | S SARATOGA | LOUISIANA AV | WMTLK | ********************PICKUP********************** EXAMINE INLET AND OUTLET SERVICE FOR LEAK INSIDE MANHOLE, FLOODING SIDEWALK AND GUTTER /** 1) MN: D004659 SN: 0086340, *TAP: SIZE: D LOC: 112 FEET FROM P LINE AT TOLEDANO, *MB: CODE: AEM7 LOC: ON SARATOGA 115FT PL TOLEDANO 3' OUTSIDE ****/ DOTTIE 2-20-19 EXP 3-12-19 | 2019-03-10 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 1 1/2 OUT-LET UNION LEAKIG ALSO 1 1/2 CURB COCK BAD REPLACED 1 1/2 CURB COCK AND TWO 1 1/2 BRASS UNION,S AND 5FT. OF 1 1/2 TUBING TIED INTO LEAD.(SOC 4FT .X 5 FT .MUD-PLOT)
201900280201 | 2019-02-14 | LEAD | 2224 | MARAIS | ELYSIAN FIELDS AV | WMTLK | **********PICK UP********** EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER & SIDEWALK /** 1) MN: A296969 SN: 0047942, *TAP: SIZE: A LOC: 98 FEET FROM P LINE AT MARIGNY, *MB: CODE: CEN LOC: ON MARAIS,98.4' FROM U.R.P.L. MARIGNY ****/ | 2019-03-08 | REMOVED WATER FROM FLOODED AREA EXAMINE METER AND FOUND NO LEAK NO CONSTRANT REGISTRATION
201900280401 | 2019-02-14 | LEAD | 1938 | GEN PERSHING |  | WILK | ML-METER LEAK ACCT#101096-553794 MTR#A336160 INLET SERVICE LEAK BEHIND CURB COCK /** 1) MN: A336160 SN: 0004210, *TAP: SIZE: B LOC: 98 FEET FROM P LINE AT URPL GEN PERSHING, *MB: CODE: BDK2 LOC: 98 FT. FROM URPL GEN PERSHING ** 2) MN: SN: 0004210, *TAP: SIZE: G LOC: 1 FEET FROM P LINE AT DANNEEL, *MB: CODE: BEK2 LOC: MH ON GEN PERSHING BET DRYADES/DANNEEL 4' P/L ****/ | 2019-04-11 | REPLACED 5/8 CURB COCK.
201900280901 | 2019-02-14 | LEAD | 1437 | ST ANTHONY AV |  | WOLK | ML-METER LEAK ACCT#119127-486759 MTR#A372583 OUTLET SERVICE LEAK INSIDE METER BOX ON SIDEWALK /** 1) MN: A175015 SN: 0050702, *TAP: SIZE: A LOC: 65 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: AFK1 LOC: 65FT FROM LRPL ROBERTSON ON ST ANTHONY ST ****/ | 2019-03-06 | EXCAVATED 3 X 2 SIDEWALK MADE REPAIRS ON INLET SERVICE BACKFILLED AND CLEANED THE AREA
201900286401 | 2019-02-15 | LEAD | 2355 | N DERBIGNY | SPAIN | WOLK | MI-CONS ON METER PER INSPECTOR MTR # A-412764 ACCT# 193971-483145 /** 1) MN: A119781 SN: 0153399, *TAP: SIZE: B LOC: 92 FEET FROM P LINE AT SPAIN, *MB: CODE: CDN LOC: 99FT FROM PL SPAIN 6FT OUTSD 2FT INSD CURB ****/ | 2019-03-08 | EXAMINED JOB + FOUND NO CONSTRANT REGISTRATION ON METER
201900287302 | 2019-04-06 | LEAD | 1424 | VERNA CT | ESPLANADE AV | WILK | EXCAVATED 2 X 4 CONCRETE SIDEWALK NEAR CURB FOUND LEAK COMING FURTHER BACK IN STREET REFER TO ZONE FOR REPAIR TO BE MADE IN STREET /** 1) MN: A157520 SN: 0068600, *TAP: SIZE: B LOC: 176 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: AD LOC: ON VERNA, 176' FROM P.L. ESPLANADE AVE. ****/ | 2019-04-09 | MADE 4 X 6 CUT IN BLACK TOP STREET AND MADE REPAIR ON 3/4 INCH INLET SERVICE ALSO REPLACED CURB COCK BACKFILLED AREA
201900287401 | 2019-02-15 | LEAD | 1621 | LAMANCHE |  | WMTBG | INSP L UDUEBOR STATES METER BOX IS BELOW GRADE AND NEEDS TO BE UPDATED. PLEASE REPAIR METER A435258 LOC 181579 METER BOX BELOW GRADE. LEFT 1 CONE FOR SAFETY /** 1) MN: A314290 SN: 0129898, *TAP: SIZE: B LOC: 170 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: CD LOC: RES ON LAMANCHE 169FT FROM PL CLAIBORNE N 8' OUTSI ****/ | 2019-02-28 | EXCAVATED AND RAISE METER BOX UP TO GRADE BACKFILLED JOB WITH RIVERSAND
201900289401 | 2019-02-15 | LEAD | 1228 | S LOPEZ | CLIO | WILK | ML-METER LEAK ACCT#163017-705249 MTR#A321823 INLET SERVICE LEAKING FROM CURB COCK, FLOODING SIDEWALK /** 1) MN: A218530 SN: 0102443, *TAP: SIZE: B LOC: 250 FEET FROM P LINE AT CLIO, *MB: CODE: AE LOC: ON SO. LOPEZ, 250' FROM P.L. CLIO, 5' OUTSIDE P.L. ****/ DOTTIE READY 4-10-19 EXP 4-30-19 | 2019-04-12 | REPLACED 5/8 CURB COCK TIED INTO LEAD.(SOC 3FT. X 3 FT .SW/DW)CONCRETE.)
201900293201 | 2019-02-16 | LEAD | 3923 | ORLEANS AV | IDA | WILK | ML-METER LEAK METER#A333290 ACCT#130527-700290 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A333290 SN: 0060396, *TAP: SIZE: A LOC: 31 FEET FROM P LINE AT IDA, *MB: CODE: BDL1 LOC: ON ORLEANS AVE 29.6' FROM RPL IDA ****/ | 2019-02-27 | EXCAVATED 3 X 2 MUD PLOT REPLACED 5/8 INCH WASHERS AND HANDWHEEL TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900295801 | 2019-02-18 | LEAD | 1411 | ST BERNARD AV | N VILLERE | WOLK | ML-INSPECTOR FOUND CONS ON METER MTR#A411983 ACCT#127396-724420 /** 1) MN: A311923 SN: 0141256, *TAP: SIZE: A LOC: 74 FEET FROM P LINE AT VILLERE N, *MB: CODE: BEKN LOC: 72' P.L. N VILLERE ****/ | 2019-03-08 | EXAMINJED JOB + FOUND NO CONSTANT REGISTRATION ON METER
201900296401 | 2019-02-18 | LEAD | 2133 | PORT |  | WMRE | LOCATION ID#150192 METER #420601 PLEASE LOCATE AND RAISE METER TO GRADE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-28 | EXCAVATED IN GUTTER BOTTOM AND LOCATED METER BOX BACKFILLED AREA
201900298901 | 2019-02-18 | LEAD | 919 | KERLEREC |  | WILK | ML-METER LEAK ACCT#123569-556101 MTR#A386179 INETSERVICE LEAKNG IN BOX ON SIDEWALK /** 1) MN: A295727 SN: 0043299, *TAP: SIZE: A LOC: 211 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CDL LOC: 211' P.L. BURGUNDY ****/ | 2019-03-04 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900299401 | 2019-02-18 | LEAD | 2629 | URSULINES AV |  | WMTLK | ML- METER LEAK ACCT # 111136-449666 METER # A401092 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** 1) MN: SN: 0013590, *TAP: SIZE: B LOC: 227 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CFL LOC: IN GARDEN 227' P.L. N DORGENOIS ****/ | 2019-03-06 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900301101 | 2019-02-18 | LEAD | 2828 | SERANTINE | ST BERNARD AV | WILK | WM- LEAK BETWEEN SIDEWALK & CURB INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A293093 SN: 0068951, *TAP: SIZE: A LOC: 242 FEET FROM P LINE AT DUPRE N, *MB: CODE: AD LOC: ON SERANTINE ST 242.5' FROM N DUPRE ST ****/ | 2019-03-08 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLD JOB WITH RIVERSAND ALSO RAISE METER BOX UP TO GRADE
201900301701 | 2019-02-18 | LEAD | 2014 | ST PHILIP |  | WILK | ML--METER LEAK ACCOUNT#116949-524790 METER#A344739 INLET SERVICE LEAK IN BRICK SIDEWALK FROM BAD BLEEDER VALVE /** 1) MN: A130888 SN: 0023526, *TAP: SIZE: A LOC: 125 FEET FROM P LINE AT PRIEUR N, *MB: CODE: BFL5 LOC: METER ON ST PHILIP 125 FT FROM PL N PRIEUR ****/ | 2019-03-06 | EXCAVATED 2 X 4 BRICK SIDEWALK FOUND LEAK ON 5/8 INCH SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900303101 | 2019-02-19 | LEAD | 3471 | PARKVIEW PL |  | WMTLK | LOCATIONID#163332-701792 METER#A239958 LEAK INSIDE METERBOX /** 1) MN: A239958 SN: 0102138, *TAP: SIZE: B LOC: 220 FEET FROM P LINE AT MOSS, *MB: CODE: BDO2 LOC: ON PARKVIEW PL., 220' FROM P.L. MOSS, 6' OUTSIDE ****/ | 2019-03-08 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201900303401 | 2019-02-19 | LEAD | 1534 | N DORGENOIS |  | WMTLK | LOCATIONID#119222-489251 METER#A274456 LEAK INSIDE METERBOX /** 1) MN: A273936 SN: 0026362, *TAP: SIZE: A LOC: 36 FEET FROM P LINE AT LAHARPE, *MB: CODE: AFK7 LOC: ON N DORGENOIS 37FT FROM PL OF LAHARPE ****/ | 2019-03-15 | EXCAVATED 3 X 2 DRIVEWAY CUT MADE ON INLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900303801 | 2019-02-19 | LEAD | 1521 | ALVAR |  | WOLK | LOCATION# 145076 CUSTOMER# 430362 METER# A374646 INSPECTOR DID AN OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION ON METER, CAN'T DETERMINE WHERE LEAK IS COMING FROM.......PLEASE REPAIR /** 1) MN: A292899 SN: 0076716, *TAP: SIZE: B LOC: 141 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: AEL2 LOC: N ROBERTSON & CLAIBORNE 177'FROM P L N ROBERTSON ****/ | 2019-03-06 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX FOUND NO CONSTANT REGISTRATION
201900304601 | 2019-02-19 | LEAD | 2005 | CONGRESS | N JOHNSON | WMTBG | MI: DEPRESSION AROUND METER MTR# A429865 METER BELOW GRADE IN MUDPLOT NEAR SIDEWALK /** 1) MN: A345122 SN: 0084689, *TAP: SIZE: B LOC: 65 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CDL LOC: ON CONGRESS 65FT FROM JOHNSON N ****/ | 2019-03-06 | EXCAVATED IN MUD PLOT + RAISED 5/8 INCH METER BOX BOTTOM TO GRADE BACKFILLED + DRESSED UP AREA
201900305001 | 2019-02-19 | LEAD | 1019 | N GAYOSO | URSULINES AV | WOLK | ML-METER LEAK METER#A408258 OUTLET SERVICE LEAK IN TREE TRUNK, CON REG /** 1) MN: A181132 SN: 0054044, *TAP: SIZE: B LOC: 10 FEET FROM P LINE AT URSULINES AVE., *MB: CODE: NDL1 LOC: ON N. GAYOSO, 10' FROM D.P.L. URSULINES AVE., 8' ****/ | 2019-03-12 | EXCAVATED IN HEAVY TREE ROOTS + MADE REPAIR ON 3/4 INCH OUTLETSERVICE LINE BACKFILLED + DRESSED UP AREA ALSO REPLACED 5/8 METER BOX BOTTOM + DAMAGED 5/8 INCH METER OLD METER INFO: A408258 FACT: 14114020 MAKE:HERSEY READ: 229
201900305901 | 2019-02-19 | LEAD | 1342 | DESLONDE |  | WILK | ML -- METER LEAK ACCT# 169910-422740 METER# B023424 EXAMINE INLET SERVICE FOR LEAK IN BOX /** 1) MN: B023424 SN: 0111978, *TAP: SIZE: B LOC: 24 FEET FROM P LINE AT VILLERE N, *MB: CODE: AEL LOC: RES 24FT FROM P.L. N.VILLERE 8' OUTSIDE PL ****/ | 2019-03-12 | EXCAVATED 4 X 4 CONCRETE SIDEWALK FOUND LEAK 3/4 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND CODLMILL
201900310501 | 2019-02-20 | LEAD | 1500 | ESPLANADE AV |  | WMTLK | LOCATION ID-118410 MTR-A342237 UNDERGROUND LEAK BETWEEN MTR AND STOP & WASTE/CONS REG ON MTR /** 1) MN: SN: 0043894, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: AFHM LOC: SIDE ST ON N ROBERTSON 47' P.L. ESPLANADE AVE ****/ | 2019-03-08 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900310701 | 2019-02-20 | LEAD | 2230 | ST CLAUDE AV |  | WILK | LOCATION ID-115034 MTR-A435175 LEAK AT CURB COCK /** 1) MN: A239169 SN: 0060176, *TAP: SIZE: B LOC: 47 FEET FROM P LINE AT MARIGNY, *MB: CODE: AKL LOC: METER ON ST CLAUDE AVE 47 FT FROM PL MARIGNY ****/ | 2019-03-11 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900312001 | 2019-02-20 | LEAD | 531 | ST MAURICE AV | CHARTRES | WOLK | ML: METER LEAK MTR# A354840 ACCT# 211623-710931 OUTLET SERVICE LEAK IN CONCRETE SIDEWALK WITH CONSTANT REGISTRATION /** 1) MN: A300770 SN: 0094714, *TAP: SIZE: B LOC: 47 FEET FROM P LINE AT CHARTRES, *MB: CODE: BECL LOC: ON ST MAURICE 15' FROM DIV. P.L. OF CHARTERS ST. ' ****/ | 2019-03-06 | REPLACED 5/8 INCH WASHERS FOUND NO CONSTANT REGISTRATION ON METER
201900312801 | 2019-02-20 | LEAD | 2322 | PIETY | N TONTI | WILK | MI- LEAK ON THE SIDEWALK INLET SERVICE LEAK IN ASPHALT STREET FLOODING CURB GETTING OFF INTO DRAIN CATCH BASIN **CHANGED FROM 2232 PIETY** /** 1) MN: A240623 SN: 0084768, *TAP: SIZE: A LOC: 168 FEET FROM P LINE AT TONTI N, *MB: CODE: ADK1 LOC: P.L. 2322 - 174' P.L. N TONTI ****/ | 2019-03-20 | EXCAVATED IN MUD PLOT + REPLACED 3/4 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900313601 | 2019-02-21 | LEAD | 2825 | ALLEN |  | WMTLK | LOCATIONID#147011-707152 METER#A412478 LEAK INSIDE METERBOX /** 1) MN: A127512 SN: 0079067, *TAP: SIZE: A LOC: 194 FEET FROM P LINE AT DUELS, *MB: CODE: CDN1 LOC: ON ALLEN 194' FROM PL DUELS ST ****/ | 2019-03-11 | EXCAVATED 3 X 2 MUD PLOT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900313901 | 2019-02-21 | LEAD | 2523 | PAUGER |  | WMTLK | LOCATIONID#207393-721173 METER#A413426 LEAK INSIDE METERBOX /** 1) MN: A287401 SN: 0059125, *TAP: SIZE: A LOC: 158 FEET FROM P LINE AT ROMAN S, *MB: CODE: BDN LOC: 156FT FROM LSPL ROMAN ****/ | 2019-03-07 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900314702 | 2019-03-09 | LEAD | 1801 | LAHARPE |  | WMRE | LOCATE RAISE TO GRADE AND SET 5/8 INCH METER HOUSE UNDER RENOVATION EXCAVATED BY HAND ACROSS ABOVE LOCATION UNABLE TO LOCAT NEED BACKHOE REFER BACK TO ZONE 4 TO LOCATE /** 1) MN: SN: 0041837, *TAP: SIZE: A LOC: 51 FEET FROM P LINE AT LAHARPE, *MB: CODE: BDHF LOC: ON ROMAN 52FT FROM LAHARPE ****/ | 2019-03-12 | EXCAVATED IN MUD PLOT + LOCATED INLET AT ABOVE LOCATION REPLACED 5/8 INCH METER BOX COMPLETED + SET 5/8 INCH METER BACKFILLED + DRESSED UP AREA
201900315001 | 2019-02-21 | LEAD | 1840 | MANDEVILLE | N PRIEUR | WILK | INET SERVICE LEAK /** 1) MN: 000000 SN: 0065673, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: BDH6 LOC: ON N PRIEUR ST 63' FROM PL MANDEVILLE ST ****/ | 2019-02-20 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE LINE AND REPLACED METER COCK BACKFILLED AND CLEANED THE AREA
201900317301 | 2019-02-21 | LEAD | 1012 | LAMANCHE |  | WILK | WM -- LEAK IN THE STREET CHANGED FROM 1010 LAMANCHE INLET SERVICE LEAK IN MUDPLOT, FLOODING SIDEWALK, HOUSE VACANT AND UNDER CONSTRUCTION /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-02-28 | EXCAVATED 4 X 4 MUD PLOT IN GUTTER BOTTOM FOUND LEAK ON ABANDON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201900317901 | 2019-02-21 | LEAD | 4837 | N RAMPART | DESLONDE | WILK | ML: METER LEAK ACCT#130893-424442 MTR# A412538 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A190092 SN: 0061243, *TAP: SIZE: A LOC: 59 FEET FROM P LINE AT RAMPART N, *MB: CODE: BDHL LOC: ON DESLONDE 61.3' FROM SPL N RAMPART ****/ | 2019-03-12 | EXCAVATED 4 X 4 MUD PLOT AND FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIRS ON OUTLET BACKFILLED JOB WITH RIVERSAND
201900318201 | 2019-02-21 | LEAD | 2118 | ST BERNARD AV | N GALVEZ | WILK | ML- METER LEAK METER#B042017 ACCT#170440-488952 INLET SERVICE LEAK IN MUD PLOT /** 1) MN: B029243 SN: 0112534, *TAP: SIZE: B LOC: 142 FEET FROM P LINE AT GALVEZ N, *MB: CODE: ADMN LOC: 142FT FROM PL GALVEZ MTR ON ST BERNARD 11FT OUTSD ****/ | 2019-03-13 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA REPLACE 3/4 METER BOTTOM ALSO RAISE METER BOX TO GRADE
201900318401 | 2019-02-21 | LEAD | 1621 | ARTS |  | WMRE | METER BOX BURIED PLEASE RAISE TO GRADE AND SET A 5/8 METER LOCATION #307000 LOCATE & RASIE TO GRADE & SET 5\8 METER HOUSE UNDER RENOVATION /** 1) MN: A156109 SN: 0058644, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: ADN1 LOC: 147' P.L. N DERBIGNY ****/ | 2019-03-14 | EXCAVATED 3 X 2 GUTTER BOTTOM ALSO 4 X 2 SIDEWALK CUT RELOCATED METER TO SIDEWALK AND LEFT WHIP FOR CUSTMOR TO TIE INTO BACKFILLED AND CLEANED THE AREA
201900318501 | 2019-02-21 | LEAD | 3316 | N GALVEZ | PIETY | WILK | MI-LEAK AT THE SIDEWALK INLET SERVICE LEAK IN CONCRETE DRIVEWAY FLOODING CURB GETTING OFF DCB /** 1) MN: SN: 0177032, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT DESIRE, *MB: CODE: CD LOC: ON GALVEZ 150FT FROM P/L DESIRE ** 2) MN: E007221 SN: 0177032, *TAP: SIZE: E LOC: 126 FEET FROM P LINE AT PIETY, *MB: CODE: CD LOC: ON GALVEZ 126FT ROM PIETY 2FT OUTSIDE ****/ | 2019-05-26 | EXCAVATED IN CONCRETE DRIVEWAY + REPLACED 2 INCH INLET SERVICE LINE FROM CURB TO MANHOLE BACKFILLED + DRESSED UP AREA. (JOB COMPLETE)
201900318901 | 2019-02-21 | LEAD | 920 | TAFT PL | DUMAINE | WILK | ML-METER LEAK METER#A296963 ACCT#141336-704160 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A254803 SN: 0072634, *TAP: SIZE: B LOC: 177 FEET FROM P LINE AT DUMAINE, *MB: CODE: BD LOC: ON TAFT PL 177' FROM PL DUMAINE ****/ | 2019-03-13 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900321101 | 2019-02-22 | LEAD | 704 | ORLEANS AV | ROYAL | WILK | WATER LEAK -INLET SERVICE. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-16 | EXCAVATED IN ASPHAALT STREET BY HAND + REPLACED 2 INCH BEND ADAPTER ON WATER MAIN COMPACTED BACKFILL + DRESED UP AREA
201900322001 | 2019-02-22 | LEAD | 2632 | LAMANCHE |  | WOLK | WM-LEAK ON THE SIDEWALK EXAMINE OUTLET SERVICE FOR LEAK NEAR SIDEWALK /** 1) MN: A312696 SN: 0162468, *TAP: SIZE: B LOC: 224 FEET FROM P LINE AT LAW, *MB: CODE: __ LOC: MTR ON LAMANCHE 224FT FRM PL LAW 3FT INSD CURB ****/ | 2019-03-12 | EXAMINED JOB AT ABOVE LOCATION FOUND NO LEAK ON OUTLET SERVICE
201900322501 | 2019-02-22 | LEAD/PLASTIC | 4767 | PAINTERS | MIRABEAU AV | WOLK | ML- METER LEAK MTR # A295981 ACCT # 151845-477996 OUTLET SERVICE LEAK BAD HANDWHEEL WITH CONSTANT REGISTRATION ON THE METER 2/23/19 CUSTOMER NOW OUT OF WATER - UPGRADE TO PRIORITY A. . JOB GIVEN TO D RANDOLPH (PET) /** 1) MN: A295981 SN: 0087096, *TAP: SIZE: A LOC: 513 FEET FROM P LINE AT CARNOT, *MB: CODE: BDL2 LOC: 513FT FROM PL CARNOT 1ST DRIVE ON PAINTERS ****/ | 2019-02-23 | EXCAVATED A 6 X 6 MUDPLOT CUT & A 2 X 2 CONCRETE CUT IN DRIVWAY. REPAIED INLET SERVICE LEAK' RELOCATED METERBOX OUT OF DRIVEWAY' & RAISED TO GRADE. FOUND LEAD ON INLET SERVICE & PVC ON OUTLET SERVICE BACKFILLED JOBSITE.
201900323103 | 2019-03-14 | LEAD | 6313 | N PRIEUR |  | WOLK | EXCAVATED IN MUD PLOT MARKED BY JERRY GILLIAM AND FOUND CONTROLLING LINE WITH NO WATER JOB REFER BACK TO ZONETORUN CONTROLLING LINE FROM WATER MAIN OFF OF DELERY STREET NEED JOB MARK OFF ON DELERY BACKFILLED AREA /** 1) MN: A179394 SN: 0126212, *TAP: SIZE: A LOC: 2 FEET FROM P LINE AT PRIEUR N, *MB: CODE: BDMZ LOC: ON DELERY 2FT FRM LAKE PL N PRIEUR 6FT OUTSIDE PL ****/ | 2019-03-18 | EXCAVATED IN GUTTER BOTTOM + MADE REPAIR ON 1 INCH CONTROLLING LINE RESTORING WATER BACK TO ABOVE LOCATION ALSO MADE REPAIR ON 2 OTHER INLETS THAT ARE FED BY 1 INCH CONTROLLING LINE
201900324001 | 2019-02-22 | LEAD | 1024 | MARAIS |  | WILK | ML-METER LEAK ACCT#125612-526269 METER#A406975 INLET SERVICE LEAK INSIDE BOX IN SIDEWALK /** 1) MN: A296138 SN: 0048018, *TAP: SIZE: A LOC: 127 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: ADO2 LOC: 128' P.L. URSULINES AVE ****/ | 2019-03-22 | EXCAVATED 4 X 4 CONCRETE DRIVEWAY FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900327001 | 2019-02-23 | LEAD | 1733 | FRANCE | N ROMAN | WMTLK | MI- LEAK ON THE SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK. (C) /** 1) MN: A290200 SN: 0102026, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT ROMAN, *MB: CODE: ADK7 LOC: 64'FROM P L N ROMAN 8' OUTSIDE ****/ | 2019-03-11 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201900329601 | 2019-02-24 | LEAD/PLASTIC | 4710 | ST PETER | N ST PATRICK | WILK | /** 1) MN: A117115 SN: 0032208, *TAP: SIZE: A LOC: 83 FEET FROM P LINE AT ST PATRICK N, *MB: CODE: CFM1 LOC: 86FT FROM P/L N ST PATRICK ****/ | 2019-02-24 | MADE A 2 X 6 MUD CUT. EXCAVATED AND MADE REPAIRS ON A 3/4 LEAD LINE. RAISED THE GRADE AND RENEWED THE OUTLET WITH PLASTIC
201900330001 | 2019-02-25 | LEAD/PLASTIC | 1339 | NUNEZ | SOCRATES | WOLK | ML-METER LEAK ACCT#232502-401668 METER#A352552 CHECK FOR OUTLET SERVICE INSIDE METER BOX, LEAK ON SIDEWALK /** 1) MN: A278006 SN: 0051857, *TAP: SIZE: A LOC: 23 FEET FROM P LINE AT SOCRATES, *MB: CODE: CF LOC: ON NUNEZ 25FT FROM SOCRATES 4FT OUTSIDE ****/ | 2019-03-18 | ARRIVED ON JOB SITE EXAMINED LEAK IN SIDEWALK BROKE 5X5 CONCRETE SIDEWALK OUT BY HAND EXCAVATED IN MUD PLOT BY HAND MADE REPAIRS ON INLET SERVICE RENEWED OUTLET BACKFILLED DRESS UP WORK SITE
201900330401 | 2019-02-25 | LEAD | 2848 | MAUREPAS |  | WILK | MI LEAK ON SIDEWALK INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A345038 SN: 0078315, *TAP: SIZE: B LOC: 190 FEET FROM P LINE AT CRETE, *MB: CODE: CDLN LOC: 192FT FROM PL CRETE ****/ | 2019-03-08 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESED UP AREA
201900331901 | 2019-02-25 | LEAD | 806 | LOUISA |  | WILK | WM--LEAK BETWEEN STREET AND SIDEWALK INLET SERVICE LEAK INSIDE METER BOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-03-11 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND COLDMILL
201900333701 | 2019-02-25 | LEAD | 1729-31 | FRANCE |  | WMTLK | WM - LEAK ON THE SIDEWALK - NEIGHBOR STATES HIS PROPERY IS BEING AFFECTED BY THIS AT 1733 FRANCE EXAMINE INLET AND OUTLET SERVICE FOR A LEAK, METER BOX UNDER WATER /** AT 1729: 1) MN: A280009 SN: 0084731, *TAP: SIZE: B LOC: 248 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: ADK7 LOC: METER ON FRANCE 248 FT FROM PL N DERBIGNY ****/ | 2019-03-11 | EXCAVATED 4 X 4 LIMESTONE GUTTER BOTTOM FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND CLODMILL ALSO REPLACE BAD WATER METER
201900333801 | 2019-02-25 | LEAD | 1733 | PIETY | N DERBIGNY | WMTLK | **********PICKUP JOB*********** EXAMINE INLET AND OUTLET SERVICE FOR A LEAK, METER BOX UNDER WATER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-03-11 | EXAMINE JOB AT ABOVE LOCATION FOUND NO LEAK THERE'S NO SUCH ABOVE ADDRESS, WRONG ADDRESS WAS GIVING. JOB COMPLETE
201900333901 | 2019-02-25 | LEAD | 2310 | PIETY | N TONTI | WILK | WM-LEAK IN STREET INLET SERVICE LEAK AT THE WATER MAIN IN STREET /** 1) MN: A210996 SN: 0118568, *TAP: SIZE: A LOC: 107 FEET FROM P LINE AT TONTI N, *MB: CODE: BDM2 LOC: ON PIETY 107FT FROM TONTI 7FT OUTSIDE ****/ | 2019-03-20 | EXCAVATED IN ASPHALT STREET + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE COMPACTED BACKFILLED + DRESSED UP AREA JOB COMPLETE
201900334801 | 2019-02-25 | LEAD/PLASTIC | 5828 | FONTAINEBLEAU DR | STATE | WDSM | DECREASE EXISTING SERVICE AND METER FROM 1 INCH TO 5/8 INCH SERVICE AND METER AT 5828 FONTAINEBLEAU DRIVE, IN SAME LOCATION FOR THE FLAT SUM OF $100.00. WFA APP.: #123714 JOB #2778 /** 1) MN: C019331 SN: 0085270, *TAP: SIZE: C LOC: 77 FEET FROM P LINE AT VINCENNES PL, *MB: CODE: BDNK LOC: CURB FIRST METER OPP 5830 77FT FROM VINCENNES ****/ DOTTIE READY 3-15-19 EXP 4-4-19 | 2019-03-23 | DECREASED 1"WATER METER TO SET 5/8 WATER METER. OLD METER INFO:SENSUS #C030024 FACT#070692448 RD:046685
201900334901 | 2019-02-25 | LEAD/PLASTIC | 5830 | FONTAINEBLEAU DR | STATE | WDSM | DECREASE EXISTING SERVICE AND METER FROM 1 INCH TO 5/8 INCH SERVICE AND METER AT 5830 FONTAINEBLEAU DRIVE IN SAME LOCATION FOR THE FLAT SUM OF $100.00 WFA APP.: #123715 JOB #2779 /** 1) MN: C027353 SN: 0085270, *TAP: SIZE: C LOC: 79 FEET FROM P LINE AT VINCENNES PL, *MB: CODE: BDNK LOC: ON FONTAINBLEAU 78FT FROM PL VINCENNES ****/ DOTTIE READY 3-15-19 EXP 4-4-19 | 2019-03-23 | DECREASED 1"WATER METER TO 5/8 METER. OLD METER INFO: SENSUS#C028885 FACT#062101464 RD#05974
201900335602 | 2019-03-27 | LEAD | 2432 | ALLEN | N DORGENOIS | WMBK | METER BOX CASING SHIFTED OVER CURB COCK. (METER WAS RESET 3/7/19 BY A. PARKER) /** 1) MN: A278989 SN: 0161549, *TAP: SIZE: B LOC: 38 FEET FROM P LINE AT ALLEN, *MB: CODE: BE LOC: ON NO. DORGENOIS, 38' FROM P.L. ALLEN ****/ | 2019-04-01 | MADE 2 X 4 SIDEWALK CUT AND RESET CASING PROPERTY INLET CURB COCK BACKFILLED AREA
201900339201 | 2019-02-26 | LEAD | 1435 | ST ANTHONY AV | N ROBERTSON | WILK | ML-METER LEAK ACCT#202614-718112 METER#A221064 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A221064 SN: 0050702, *TAP: SIZE: B LOC: 64 FEET FROM P LINE AT NO. ROBERTSON, *MB: CODE: __ LOC: ON ST. ANTHONY, 65' FROM C.P.L. NO. ROBERTSON, 3' ****/ | 2019-03-11 | EXAMINED + FOUND JOB ALREADY REPAIRED AT AN EARLY DATE
201900339701 | 2019-02-26 | LEAD | 1762 | GENTILLY BL |  | WILK | ML METER LEAK ACCOUNT #126063-491696 METER #A382492 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A331300 SN: 0052784, *TAP: SIZE: B LOC: 92 FEET FROM P LINE AT GENTILLY BLVD, *MB: CODE: BDH1 LOC: ON AUBRY,93' FROM P.L. GENTILLY BLVD.,7.5' OUTSIDE ****/ | 2019-03-13 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201900340701 | 2019-02-26 | LEAD | 1309 | ST ANTHONY |  | WILK | WM- LEAK AT CURB INLET SERVICE LEAK IN ASPHALT STREET 03/06/19 LEAK NOW CAUSING POOR PRESSURE PER SR#12868902 (AJR) /** 1) MN: 000000 SN: 0052634, *TAP: SIZE: A LOC: 114 FEET FROM P LINE AT MARAIS, *MB: CODE: AF4 LOC: METER ON ST ANTHONY 87 FT FROM PL MARAIS ****/ | 2019-04-12 | EXAMINED JOB AT ABOVE LOCATED AND FOUND JOB ALREADY COMPLETE
201900342801 | 2019-02-27 | LEAD | 1205 | N LOPEZ | BELL | WILK | WM- LEAK IN THE STREET INLET SERVICE LEAK IN THE MUD PLOT NEAR LARGE TREE TRUNK /** 1) MN: D004265 SN: 0015633, *TAP: SIZE: D LOC: 58 FEET FROM P LINE AT BELL, *MB: CODE: AFN1 LOC: ON N LOPEZ 59' FROM BELL 2' OUTSIDE PL 10' INSIDE ** 2) MN: SN: 0015633, *TAP: SIZE: B LOC: 53 FEET FROM P LINE AT BELL, *MB: CODE: __ LOC: ON N LOPEZ 52.6' FROM P.L. BELL ****/ | 2019-03-20 | EXCAVATED IN TREE ROOTS BY HAND AND MADE REPAIRS ON 3/4 INCH TAILPIECE 6 INCH WATER MAIN BACKFILLED AREA
201900343001 | 2019-02-27 | LEAD | 3319 | N ROMAN |  | WMTLK | LOCATIONID#152064-431692 METER#A388100 LEAK INSIDE METERBOX /** 1) MN: A295074 SN: 0087586, *TAP: SIZE: A LOC: 183 FEET FROM P LINE AT PIETY, *MB: CODE: BE LOC: 183FT FROM P.L. PIETY ON N ROMAN ST ****/ | 2019-03-19 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERAND AND COLDMILL
201900343101 | 2019-02-27 | LEAD | 2407 | MAZANT |  | WMTLK | LOCATIONID#172922-434226 METER#A115587 LEAK INSIDE METERBOX /** 1) MN: A115587 SN: 0116404, *TAP: SIZE: C LOC: 77 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BDL2 LOC: 99' PL. NO.ROCHEBLAVE 7' OUTSIDE 3' INSIDE CURB ****/ | 2019-03-12 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900343401 | 2019-02-27 | LEAD | 1814 | INDEPENDENCE |  | WILK | LOCATION: 302538 MTR# A 425840 INSP L UDUEBOR STATES INLET SERVICE NEED REPAIRS. INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A296780 SN: 0100923, *TAP: SIZE: A LOC: 99 FEET FROM P LINE AT ROMAN N, *MB: CODE: AD LOC: 99'FROM PL N ROMAN 7' OUTSIDE PL ****/ | 2019-03-20 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900346901 | 2019-02-27 | LEAD | 1607 | ST PHILIP | N ROBERTSON | WILK | WM-LEAK ON THE SIDEWALK INLET LEAK ON THE SIDEWALK (C) /** 1) MN: A142941 SN: 0039960, *TAP: SIZE: A LOC: 56 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: ADK1 LOC: 55' P.L. N ROBERTSON ****/ | 2019-03-26 | EXCAVATED 4 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND CODLMILL
201900348701 | 2019-02-28 | LEAD | 3713 | DUMAINE |  | WMTLK | LOCATIONID#145583-706465 METER#135080 LEAK INSIDE METERBOX /** 1) MN: A135080 SN: 0077249, *TAP: SIZE: A LOC: 123 FEET FROM P LINE AT WILSON DR, *MB: CODE: AD LOC: ON DUMAINE, 123.5' FROM P.L. WILSON DR. ****/ | 2019-03-15 | EXCAVATED 2 X 1 SIDEWALK CUT REPLACEMETER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900348801 | 2019-02-28 | LEAD | 3905 | DUMAINE |  | WMTLK | LOCATIONID#108628-514790 METER#A377175 LEAK INSIDE METERBOX /** 1) MN: SN: 0022276, *TAP: SIZE: B LOC: 13 FEET FROM P LINE AT ROOSEVELT PL, *MB: CODE: CD LOC: 14FT FROM USPL ROOSEVELT PLACE ON DUMAINE ****/ | 2019-03-15 | EXCAVATED 4 X 2 GUTTER BOTTOM MADE REPAIR UNDER CURB ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201900351501 | 2019-02-28 | LEAD | 5717 | WINGATE DR | PRENTISS AV | WILK | LEAK IN THE STREET (PHOTOS SENT TO R. STANWOOD) INLET SERVICE LEAK IN AN ASPHALT STREET FROM A OLD PATCH /** 1) MN: A220715 SN: 0106781, *TAP: SIZE: A LOC: 205 FEET FROM P LINE AT PRENTISS AVE, *MB: CODE: ADLZ LOC: ON WINGATE DR., 206' FROM P.L. PRENTISS AVE., 7' ****/ | 2019-03-12 | EXCAVATED IN THE STREET TO REPAIR A INLET SERVICE LEAK . HAD TO MAKE A 7 X 10 STREET CUT FOUND LEAD ON INLET
201900352401 | 2019-02-28 | LEAD | 1975 | LAW | ALLEN | WILK | ML-METER LEAK***METER#A40720 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A218909 SN: 0064366, *TAP: SIZE: C LOC: 47 FEET FROM P LINE AT NEW ORLEANS, *MB: CODE: CDN1 LOC: ON LAW 47' FROM PL NEW ORLEANS 9' OUTSIDE PL ****/ | 2019-03-13 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900353501 | 2019-02-28 | LEAD | 2721 | DUMAINE | N GALVEZ | WMTLK | METER LEAKING AGAIN METER# A422601 ACCT# 102174-520775 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK, METER BOX UNDER WATER 03/01/19 CUSTOMER WAITING ON REPAIR *****CUST INSPECTION DEADLINE IS 3/13/19, CAN'T GET INSPECTION WITHOUT REPAIR***** (KSW) /** 1) MN: A308773 SN: 0004901, *TAP: SIZE: B LOC: 189 FEET FROM P LINE AT BROAD N, *MB: CODE: AFK LOC: ON DUMAINE 189FT FROM LSPL OF N BROAD ****/ | 2019-03-13 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900354801 | 2019-03-01 | LEAD | 1404 | DESIRE | N VILLERE | WILK | MI- LEAK ON SIDEWALK **********DAMAGE CLAIM********** CUT INLET SERVICE BY HARD ROCK CONSTRUCTION STREET UNDER CONSTRUCTION, PIPE CRUMP OFF. /** 1) MN: A257151 SN: 0074888, *TAP: SIZE: B LOC: 33 FEET FROM P LINE AT VILLERE N, *MB: CODE: ADN5 LOC: ON DESIRE ST 34' FROM PL N VILLERE ST ****/ | 2019-05-07 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA FORCE ACCOUNT HARD ROCK CONSTRUCTION FOR REPAIR NO METER
201900357401 | 2019-03-01 | LEAD | 3010 | PAUGER | N TONTI | WMBK | ML - METER LEAK MTR # A416229 ACCT # 268419-720838 BROKEN LOWER METER BOX. ***HOUSE UNDER RENOVATION*** /** 1) MN: A114907 SN: 0060870, *TAP: SIZE: A LOC: 87 FEET FROM P LINE AT TONTI N, *MB: CODE: CDLM LOC: ON PAUGER 86.6' FROM LPL N TONTI ****/ | 2019-03-13 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH METER BOX CASING BACKFILLED + DRESSED UP AREA
201900364501 | 2019-03-04 | LEAD/PLASTIC | 7923 | BELFAST | FERN | WOLK | ML METERLEAK MTR#A370190 LOC/CUST#163968-716035 CONS REG ON METER. /** 1) MN: A213652 SN: 0103491, *TAP: SIZE: A LOC: 202 FEET FROM P LINE AT FERN, *MB: CODE: AD LOC: ON BELFAST, 201' FROM P.L. FERN, 8' OUTSIDE P.L. ****/ DOTTIE READY 3-7-19 EXP 3-27-19 | 2019-03-16 | EXCAVTED IN MUDPLOT CHANGED METER BOX.BACKFILLED MUDPLOT WITH RIVERSAND.
201900368201 | 2019-03-05 | LEAD | 3356 | DUMAINE |  | WMTLK | LOCATIONID#118230-521737 METER#A397727 METERBOX OVERFLOWING /** 1) MN: A280152 SN: 0029182, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT DUMAINE, *MB: CODE: BF4O LOC: 1ST METER ON SIDE STREET OUTSIDE OF FENCE ****/ | 2019-03-20 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900368701 | 2019-03-05 | LEAD | 1230 | N JOHNSON |  | WMTLK | LOCATIONID#100634-524664 METER#A406988 LEAK INSIDE METERBOX /** 1) MN: A155779 SN: 0003817, *TAP: SIZE: A LOC: 68 FEET FROM P LINE AT BARRACKS, *MB: CODE: AFK7 LOC: ON NO. JOHNSON,68' FROM U.S.P.L. BARRACKS ****/ | 2019-03-22 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA
201900368901 | 2019-03-05 | LEAD | 1219 | N PRIEUR |  | WMTLK | LOCATIONID#112115-524731 METER#A409422 LEAK INSIDE METERBOX /** 1) MN: A309461 SN: 0063162, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT BARRACKS, *MB: CODE: BFL7 LOC: 134' P.L. BARRACKS ****/ | 2019-03-22 | EXAMINED AND PUMPED METER BOX DOWN AND REPLACED 5/8 INCH WASHERS ON INLET AND OUTLET IN DRIVEWAY
201900370301 | 2019-03-06 | LEAD/PLASTIC | 7710 | GREEN | ADAMS | WOLK | ML- METER LEAK MTR # A427201 ACCT # 112353-581994 OUTLET SERVICE LEAKING FROM HANDWHEEL, FLOODING GRASS /** 1) MN: A304624 SN: 0048201, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT ADAMS, *MB: CODE: AF LOC: ON GREEN 82FT FROM ADAMS ****/ | 2019-03-18 | EXCAVATED IN MUD PLOT TO REPAIR A BAD HANDWHEEL AND ALL SO A BAD 5/8" METER BOX COCK RAISE METER TO GRADE FOUND LEAD ON INLET
201900371801 | 2019-03-06 | LEAD | 200 | N JEFFERSON DAVIS PK | IBERVILLE | WILK | ML- METER LEAKING AGAIN MTR # A387693 ACCT # 103598-519066 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A268316 SN: 0006420, *TAP: SIZE: A LOC: 14 FEET FROM P LINE AT IBERVILLE LRPL, *MB: CODE: M6 LOC: 14' FROM LRPL IBERVILLE ****/ | 2019-03-20 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201900372501 | 2019-03-06 | LEAD | 1929 | N DORGENOIS |  | WILK | WM - LEAK ON THE SIDEWALK - IN FRONT OF THE PROPETY NEXT DOOR **************B LEVE IN SYSTEM*************** INLET SERVICE LEAK NEAR STEPS, NO METER IN BOX /** 1) MN: A153429 SN: 0061841, *TAP: SIZE: B LOC: 50 FEET FROM P LINE AT A. P. TREAUD, *MB: CODE: BD LOC: ON N DORGENOIS ST 52' FROM USPL A. P. TREAUD ****/ | 2019-03-11 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 3/4 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201900374901 | 2019-03-06 | LEAD | 1461 | N ROBERTSON |  | WILK | ML-METER LEAK ACCT#106105-486203 METER#A295349 INLET SERVICE LEAK IN SIDEWALK COMING FROM BAD BLEEDER VALVE **CHANGED FROM 1461 N ROBERTSON** /** 1) MN: A284498 SN: 0008121, *TAP: SIZE: B LOC: 131 FEET FROM P LINE AT KERLEREC, *MB: CODE: AENO LOC: XX 131' P.L. KERLEREC ****/ | 2019-03-22 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201900375301 | 2019-03-06 | LEAD | 928 | CLOUET | N RAMPART | WILK | ML: METER LEAK ACCT#112860-563160 MTR#A430359 INLET SERVICE LEAK IN METER BOX /** 1) MN: A278471 SN: 0014887, *TAP: SIZE: A LOC: 105 FEET FROM P LINE AT RAMPART N, *MB: CODE: BFL6 LOC: 105FT FROM URPL N RAMPART ****/ | 2019-03-24 | EXCAVATED IN BRICK SIDEWALK AT THE BASE OG A TREE THORUGH HEAVY TREE ROOTS BY HAND + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA REPLACED DAMAGED 5/8 INCH WATER METER OLD METER INFO: A430359 FACT: 16355948 MAKE: HERSEY READ: 52
201900375401 | 2019-03-06 | LEAD | 2414 | MUSIC | N ROCHEBLAVE | WILK | MI- LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET FLOODING AREA LEFT ONE (1) SAFETY CONE /** 1) MN: SN: 0076292, *TAP: SIZE: A LOC: 113 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: CDN1 LOC: 113' P.L. N ROCHEBLAVE ****/ | 2019-03-21 | EXCAVATED IN ASPHALT STREET + REPLACED 3/4 INCH BEND ADAPTER ON WATER MAIN COMPACTED BACKFILLED + DRESSED UP AREA
201900375601 | 2019-03-06 | LEAD | 3030 | FLORIDA AV |  | WOLK | WM--LEAK IN THE STREET OUTLET SERVICE LEAK IN MUDPLOT **CHANGED FROM 3030 FRANKLIN AV** /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-03-15 | EXCAVATED 3 X 1 MUD PLOT MADE REPAIR ON OUTLET AT PROPERTY BACKFILLED AND CLEANED THE AREA
201900377701 | 2019-03-07 | LEAD | 1824 | ANNETTE | ROMAN | WMTLK | ML- METER LEAK MTR# A432501 ACCT# 135369-494684 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: A263075 SN: 0066018, *TAP: SIZE: A LOC: 188 FEET FROM P LINE AT ROMAN N, *MB: CODE: CDN1 LOC: 188FT FROM PL ROMAN ****/ | 2019-03-15 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX
201900378801 | 2019-03-07 | LEAD | 2315 | ANNETTE |  | WILK | MI - CONTRACTOR HIT WATER LINE ENTERGY GAS 3700 TULANE AVE - NEW ORLEANS LA 70119 ACCORDING TO CSM - THERE IS NO OPEN ACCOUNT AT THIS LOCATION *******DAMAGE CLAIM******* (J.GILLIAM @ 11:14AM) INLET @ THE MAIN IN STREET BY ENTERGY GAS, STREET IS FLOODED /** 1) MN: A325208 SN: 0102752, *TAP: SIZE: A LOC: 125 FEET FROM P LINE AT TONTI N, *MB: CODE: AD LOC: ON ANNETTE 124' FROM PL N TONTI 7' OUTSIDE PL 2' I ****/ | 2019-03-07 | EXCAVATED IN CUT IN ASPHALT STREET MADE BY ENTERGY MADE REPAIR ON 3/4 INCH INLET SERVICE LINE FORCE ACCOUNT ENTERGY FOR REPAIRS
201900379501 | 2019-03-07 | LEAD | 2900 | PARIS AV |  | WMRE | INSP L MITCHELL STATES HE IS UNABLE TO LOCATE SERVICE TO CHANGE METER. PLEASE LOCATE AND CHANGE METER A274790 LOC 131421 LOCATE, RAISE TO GRADE AND CHANGE METER /** 1) MN: A274790 SN: 0062375, *TAP: SIZE: A LOC: 114 FEET FROM P LINE AT AGRICULTURE, *MB: CODE: CDWM LOC: ON PARIS AVE.,91.5' FROM U.P.L. AGRICULTURE ****/ | 2019-03-20 | EXCAVATED IN HIGH GRASS AND LOCATED METER OF MEASUREMENT GIVEN CHANGE METER INSIDE METER BOX METER ALREADY TO GRADE OLD METER INFO: A274790 FACT: 45143618 MAKE: SENSUS READ:14002
201900380601 | 2019-03-07 | LEAD | 3226 | ORLEANS AV |  | WOLK | LOCATION: 307108 INSP M FRAZIER STATES METER BOX IS BELOW GRADE. PLEASE RAISE AND SET A 5/8 METER. CUSTOMER IS HOME WAITING ON WATER OUTLET TIE IN HOUSE UNDER RENOVATION AND SET 5/8 METER /** 1) MN: SN: 0082381, *TAP: SIZE: B LOC: 104 FEET FROM P LINE AT HAGAN AVE, *MB: CODE: CDN2 LOC: ON ORLEANS AVE 104' FROM PL HAGAN AVE ****/ | 2019-03-11 | EXCAVATED 3 X 3 MUD PLOT RAISED METER BOX UP TO GRADE + SET METER BACKFILLED AND CLEANED THE AREA
201900381201 | 2019-03-07 | LEAD | 2024 | REYNES | N JOHNSON | WMLK | WATER LEAK -MAIN. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** 1) MN: B026809 SN: 0128217, *TAP: SIZE: B LOC: 155 FEET FROM P LINE AT JOHNSON N, *MB: CODE: ADK LOC: RES ON REYNES 153FT FROM PL JOHNSON ****/ | 2019-03-24 | EXCAVATED 8 X 6 STREET CUT MADE REPAIR ON INLET SERVICE LINE AT MAIN TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900381501 | 2019-03-07 | LEAD | 2455 | REYNES | N DORGENOIS | WMTLK | WATER LEAK -METER. LEAK IS VISIBLE. LEAK LOCATION WAS MARKED WITH BLUE PAINT BY ECHOLOGICS. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-03-21 | CHOPPED HIGH GRASS AND FOUND BLUE MARK BY ECHOLOGIC EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 INCH ABANDON SERVICE BACKFILLED AREA
201900382001 | 2019-03-07 | LEAD | 3018 | REPUBLIC |  | WMLK | WM-LEAK IN BETWEEN STREET AND SIDEWALK EXAMINE LEAK ON WATER MAIN FLOODING GUTTER BOTTOM /** 1) MN: SN: 0074724, *TAP: SIZE: B LOC: 132 FEET FROM P LINE AT ABUNDANCE, *MB: CODE: CDL1 LOC: ON REPUBLIC 134FT PL ABUNDANCE 10' OUTSIDE 2' IN- ****/ | 2019-03-24 | EXCAVATED IN LIMESTONE GUTTER BOTTOM + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900382401 | 2019-03-07 | LEAD | 1927 | N DORGENOIS | HAVANA | WILK | MI: LEAK INSIDE METER BOX NO METER AT LOCATION INLET SERVICE IN SIDEWALK NO METER IN BOX GETTING OFF IN DCB /* /** 1) MN: A302589 SN: 0082741, *TAP: SIZE: A LOC: 217 FEET FROM P LINE AT HAVANA, *MB: CODE: AF LOC: ON DORGENOIS 217FT FROM HAVANA ****/ | 2019-03-15 | EXCAVATED BEHIND METER BOX AND MADE REPAIR ON 3/4 INCH INLET SERVICE BACKFILLED AREA JOB COMPLETE
201900382501 | 2019-03-07 | LEAD | 1662 | ABUNDANCE | BRUXELLES | WOLK | ML- METER LEAK MTR # A375905 ACCT # 147065-701960 OUTLET SERVICE LEAK IN SIDEWALK /** 1) MN: A258839 SN: 0078873, *TAP: SIZE: B LOC: 129 FEET FROM P LINE AT BRUXELLES, *MB: CODE: BDK2 LOC: 129' P.L. BRUXELLES ****/ | 2019-03-20 | EXCAVATED 2 X 4 MUD PLOT IN SIDEWALK FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIR ON OUTLET BACKFILL JOB WITH COLDMILL
201900383601 | 2019-03-08 | LEAD/PLASTIC | 7119 | MARSHALL FOCH |  | WMTLK | ML- METER LEAK MTR# B-022057 ACCT # 178130-512208 /** 1) MN: B999987 SN: 0123619, *TAP: SIZE: B LOC: 148 FEET FROM P LINE AT CONRAD, *MB: CODE: BDON LOC: 148' P/L CONRAD 8' OUTSIDE ****/ | 2019-03-21 | EXCAVATED IN MUD PLOT TO REPAIRE A INLET LEAK BEHIND THE BOX , ALL SO RAISE METER TO GRADE FOUND LEAD OUTLET AND PLASTIC ON THE INLET
201900384101 | 2019-03-08 | LEAD | 1011 | URSULINES AV | BURGUNDY | WILK | ML MTR# B031002 CUST & LOC #110664-705237 SERVICE ADDRESS: 1011 URSULINES AVE INSP COMM: F/ON-L/ON (OCC) RD. 19295.... DID OUTSIDE INSP. FOUND LEAK AT CURB COCK SIDE OF MET, NO CONS OR REPAIRS MADE /** 1) MN: B031002 SN: 0022203, *TAP: SIZE: B LOC: 76 FEET FROM P LINE AT BURGUNDY, *MB: CODE: BEN LOC: 75' P.L. BURGUNDY ****/ | 2019-03-19 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACE METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900385401 | 2019-03-08 | LEAD | 2410 | ALABO | N ROCHEBLAVE | WILK | WM-LEAK IN STREET INLET SERVICE LEAK IN ASPHALT STREET /** 1) MN: A140234 SN: 0133752, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: ADL5 LOC: RES ON ALABO 64FT PL N ROCHEBLAVE 6' INSIDE CURB ****/ | 2019-03-23 | EXCAVATED 7 X 10 STREET CUT MADE REPAIR ON ABANDON INLET SERVICE BACKFILLED AND CLEANED THE AREA
201900387001 | 2019-03-08 | LEAD/PLASTIC | 2508 | VERBENA | IRIS | WILK | ML- METER LEAK****METER#A372378 ACCT#137454-476343 DISPATCHER DID NOT RECEIVE PRINTED TO PHONE CENTER /** 1) MN: A283572 SN: 0085257, *TAP: SIZE: B LOC: 76 FEET FROM P LINE AT IRIS, *MB: CODE: ADN LOC: ON VERBENA 76' FROM PL OF IRIS ****/ | 2019-04-24 | EXCAVATED DOWN ON INLET AND OUTLET SERVICES. FOUND LEAD AND PLASTIC TUBING AND CURB COCK WAS LEAKING. MADE REPAIRS BY REPLACING COCK WASHERS BACKFILLED. JOB COMPLETE
201900390601 | 2019-03-08 | LEAD | 2216 | CHOCTAW | N MIRO | WMBK | **************PICKUP*********** BROKEN METER BOX CASING /** 1) MN: C016905 SN: 0132572, *TAP: SIZE: C LOC: 126 FEET FROM P LINE AT MIRO N, *MB: CODE: OOO LOC: ON CHOCTAW 126' FROM PL N MIRO 2' OUTSIDE PL ****/ | 2019-03-11 | REPLACE UPPER METER BOX CASING AT ABOVE LOCATION
201900390801 | 2019-03-08 | LEAD | 4202 | N CLAIBORNE AV | FRANCE | WILK | ML: METER LEAK, MTR # A390099, ACCOUNT # 203487-726410 INLET SERVICE LEAK LEAKING FROM CURB COCK IN SIDEWALK /** 1) MN: A317221 SN: 0163899, *TAP: SIZE: A LOC: 46 FEET FROM P LINE AT FRANCE, *MB: CODE: OOO LOC: ON N CLAIBORNE 46FT FROM PL FRANCE 6FT INSD CURB ****/ | 2019-03-19 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 3/4 INCH INLET SERVICE MAE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900393901 | 2019-03-09 | LEAD | 3129 | LANCASTER |  | WILK | WM LEAK AT THE CURB INLET SERVICE LEAK IN CONCRETE STREET /** 1) MN: A216947 SN: 0120854, *TAP: SIZE: B LOC: 248 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: CDK LOC: ON LANCASTER 248FT FROM P.L. GEN MEYER ****/ | 2019-04-27 | ARRIVED ONJOB EXAMINED LEAK IN STREET MADE CUT IN STREET OVER WATER MAIN REPAIR ON INLET SERVICE AT WATER MAIN BACKFILLED DRESSED UP WORK SITE. JOB COMPLETE
201900396901 | 2019-03-11 | LEAD | 3913 | ST CLAUDE AV | BARTHOLOMEW | WILK | ML: METER LEAK, MTR # A300014, ACCT # 114343-430142 EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A300014 SN: 0027681, *TAP: SIZE: A LOC: 119 FEET FROM P LINE AT ALVAR, *MB: CODE: BFK2 LOC: INSIDE BY FENCE 119' P.L. ALVAR ****/ | 2019-03-21 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201900397901 | 2019-03-11 | LEAD | 3126 | JENA | S ROMAN | WMTLK | ML- METER LEAK MTR # A248247 ACCT # 153046-716640 EXAMINE INLET AND OUTLET SERVICR FOR LEAK METER UNDER WATER ON S ROMAN /** 1) MN: A248247 SN: 0088871, *TAP: SIZE: B LOC: 57 FEET FROM P LINE AT JENA, *MB: CODE: CDL1 LOC: 2ND METER ON S ROMAN 57FT FROM PL JENA BY FENCE ****/ DOTTIE READY 3/14/19 EXP 4/3/19 | 2019-03-16 | EXCAVTED IN MUDPLOT OVER INLET SERVICE CHANGED METER BOX COCK BACKFILLED WITH RIVERSAND.RAISED METER TO GRADE.
201900398001 | 2019-03-11 | LEAD | 3124 | JENA | S ROMAN | WMTLK | ML- METER LEAK MTR # A351543 ACCT # 153045-716640 EXAMINE INLET AND OUTLET SERVICR FOR LEAK METER UNDER WATER ON S ROMAN /** 1) MN: A351543 SN: 0088871, *TAP: SIZE: B LOC: 57 FEET FROM P LINE AT JENA, *MB: CODE: CDL1 LOC: 1ST METER ON SO ROMAN 56FT FROM PL JENA ****/ DOTTIE READY 3/11/19 EXP 3/14/19 | 2019-03-16 | EXCAVATED IN MUDPLOT OVER INLET SERVICE CHANGED METER BOX COCK AND HAND WHEEL.BACFILLED WITH RIVER SAND.
201900401801 | 2019-03-12 | LEAD | 1722 | MANDEVILLE |  | WMTLK | MI LEAK ON THE SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER. CARS PARKING ON METER /** 1) MN: A292406 SN: 0066031, *TAP: SIZE: A LOC: 174 FEET FROM P LINE AT DERBIGNY NO., *MB: CODE: CDN LOC: ON MANDEVILLE, 174'FROM P.L. NO. DERBIGNY ****/ | 2019-03-21 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900402501 | 2019-03-12 | LEAD/PLASTIC | 4701 | PALMYRA |  | WILK | ML--METER LEAK ACCOUNT#127032-492601 METER#A391774 INLET SERVICE LEAK IN THE MUD PLOT FOUND EXCAVATED & COVER WITH A BOARD /** 1) MN: A275763 SN: 0052074, *TAP: SIZE: A LOC: 51 FEET FROM P LINE AT PALMYRA, *MB: CODE: BDH3 LOC: ON SO. ST. PATRICK,48.6' FROM L.S.P.L. PALMYRA ****/ | 2019-03-21 | EXCAVATED IN MUD PLOT THROUGH DEBRIS TO REPAIR A 5/8" INLET SERVICE LEAK CHANEGD THE COCK BACKFILLED AND DRESS UP WITH RIVER SAND LEAD INLET & OUT PVC
201900402901 | 2019-03-12 | LEAD | 3821 | MARAIS |  | WMTLK | INSP L UDUEBOR STATES HE IS UNABLE TO SET METER. INLET AND OUTLET ARE TWO DIFFERENT SIZES. PLEASE REPAIR AND SET 3/4 METER. LOC 154191 INLET & OUTLET SERVICE ARE NOT THE SAME SIZE. METER SHOP NOT ABLE TO SET METER. *****UNDER RENOVATIONS***** /** 1) MN: SN: 0078012, *TAP: SIZE: B LOC: 162 FEET FROM P LINE AT PAULINE, *MB: CODE: ADM5 LOC: ON MARAIS,162' FROM P.L. PAULINE,8' OUTSIDE P.L., ****/ | 2019-03-24 | EXCAVATED IN SIDEWALK + REPLACED 5/8 INCH CURB COCK WITH 3/4 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900403001 | 2019-03-12 | LEAD | 935 | N DUPRE | ST PHILIP | WILK | ML- METER LEAK METER# A316191 ACCT# 129575-720509 INLET SERVICE LEAKING INSIDE METER BOX /** 1) MN: A316191 SN: 0175058, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT ST PHILIP, *MB: CODE: CD LOC: 117' FROM LRPL ST PHILIP ****/ | 2019-03-22 | EXCAVATED IN SMALL TREE ROOTS IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201900403301 | 2019-03-12 | LEAD | 1508 | CAFFIN AV | N CLAIBORNE AV | WILK | WM-LEAK IN STREET INLET SERVICE LEAK IN A CONCRETE STREET @ THE MAIN /** 1) MN: A307972 SN: 0122256, *TAP: SIZE: A LOC: 49 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: ADK LOC: RES ON CAFFIN 51FT PL N ROBERTSON 7' OUTSIDE ****/ | 2019-03-24 | EXCAVATED 4 X 8 STREET CUT ALSO 12 X 4 MUD PLOT ABOVE 6 INCH WATER MAIN REPLACE CRYSTALIZE LINE FROM WATER MAIN TO STREET TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900405601 | 2019-03-12 | LEAD | 1715 | NEW ORLEANS | N ROMAN | WILK | ML-METER LEAK EXAMINE INLET SERVICE FOR ALEAK INSIDE METER BOX /** 1) MN: A268723 SN: 0051890, *TAP: SIZE: A LOC: 126 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: CDK LOC: 126' P.L. N DERBIGNY ****/ | 2019-03-21 | REPLACED 5/8 INCH WASHERS IN METER BOX
201900408501 | 2019-03-12 | LEAD | 2120 | N BROAD |  | WOLK | MI- LEAK IN THE SIDEWALK OUTLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A306567 SN: 0069657, *TAP: SIZE: A LOC: 161 FEET FROM P LINE AT DUELS, *MB: CODE: ADL LOC: 161FT FROM PL DUELS 10FT OUTSD 2FT INSIDE ****/ | 2019-03-26 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900409501 | 2019-03-13 | LEAD | 3221 | ST ANN |  | WOLK | ML METERLEAK MTR#A405685 LOC/CUST#127914-520248 CONS REG ON METER. /** 1) MN: A325807 SN: 0054472, *TAP: SIZE: A LOC: 138 FEET FROM P LINE AT HAGAN AVE, *MB: CODE: CDLM LOC: GUTTER EDGE 137' P.L. HAGAN AVE ****/ | 2019-03-26 | EXAMINED JOB AT ABOVE LOCATION FOUND NO LEAK ON OUTLET SERVICE
201900411901 | 2019-03-13 | LEAD | 2400 | ST ANTHONY AV | N ROCHEBLAVE | WILK | ML- METER LEAK METER# A426232 ACCT# 205613-728286 INLET SERVICE LEAK VEHICLES ARE PARKING ON METER /** 1) MN: A308151 SN: 0169943, *TAP: SIZE: B LOC: 48 FEET FROM P LINE AT ST ANTHONY, *MB: CODE: OOOO LOC: ON NO. ROCHEBLAVE, 38' FROM P.L. ST. ANTHONY, 6' ****/ | 2019-03-25 | EXCAVATED 2 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH SERVICE MADE REPAIRS ON INELT BACKFILLED JOB WITH RIVERSAND
201900413101 | 2019-03-13 | LEAD | 3136 | N GALVEZ | CLOUET | WILK | ML. METER LEAK, MTR # A276296, ACCOUNT # 136038-433276 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A276296 SN: 0087389, *TAP: SIZE: A LOC: 386 FEET FROM P LINE AT CLOUET, *MB: CODE: BD LOC: ON N GALVEZ ST 286' FROM PL CLOUET ****/ | 2019-03-27 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900413501 | 2019-03-13 | LEAD | 1037 | MAZANT | N RAMPART | WILK | ML- METER LEAK METER # A391919 ACCT # 207618-VACANT INLET SERVICE LEAK CARS ROLLING OVER METER /** 1) MN: A234802 SN: 0082424, *TAP: SIZE: A LOC: 140 FEET FROM P LINE AT RAMPART N, *MB: CODE: OOO LOC: ON MAZANT 140FT FROM P.L. N RAMPART 8FT OUTSIDE ****/ | 2019-03-27 | EXCAVATED 4 X 4 LIMESTONES GUTTER BOTTOM FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET AND RAISE METER BOX UO TO GRADE BACKFILL JOB WITH RIVERSAND AND COLDMILL
201900413601 | 2019-03-13 | LEAD | 1018 | BIENVILLE | N RAMPART | WILK | MI- LEAK ON SIDEWALK INLET SERIVE LEAK IN METER BOX IN A BRICK SIDEWALK /** 1) MN: C023202 SN: 0168099, *TAP: SIZE: C LOC: 42 FEET FROM P LINE AT RAMPART N, *MB: CODE: OOO LOC: ON BIENVILLE 41FT FROM PL N RAMPART ** 2) MN: C022237 SN: 0168099, *TAP: SIZE: C LOC: 42 FEET FROM P LINE AT RAMPART N, *MB: CODE: OOO LOC: ON BIENVILLE APT D 44FT FROM PL N RAMPART THERE ARE 3 MORE NOT LISTED. ****/ | 2019-03-25 | EXCAVATED 2 X 4 BRICK SIDEWALK FOUND LEAK ON 1 INCH OUTLET SERVICE MADE REPAIRS ON OUTLET BACKFILL JOB WITH MUD AND LEFT 1 SAFETY CONE NEED TO BE DRESSED UP
201900414001 | 2019-03-13 | LEAD | 2001 | ALMONASTER AV |  | WMTLK | WM: LEAK IN STREET NO LEAK IN STREET EXAMINE INLET /OUTLET SERVICE FOR A LEAK INSIDE METER BOX, /** 1) MN: A263853 SN: 0074380, *TAP: SIZE: B LOC: 78 FEET FROM P LINE AT ALMONASTER AVE., *MB: CODE: BDHK LOC: ON NO. JOHNSON, 78' FROM P.L. ALMONASTER AVE.,7.5' ****/ | 2019-03-27 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900414501 | 2019-03-13 | LEAD/PLASTIC | 2612 | SONIAT | CLARA | WILK | WM- LEAK BETWEEN SIDEWALK AND STREET INLET SERVICE LEA IN MUDPLOT FLOODING CURB GETTING OFF INTO DRAIN CATCH BASIN 04/25/19 LEAK CAUSING POOR PRESSURE PER SR#12873927 (AJR) /** 1) MN: D004685 SN: 0061250, *TAP: SIZE: D LOC: 100 FEET FROM P LINE AT CLARA, *MB: CODE: BEM1 LOC: MH ON SONIAT 100FT FRM PL CLARA 5FT OUTSD PL 7FT ****/ DOTTIE READY 5-1-19 EXP 5-21-19 | 2019-05-05 | MADE REPAIR ON 1 1/2 INLET SEWRIVE .BACKFILLED MUDPLOT WITH RIVERSAND.
201900414701 | 2019-03-13 | LEAD | 1517 | N TONTI |  | WMTLK | ML -- METER LEAK METER# A407243 ACCT# 133743-449127 EXAMINE INLET/OUTLET SERVICE FOR A LEAK ALSO RAISE TO GRADE /** 1) MN: A147771 SN: 0064844, *TAP: SIZE: A LOC: 173 FEET FROM P LINE AT COLUMBUS, *MB: CODE: CD LOC: ON NO. TONTI, 173' FROM P.L. COLUMBUS ****/ | 2019-03-26 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900418101 | 2019-03-14 | LEAD | 1330 | KERLEREC |  | WILK | LOCATION: 111873 MTR# A 435650 INSP L UDUEBOR STATES INLET SERVICE IS LEAKING. PLEASE REPAIR. INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A140573 SN: 0025775, *TAP: SIZE: B LOC: 195 FEET FROM P LINE AT VILLERE, *MB: CODE: CD LOC: ON KERLEREC 195FT FROM VILLERE ****/ | 2019-04-02 | EXCAVATED 4 X 4 BRICK SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900418201 | 2019-03-14 | LEAD | 820 | UNION |  | WMLK | WM -- LEAK IN STREET LEAK ON WATER MAIN IN AN ASPHALT STREET /** 1) MN: D004814 SN: 0081317, *TAP: SIZE: C LOC: 163 FEET FROM P LINE AT CARONDELET, *MB: CODE: BEM4 LOC: ON UNION ST 162.5' FROM PL CARONDELET ** 2) MN: SN: 0000000, *TAP: SIZE: __ LOC: 166 FEET FROM P LINE AT CARONDELET, *MB: CODE: __ LOC: 15' P.L. UNION -166' P.L. CARONDELET ****/ | 2019-05-25 | EXCAVATED 8 X 7 STREET CUT MADE REPAIR ON ABANDON INLET SERVICE AT MAIN BACKFILLED AND CLEANED THE AREA
201900418702 | 2019-03-30 | LEAD | 2557 | N PRIEUR | FRANKLIN AV | WILK | EXAMINED PUMPED INSIDE METER BOX DOWN AND FOUND LEAK BEHIND METER BOX UNABLE TO MAKE REPAIR DUE TO BLACK ACURA ON JOB SITE (CG) CUSTOMER STATES BLACK ACURA HAS MOVED FROM AREA BLOCKING METER 04/08/19 /** 1) MN: A316268 SN: 0112322, *TAP: SIZE: B LOC: 136 FEET FROM P LINE AT PAINTERS, *MB: CODE: BDN2 LOC: 135FT FROM PL PAINTERS 9' OUTSIDE PL ** 2) MN: SN: 0112322, *TAP: SIZE: B LOC: 137 FEET FROM P LINE AT PAINTERS, *MB: CODE: CD LOC: ON N PRIEUR 137' FROM P.L. PAINTERS 9'OUTSIDE 2'IN ****/ | 2019-04-10 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH ABANDON INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSNAD AND COLDMILL
201900421501 | 2019-03-14 | LEAD | 2424 | EADS |  | WOLK | MI LEAK ON THE SIDEWALK EXAMINE OUTLET SERVICE FOR A LEAK /** 1) MN: A341325 SN: 0075315, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CDLN LOC: ON EADS 134' FROM URPL OF DORGENOIS N ****/ | 2019-04-10 | EXCAVATED 2 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND NO LEAK ON OUTLET
201900422001 | 2019-03-14 | LEAD | 3907 | DUMAINE | PICHELOUP PL | WILK | ML- METER LEAK MTR # B028565 ACCT # 153450-701896 CHANGED FROM 3909 DUMAINE INLET SERVICE LEAK BEHIND CURB COCK ENTERING METER BOX /** 1) MN: B014614 SN: 0089392, *TAP: SIZE: C LOC: 50 FEET FROM P LINE AT PICHELOUP PL, *MB: CODE: BD LOC: ON DUMAINE, 51' FROM P.L. PICHELOUP PL.,8' OUTSIDE ****/ | 2019-04-01 | EXCAVATED 2 X 4 MUD PLOT FOUND LEAK ON 3/4 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900422101 | 2019-03-14 | LEAD | 1014 | ROYAL | ST PHILIP | WILK | **********PICK UP********** INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: C024545 SN: 0029262, *TAP: SIZE: C LOC: 103 FEET FROM P LINE AT ST PHILIP, *MB: CODE: BER6 LOC: 5 APTS 102' P.L. ST PHILIP ****/ | 2019-04-10 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 1 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND COLDMILL
201900423401 | 2019-03-14 | LEAD | 1801 | N TONTI |  | WILK | ML-METER LEAK ACCT#131006-490137 MTR#A339790 INLET SERVICE LEAK /** 1) MN: A339790 SN: 0064292, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT TONTI N, *MB: CODE: ADHL LOC: SIDE ST CURB END OF HOUSE ON HAVANA 52' P.L. ****/ | 2019-04-02 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900426001 | 2019-03-15 | LEAD | 1247 | TENNESSEE |  | WILK | ML--METER LEAK ACCOUNT # 304307-711825 METER#A430257 INLET SERVICE LEAK IN METER BOX /** 1) MN: A322339 SN: 0106966, *TAP: SIZE: A LOC: 141 FEET FROM P LINE AT URQUHART, *MB: CODE: ADL LOC: MTR 141FT FROM PL URQUHART ON TENNESSEE 9FT OUTSD ****/ | 2019-04-01 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK 5/8 INCH HANDWHEEL + DAMAGEDE 5/8 INCH WATER METER ALSO RAISED 5/8 INCH METER BOX BOTTOM TO GRADE BACKFILLED UP AREA OLD METER INFO: A430257 FACT:16355846 MAKE: HERSEY READ:142
201900426202 | 2019-03-31 | LEAD | 1035 | MOSS | ST JOHN CT | WILK | LOCATE WATER METER ..EXAMINED JOB AT ABOVE LOCATION AND FOUND NO TAP INFORMATION NEED TO RAN FROM MAIN REFER BACK TO ZONE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-02 | EXCAVATED IN CONCRETE SIDEWALK + ASPHALT STREET + INSTALLED ONE 3/4 INCH WATER SERVICE FROM WATER MAIN TO PROPERTY ALSO SET 5/8 INCH METER COMPACTED BACKFILL + DRESSED UP AREA
201900426601 | 2019-03-15 | LEAD/PLASTIC | 3439 | PALMYRA | S CLARK | WILK | WM - LEAK IN THE STREET INLET SERVICE LEAK BEHIND CURB COCK, LEAKING FROM BLEERDER /** 1) MN: A133058 SN: 0066539, *TAP: SIZE: A LOC: 33 FEET FROM P LINE AT PALMYRA, *MB: CODE: ADKL LOC: ON S CLARK 32.5FT FROM PL OF PALMYRA ****/ DOTTIE READY 3-21-19 EXP 4-10-19 | 2019-03-24 | REPLACED 5/8 CURB COCK ALSO RAISE METER TO GRADE.
201900426701 | 2019-03-15 | LEAD | 3010 | PAUGER | N TONTI | WILK | ML - METER LEAK MTR # A416229 ACCT # 268419-720838 INLET SERVICE LEAK METER KEEPS EXPANDING /** 1) MN: A114907 SN: 0060870, *TAP: SIZE: A LOC: 87 FEET FROM P LINE AT TONTI N, *MB: CODE: CDLM LOC: ON PAUGER 86.6' FROM LPL N TONTI ****/ | 2019-03-29 | EXAMINE JOB AT ABOVE LOCATION FOUND NO LEAK
201900429501 | 2019-03-15 | LEAD | 2346 | N MIRO |  | WMTLK | LOCATION: 168294 MTR# A 433690 INSP UDUEBOR STATES INLET & OUTLET NOT LINING UP. OUTLET WASHER LEAKING. PLEASE REPAIR. EXAMINE INLET AND OUTLET SERVICE FOR A LEAK, METER BOX UNDER WATER /** 1) MN: A328286 SN: 0110052, *TAP: SIZE: B LOC: 107 FEET FROM P LINE AT SPAIN, *MB: CODE: CDK6 LOC: ON NO. MIRO, 107' FROM P.L. SPAIN, 10' OUTSIDE ****/ | 2019-03-29 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900429601 | 2019-03-15 | LEAD | 707 | CAFFIN AV |  | WMTLK | ML--METER LEAK ACCOUNT # 103761-425214 METER#A326038 EXAMINE INLET AND OUTLET SERVICE FOR A LEAK, METER BOX UNDER WATER /** 1) MN: SN: 0042567, *TAP: SIZE: A LOC: 36 FEET FROM P LINE AT ROYAL, *MB: CODE: BFZ LOC: ON CAFFIN AVE 36,5FT FROM LRPL OF ROYAL ****/ | 2019-04-01 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900430501 | 2019-03-16 | LEAD | 926 | N JOHNSON |  | WMTLK | WM-LEAK ON THE SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** 1) MN: A253281 SN: 0037572, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT ST PHILIP, *MB: CODE: BDL2 LOC: NR DR AT 924 - 134' P.L. ST PHILIP ****/ | 2019-03-20 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900433501 | 2019-03-18 | LEAD | 1907 | ORLEANS AV | N ROMAN | WMTLK | LOCATION ID #146734 MTR# A367052 UNDERGROUND LEAK AROUND METER /** 1) MN: A324974 SN: 0030495, *TAP: SIZE: B LOC: 63 FEET FROM P LINE AT ROMAN, *MB: CODE: ADL LOC: ON ORLEANS AVE 62' FROM SPL N ROMAN ****/ | 2019-04-23 | EXCAVATED 2 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900433801 | 2019-03-18 | LEAD | 1336 | SPAIN | N VILLERE | WOLK | MI- CONS ON METER PER INSPECTOR METER # A-4319801 ACCT # 130088-711258 /** 1) MN: A264160 SN: 0045107, *TAP: SIZE: A LOC: 50 FEET FROM P LINE AT VILLERE N, *MB: CODE: AE1 LOC: ON SPAIN,50.6' FROM U.R.P.L. NO. VILLERE ****/ | 2019-04-11 | EXCAVATED IN BRICK SIDEWALK + REPLACED 5/8 INCH HANDWHEEL BACKFILLED + DRESSED UP AREA
201900434001 | 2019-03-18 | LEAD | 1907 | ORLEANS AV | N ROMAN | WOLK | ML MTR# A367052 LOC & CUST# 146734-525394 SERVICE ADDRESS: 1907 ORLEANS AVE INSP COMM: F/ON- L/OFF, RD. 16146.... CONS REG ON THE MTR PERFORM S&W TEST, CONS CONTINUE TO RUN. PROP APPEARS VAC /** 1) MN: A324974 SN: 0030495, *TAP: SIZE: B LOC: 63 FEET FROM P LINE AT ROMAN, *MB: CODE: ADL LOC: ON ORLEANS AVE 62' FROM SPL N ROMAN ****/ | 2019-04-01 | EXAMINED JOB AT ABOVE LOCATION FOUND NO LEAK ON OUTLET SERVICE
201900435501 | 2019-03-18 | LEAD | 1212 | N ROCHEBLAVE |  | WMTLK | LOCATIONID#135500-523918 METER#A402561 LEAK INSIDE METERBOX /** 1) MN: A225881 SN: 0066204, *TAP: SIZE: A LOC: 106 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: C LOC: ON NO. ROCHEBLAVE, 109' FROM P.L. GOV. NICHOLLS ****/ | 2019-04-01 | REPLACE BOTH INLET AND OUTLET WASHERS METER BOX CASING AT ABOVE LOCATION
201900435701 | 2019-03-18 | LEAD | 707 | N GALVEZ |  | WMTLK | LOCATIONID#219970-526812 METER#C035429 LEAK INSIDE METERBOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-01 | REPLACED BOTH INLET AND OUT WASHERS AT ABOVE LOCATION
201900436101 | 2019-03-18 | LEAD | 6786 | DEANNE |  | WMTLK | LOCATIONID#168645-722783 METER#A369279 LEAK INSIDE METERBOX /** 1) MN: A293038 SN: 0115582, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT PINES BL, *MB: CODE: ADLM LOC: RES 112FT PL PINES BL 7' OUTSIDE 2' INSIDE CURB ****/ | 2019-03-28 | EXCAVATED DOWN ON INLET SERVICE FROM METER TO CURB. FOUND LEAD AND CURB COCK WAS LEAKING. MADE REPAIRS BY REPLACING COCK WASHERS. BACKFILLED.
201900438501 | 2019-03-18 | LEAD | 3830 | ORLEANS AV | N SCOTT | WILK | WM-LEAK IN SIDEWALK EXAMINE INLET SERVICE FOR LEAK INSIDE BOX IN SIDEWALK /** 1) MN: A314183 SN: 0060652, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT SCOTT N, *MB: CODE: CE LOC: 99FT FROM RPL SCOTT ****/ | 2019-03-28 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL ALSO REPLACE CHOKE 5/8 INCH METER AT ABOVE LOCATION ***************OLD METER INFO************** METER:A314183 FAC:53072066 MAKE:SENSUS READ:13681
201900438601 | 2019-03-18 | LEAD | 2227 | N PRIEUR | ELYSIAN FIELDS AV | WILK | WM- LEAK IN THE SIDE INLET SERVICE LEAK INSIDE BOX /** 1) MN: A118991 SN: 0068414, *TAP: SIZE: A LOC: 202 FEET FROM P LINE AT ELYSIAN FIELDS, *MB: CODE: AD LOC: ON N PRIEUR 202' FROM PL OF ELYSIAN FIELDS ****/ | 2019-03-28 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900441301 | 2019-03-18 | LEAD | 834 | LESSEPS | BURGUNDY | WOLK | INSP L UDUEBOR HAD LOCATION FOR CHANGE ORDER. UNABLE TO SET NEW METER, WHEEL BROKEN. CUSTOMER WAITING ON WATER. PLEASE REPAIR AND SET 5/8 METER. LOC 131806 BROKEN HANDWHEEL. ALSO RESET ONE 5/8 METER AS REQUESTED. CUSTOMER OUT OF WATER, JOB GIVEN TO J GILLIAM /** 1) MN: A279808 SN: 0062571, *TAP: SIZE: A LOC: 260 FEET FROM P LINE AT DAUPHINE, *MB: CODE: ADL LOC: ON LESSEPS 261' FROM PL DAUPHINE ****/ | 2019-03-18 | EXCAVATED 2 X 2 MUD PLOT THROUGH TREE ROOTS REPLACED HANDWHEEL INSDIE METER AND SET 5/8 INCH METER BACKFILLED AND CKLEANED THE AREA
201900441701 | 2019-03-18 | LEAD | 1017 | ANDRY |  | WMTLK | ML - METER LEAK ACCOUNT NUMBER - 140213-424914 METER NUMBER - B040080 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: B023847 SN: 0070957, *TAP: SIZE: B LOC: 154 FEET FROM P LINE AT RAMPART N, *MB: CODE: CDL LOC: ON ANDRY 154FT FROM N RAMPART ****/ | 2019-04-01 | REPLACED 3/4 INCH HANDWHEEL + GUTS IN METER BOX ALSO REPLACED DAMAGED 3/4 INCH WATER METER OLD METER INFO: B040080 FACT: 15500512 MAKE: HERSEY READ: 222
201900444701 | 2019-03-18 | LEAD | 2900 | URSULINES AV | N DUPRE | WILK | ML- METER LEAK MTR# A294355 ACCT# 125210-521011 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A294355 SN: 0047354, *TAP: SIZE: C LOC: 34 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: OOO LOC: ON S DUPRE 53FT FROM PL URSULINES AVE ** 2) MN: A318741 SN: 0047354, *TAP: SIZE: C LOC: 54 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: OOOO LOC: ON NO. DUPRE, 53' FROM P.L. URSULINES AVE., 6' ****/ | 2019-04-01 | EXCAVATED 2 X 4 MUD PLOT AND FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900446901 | 2019-03-19 | LEAD | 2245 | N VILLERE |  | WMTLK | LOCATIONID#104564-481588 METER#A416496 LEAK INSIDE METERBOX /** 1) MN: A247439 SN: 0007279, *TAP: SIZE: A LOC: 29 FEET FROM P LINE AT MARIGNY, *MB: CODE: CEK LOC: ON N VILLERE 29FT FROM ISPL OF MARIGNY ****/ | 2019-03-27 | EXCAVATED 4 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND COLDMILL
201900447001 | 2019-03-19 | LEAD | 2247 | N VILLERE |  | WMTLK | LOCATIONID#112499-717426 METER#A326307 LEAK INSIDE METERBOX /** 1) MN: A192244 SN: 0014367, *TAP: SIZE: A LOC: 85 FEET FROM P LINE AT MARIGNY, *MB: CODE: AFN2 LOC: 85' P.L. MARIGNY ****/ | 2019-03-27 | EXCAVATED 4 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201900450001 | 2019-03-19 | LEAD | 1936 | N TONTI |  | WILK | INSP L UDUEBOR HAD LOCATION FOR AN EXAMINE SERVICE ORDER. FOUND OUTLET SERVICE LEAK, NO WASHER LEAK. PLEASE REPAIR METER A403241 LOC 155880 INLET SERVICE LEAK IN PREVIOUS CUT /** 1) MN: A311753 SN: 0087267, *TAP: SIZE: A LOC: 36 FEET FROM P LINE AT ALLEN, *MB: CODE: CDK LOC: ON NO. TONTI, 35.5' FROM P.L. ALLEN,8.5' OUTSIDE ****/ | 2019-03-27 | EXAMINE JBO AT ABOVE LOCATION FOUND NO LEAK ON INLET OR OUTLET
201900450801 | 2019-03-19 | LEAD | 1515 | TUPELO |  | WMRE | INSP L UDUEBOR STATES SERVICE HAS OUTLET SERVICE LEAK AND WHIP NEEDS TIE IN. PLEASE REPAIR METER A433653 LOC 307154 LOCATE, RAISE TO GRADE ALSO OUTLET TIE IN, HOUSE UNDER RENOVATION /** 1) MN: A317789 SN: 0095305, *TAP: SIZE: A LOC: 98 FEET FROM P LINE AT NO. ROBERTSON, *MB: CODE: BDLM LOC: ON TUPELO, 98' FROM P.L. NO. ROBERTSON, 8' OUTSIDE ****/ | 2019-03-22 | EXCAVATED 2 X 4 CONCRETE SIDEWALK RENEW 5/8 INCH OUTLET SERVICE FROM METER BOX TO PROPERTY TIE INTO 3/4 INCH PLASTIC LINE BACKFILLED JOB WITH RIVERSAND LEFT ONE SAFETY CONE PILE NEED TO BE PICKED UP
201900455001 | 2019-03-19 | LEAD/PLASTIC | 6019 | CHAMBERLAIN DR | BURBANK DR | WILK | WM- LEAK BETWEEN SIDEWALKAND THE STREET INLET SERVICE LEAK IN SIDEWALK FLOODING STREET /** 1) MN: B021944 SN: 0121204, *TAP: SIZE: B LOC: 195 FEET FROM P LINE AT BURBANK DR, *MB: CODE: ADL4 LOC: 191FT PL BURBANK DR 7' OUTSIDE 8' INSIDE CURB ****/ | 2019-05-01 | EXCAVATED A 5 X 9 MUD PLOT CUT IN TREE ROOTS . REPAIR INLET SERVICE LEAK MULTIPLE TIMES, RAISED 3/4" METER BOX TO GRADE & RENWED OUTLET SERVICE FROM METER TO P.L BACKFILLED JOBSITE FOUN LEAD INLET SERVICE
201900455401 | 2019-03-19 | LEAD | 1003 | LAMANCHE | N RAMPART | WILK | WM-LEAK IN THE STREET FLOODING AREA INLET SERVICE LEAK IN MUDPLOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-01 | EXCAVATED IN MUD PLOT + GUTTER BOTTOM + REPLACED 5/8 INCH HANDWHEEL BACKFILLED DRESSED UP AREA
201900455801 | 2019-03-20 | LEAD | 3005 | N CLAIBORNE AV | MONTEGUT | WOLK | MI- CONS ON METER PER INSPECTOR METER # A-340572 ACCT #155310-716948 /** 1) MN: A133316 SN: 0090216, *TAP: SIZE: B LOC: 48 FEET FROM P LINE AT MONTEGUT, *MB: CODE: AEL1 LOC: 46FT FROM PL MONTEGUT 7.5 OUTSIDE P/L 1.5 INSIDE ****/ | 2019-04-04 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900456801 | 2019-03-20 | LEAD | 1579 | N PRIEUR |  | WMTLK | LOCATIONID#301118-701073 METER#A424004 LEAK INSIDE METERBOX /** 1) MN: A317733 SN: 0062725, *TAP: SIZE: A LOC: 36 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: BDK LOC: ON NO. PRIEUR,34' FROM U.S.P.L. LAPEYROUSE ****/ | 2019-04-02 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND
201900457101 | 2019-03-20 | LEAD | 809 | POLAND AV | DAUPHINE | WOLK | ML MTR# A282796 LOC & CUST# 209512-718849 SERVICE ADDRESS: 809 POLAND AVE INSP COMM: F/ON-L/ON (OCC) RD. 2186.... CONS REG ON MTR, NO VISIBLE FAUCET /** 1) MN: A141566 SN: 0047344, *TAP: SIZE: D LOC: 63 FEET FROM P LINE AT DAUPHINE, *MB: CODE: CD LOC: ON POLAND 62' FROM P.L. DAUPHINE 9'OUTSIDE 3'IN- ** 2) MN: A330882 SN: 0047344, *TAP: SIZE: D LOC: 63 FEET FROM P LINE AT DAUPHINE, *MB: CODE: CD LOC: ON POLAND 63' FROM P.L. DAUPHINE 9'OUTSIDE 3'IN- THERE ARE 2 MORE NOT LISTED. ****/ | 2019-04-04 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900460901 | 2019-03-20 | LEAD | 417 | S RAMPART |  | WILK | MI LEAK ON SIDEWALK INLET SERVICE LEAK BETWEEN CURB AND STREET /** 1) MN: D006661 SN: 0028254, *TAP: SIZE: D LOC: 161 FEET FROM P LINE AT PERDIDO, *MB: CODE: AEN6 LOC: ON SO. RAMPART,161' FROM P.L. PERDIDO,6' OUTSIDE ** 2) MN: SN: 0028256, *TAP: SIZE: B LOC: 166 FEET FROM P LINE AT PERDIDO, *MB: CODE: __ LOC: ON S RAMPART 166' FROM USPL PERDIDO ****/ | 2019-03-30 | MADE 6 X 6 CUT IN CONCRETE BASE STREET AND TIGHEN UP FITTING ON 2 INCH SERVICE TO STOP LEAK BACKFILLED AREA SERVICE FOR ITAIIAN PIE RESTAURANT
201900462301 | 2019-03-20 | LEAD | 1138 | CHARTRES | GOV NICHOLLS | WILK | MI- LEAK IN THE STREET INLET SERVICE LEAK BETWEEN CURB/ASPHALT STREET GETTING OFF INTO DRAIN CATCH BASIN **CHANGED FROM 1130 CHARTRES** /** 1) MN: D004806 SN: 0077466, *TAP: SIZE: D LOC: 40 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: BER6 LOC: 42FT FROM PL GOV NICHOLLS ON CHARTRES 2FT OUTSIDE ****/ | 2019-04-18 | EXCAVATED IN CONCRETE SIDEWALK + AMDE REPAIR ON 1 INCH SERVICE LINE BACKFILLED + DRESSED UP AREA. JOB COMPLETE
201900463601 | 2019-03-20 | LEAD | 851 | TAFT PL | DUMAINE | WMTLK | ML-METER LEAK METER#A314175 ACCT#140719-514213 EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: A251532 SN: 0075878, *TAP: SIZE: B LOC: 197 FEET FROM P LINE AT DUMAINE, *MB: CODE: BD LOC: ON TAFT 200' FROM PL OF DUMAINE ****/ | 2019-03-28 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND ALSO RAISE METER BOX UP TO GRADE AND REPLACE CHOKE 5/8 INCH METER OLD METER INFO: A335916 FACT: 57211321 MAKE: SENSUS READ: 1877
201900465401 | 2019-03-21 | LEAD | 1840 | CHARBONNET | N PRIEUR | WMLK | MI- LEAK BETWEEN SIDEWALK AND CURB EXAMINE WATER MAIN FOR LEAK IN STREET /** 1) MN: A335757 SN: 0156935, *TAP: SIZE: B LOC: 33 FEET FROM P LINE AT PRIEUR N, *MB: CODE: AD LOC: MTR ON CHARBONNET 30 FT FRM PL N PRIEUR 2FT INSIDE ****/ | 2019-03-31 | EXCAVATED 8 X 10 STREET CUT MADE REPAION ABANDON INLET SERVICE LINE AT AMIN BACKFILLED AND CLEANED TEH AREA. *NO METER AT THIS LOCATION* (JOB COMPLETE)
201900467401 | 2019-03-21 | LEAD | 2163 | N TONTI |  | WMTLK | LOCATIONID#209235-483748 METER#A381951 LEAK INSIDE METERBOX /** 1) MN: 000000 SN: 0061619, *TAP: SIZE: A LOC: 159 FEET FROM P LINE AT FRENCHMEN, *MB: CODE: ADK2 LOC: ON NO. TONTI,159' FROM U.S.P.L. FRENCHMEN ****/ | 2019-04-14 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION. JOB COMPLETE
201900467501 | 2019-03-21 | LEAD | 7 | PRESS | DAUPHINE | WOLK | LOCATION# 222612-427113 METER# A424279 INSPECTOR DID AN OUTSIDE INSPECTION FD CONSTANT REG ON METER NO S&WB VALVE TO TEST .PLEASE REPAIR /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-03-29 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH HANDWHEEL BACKFILL + DRESSEDUP AREA
201900467601 | 2019-03-21 | LEAD | 920 | N JOHNSON |  | WILK | WM: LEAK ON SIDEWALK *PLEASE CALL UPON ARRIVAL* CHANGED FROM 922 N JOHNSON INLET SERVICE LEAK, NO METER IN BOX, WATER PASSING IN OFF POSITION /** 1) MN: SN: 0046668, *TAP: SIZE: A LOC: 145 FEET FROM P LINE AT DUMAINE, *MB: CODE: BDL2 LOC: ON N JOHNSON 146FT FROM PL OF DUMAINE ****/ | 2019-04-05 | EXCAVATED 2 X 4 BRICK SIDEWALK FOUND LEAK ON ABANDON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL. JOB COMPLETE
201900467901 | 2019-03-21 | LEAD | 1351 | ST ANTHONY AV | URQUHART | WILK | ML- METER LEAK METER# A375909 ACCT# 122522-711812 BAD BLEEDER VALVE, FOUND OFF LEFT OFF /** 1) MN: A113701 SN: 0061710, *TAP: SIZE: A LOC: 81 FEET FROM P LINE AT URQUHART, *MB: CODE: ADM LOC: ON ST. ANTHONY,109' FROM L.S.P.L. URQUHART ****/ | 2019-04-11 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA JOB COMPLETE
201900468201 | 2019-03-21 | LEAD | 1517 | KERLEREC |  | WILK | INSP L UDUEBOR STATES INLET AND OUTLET NOT LINING UP AND IT'S CAUSING SERVICE TO LEAK. PLEASE REPAIR METER B042229 LOC 104135 INLET AND OUTLET SERVICE NOT LINING UP, FOUND OFF LEFT OFF HOUSE UNDER RENOVATION /** 1) MN: B025112 SN: 0038584, *TAP: SIZE: B LOC: 125 FEET FROM P LINE AT CLAIBORNE AVE N URPL, *MB: CODE: AFNO LOC: 125' FROM LRPL CLAIRBORN AVE N ****/ | 2019-04-02 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900468401 | 2019-03-21 | LEAD | 1703 | PAULINE | N DERBIGNY | WILK | ML: METER LEAK ACCT# 149174-432491 MTR#A312521 INLET SERVICE LEAK IN BOX /** 1) MN: A312521 SN: 0081408, *TAP: SIZE: A LOC: 15 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: CDL LOC: ON PAULINE 16FT FROM PL OF N DERBIGNY ****/ | 2019-04-17 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND. JOB COMPLETE
201900469001 | 2019-03-21 | LEAD | 2312 | N PRIEUR | MANDEVILLE | WILK | WM- LEAK IN THE STREET INLET SERVICE LEAK IN MUDPLOT AT CURB GETTING OFF INTO DRAIN CATCH BASIN /** 1) MN: A232200 SN: 0054712, *TAP: SIZE: A LOC: 126 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: BDM6 LOC: ON NO. PRIEUR,126' FROM L.R.P.L. MANDEVILLE ****/ | 2019-04-14 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON ABANDON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900471501 | 2019-03-22 | LEAD | 1818 | LOUISA DR | N ROMAN | WMTLK | ML MTR# A244950 LOC & CUST# 164683-431781 SERVICE ADDRESS: 1818 LOUISA DR. INSP COMM: LK INSIDE METER, UNABLE TO TELL WHERE LEAK IS COMING FROM. FILLED UP WHEN PUMP WAS REMOVED (OCC) RD. 5557 /** 1) MN: A244950 SN: 0099849, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT ROMAN N, *MB: CODE: BG4 LOC: ON LOUISA 151' FROM PL N ROMAN 2' OUTSIDE PL 7' IN ****/ | 2019-04-17 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK COMING FURTHER BACK ON PROPERTY REFER TO (P.O.P) FOR REPAIR TO BE MADE BACKFILLED JOB WITH RIVERSAND
201900471901 | 2019-03-22 | LEAD | 2206 | ANNETTE | N MIRO | WMTLK | LOCATIONID#134263-495068 METER#A432508 LEAK INSIDE METERBOX /** 1) MN: A275072 SN: 0065031, *TAP: SIZE: A LOC: 53 FEET FROM P LINE AT MIRO N, *MB: CODE: __ LOC: ON ANNETTE 51' FROM PL OF MIRO ****/ | 2019-04-13 | REPLACE BROKEN 5/8 INCH HANDWHEEL AT ABOVE LOCATION
201900475201 | 2019-03-22 | LEAD | 5415 | URQUHART | ANDRY | WMTLK | LOCATIONID#165748-423208 METER#A395515 LEAK INSIDE METERBOX,OVERFLOWING /** 1) MN: A250689 SN: 0106017, *TAP: SIZE: A LOC: 94 FEET FROM P LINE AT ANDRY, *MB: CODE: ADK LOC: MTR ON URQUHART 94FT FROM PL ANDRY 5FT OUTSIDE PL ****/ | 2019-04-11 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND
201900476101 | 2019-03-22 | LEAD | 5923 | MARAIS | ALABO | WMTLK | LOCATIONID#188932-725679 METER#A373889 LEAK INSIDE METERBOX /** 1) MN: A283559 SN: 0089085, *TAP: SIZE: A LOC: 13 FEET FROM P LINE AT ALABO, *MB: CODE: AD LOC: 12FT PL ALABO 8' OUTSIDE ****/ | 2019-04-11 | EXCAVATED 2 X 4 MUD PLOT FOUND LEAK ON 3/4 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900476201 | 2019-03-22 | LEAD | 1531 | ARTS | CLAIBORNE AVE BRIDGE | WOLK | ACCT# 129918-724237 MTR# A419428 INSPECTOR FOUND CONSTANT REGISTRATION ON METER /** 1) MN: A153358 SN: 0059155, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: CDLM LOC: 80FT FROM LRPL N CLAIBORNE ****/ | 2019-04-11 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900478401 | 2019-03-22 | LEAD | 1521 | N DERBIGNY | COLUMBUS | WMTLK | ML- METER LEAK MN:A431378 ACCT#125485-487685 EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: A196203 SN: 0047686, *TAP: SIZE: A LOC: 160 FEET FROM P LINE AT LAHARPE, *MB: CODE: ADK LOC: 160FT FROM USPL LAHARPE ****/ | 2019-04-09 | EXCAVATED IN LIMESTONE GUTTER BOTTOM + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900478501 | 2019-03-22 | LEAD | 1627 | AGRICULTURE | PARIS AV | WILK | WM - LEAK IN THE STREET. INLET SERVICE LEAK IN GUTTER BOTTOM /** 1) MN: A246387 SN: 0066638, *TAP: SIZE: B LOC: 162 FEET FROM P LINE AT PARIS AVE, *MB: CODE: CDL LOC: 184FT FROM PL PARIS AVE ****/ | 2019-03-30 | EXAMINED AND PUMPED INSIDE METER BOX DOWN AND REPLACED WASHERS ON INLET AND OUTLET INSIDE METER BOX
201900481501 | 2019-03-23 | LEAD | 2327 | LAMANCHE | N ROCHEBLAVE | WMTLK | ML- METER LEAK METER# A397246 ACCT# 193354-421672 EXAMINE INLET/OUTLET SERVICE FOR A LEAK. FLOODING - UNABLE TO PUMP METER BOX DOWN (C) /** 1) MN: A297336 SN: 0152718, *TAP: SIZE: B LOC: 114 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BE2 LOC: RES ON LAMANCHE 114FT FROM PL ROCHEBLAVE N 5' OUTS ****/ | 2019-04-01 | EXAMINED JOB AND PUMP INSIDE METER BOX DOWN AND REPLACED WASHERS ON INLET AND OUTLET INSIDE DRIVEWAY
201900483001 | 2019-03-24 | LEAD | 638 | S LOPEZ | GRAVIER | WILK | ML-METER LEAK ACCT#105832-705976 MTR#A375692 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: SN: 0045437, *TAP: SIZE: A LOC: 137 FEET FROM P LINE AT GRAVIER, *MB: CODE: CDL1 LOC: 137 URP LINE GRAVIER ****/ DOTTIE READY 5-3-19 EXP 5-23-19 | 2019-05-04 | REPLACED 5/8 CUCRB COCK.3FT. X 3FT. MUDPLOT JOB COMPLETE
201900483501 | 2019-03-24 | LEAD | 1401 | SIMON BOLIVAR AV | THALIA | WILK | LEAK IN STREET INLET SERVICE LEAK IN ASPHALT JOB UPGRADED TO PRIORITY -A- AREA FLOODING HERMAN WILLIAMS ZONE 4 ON LOCATION AT 1725 /** 1) MN: E004017 SN: 0048010, *TAP: SIZE: E LOC: 70 FEET FROM P LINE AT THALIA, *MB: CODE: CELN LOC: IN MH 80FT FROM PL THALIA ****/ | 2019-03-24 | MADE A 12 X 10 CUT IN ASPHALT STREET + MADE REPAIR ON 2 INCH INLET SERVICE LINE COMPACTED BACKFILL + DRESSED UP AREA
201900484601 | 2019-03-25 | LEAD | 1339 | JOSEPH | PITT | WILK | ML METER LEAK ACCOUNT 139670-707490 METER #A322091 INLET SERVICE LEAK BEHIND CURB COCK /** 1) MN: A322091 SN: 0070278, *TAP: SIZE: C LOC: 131 FEET FROM P LINE AT PITT, *MB: CODE: BDLN LOC: 145' P.L. PITT ****/ DOTTIE READY 5-3-19 EXP 5-23-19 | 2019-05-04 | CHANGED 5/8 METER BOX COCK. JOB COMPLETE
201900485601 | 2019-03-25 | LEAD | 828 | LESSEPS |  | WILK | LOCATION: 109258 MTR# A 433612 INSP L. UDUEBOR STATES INLET SERVICE IS LEAKING. PLEASE REPAIR. INLET SERVICE LEAK /** 1) MN: A192115 SN: 0053991, *TAP: SIZE: A LOC: 115 FEET FROM P LINE AT BURGUNDY, *MB: CODE: ADLZ LOC: ON LESSEPS 115FT FROM BURGUNDY ****/ | 2019-04-09 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK WITH NEW ONE BACKFILLED AREA
201900486001 | 2019-03-25 | LEAD | 2047 | N ROCHEBLAVE | ANNETTE | WILK | WM - LEAK IN THE STREET INLET SERVICE LEAK IN THE STREET IN FRONT VACANT LOT /** 1) MN: B028144 SN: 0079280, *TAP: SIZE: B LOC: 153 FEET FROM P LINE AT ANNETTE, *MB: CODE: B LOC: 153' P.L. ANNETTE ****/ | 2019-03-30 | EXCAVATED 8 X 10 STREET CUT MADE REPAIR ON INLET SERVICE TO STOP LEAK BACKFILLED AND CLEANED THE AREA JOB COMPLETE
201900486901 | 2019-03-25 | LEAD | 922 | FORSTALL |  | WILK | WM--- LEAK IN BETWEENT STREET AND CURB INLET SERVICE LEAK @ THE CURB /** 1) MN: B026064 SN: 0122340, *TAP: SIZE: B LOC: 212 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CDL LOC: ON FORSTALL 210FT FROM PL BURGUNDY ****/ | 2019-03-31 | EXCAVATED 4 X 4 EXISTING STREET CUT IN RAIN MADE REPAIR ON INLET SERVICE LINE TO STOP BACKFILLD AND CLEANED THE AREA
201900488201 | 2019-03-25 | LEAD | 1707 | BENTON |  | WMLK | MI- LEAK ON THE SIDEWALK ( LEAK SITS ON THE SIDE OF THE HOME ON BENTON) EXAMINE WATER MAIN FOR A LEAK IN THE STREET /** 1) MN: B030775 SN: 0138482, *TAP: SIZE: B LOC: 67 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BEKO LOC: ON BENTON 67FT FROM PL DERBIGNY ****/ | 2019-03-31 | EXCAVATED 8 X 6 STREET CUT ALSO AN ADDITIONAL 6 X 6 STREET CUT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA LEFT TWO BARRELS ON EACH STREET CUT
201900489201 | 2019-03-25 | LEAD | 3162 | N VILLERE | LOUISA | WILK | WM- LEAK ON THE SIDEWALK INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A211921 SN: 0054909, *TAP: SIZE: A LOC: 56 FEET FROM P LINE AT LOUISA, *MB: CODE: ABDL LOC: 47' P.L. LOUISA ****/ | 2019-04-22 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND. JOB COMPLETE
201900495501 | 2019-03-26 | LEAD | 1936 | CLOUET | N JOHNSON | WILK | WM- LEAK BETWEE THE STREET AND CURB INLET SERVICE LEAK /** 1) MN: A272276 SN: 0084170, *TAP: SIZE: A LOC: 295 FEET FROM P LINE AT PRIEUR N, *MB: CODE: CD LOC: ON CLOUET ST 295' FROM PL N PRIEUR ****/ | 2019-04-16 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND
201900499401 | 2019-03-27 | LEAD | 1555 | N BROAD |  | WMTLK | ML METERLEAK MTR#A425800 LOC/CUST#302049-708503 CHK FOR POSS LEAK AT METER. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-05 | EXAMINED JOB AT ABOVE LOCATION FOUND NO LEAK ON INLET OR OUTLET
201900500701 | 2019-03-27 | LEAD | 1840 | MANDEVILLE | N PRIEUR | WMTLK | ML- METER LEAK ACCT# 207992-483186 MTR# A342100 EXAMINE INLET/OUTLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: 000000 SN: 0065673, *TAP: SIZE: A LOC: 63 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: BDH6 LOC: ON N PRIEUR ST 63' FROM PL MANDEVILLE ST ****/ | 2019-03-29 | EXCAVATED 4 X 4 LIMESTONES GUTTER BOTTOM FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900500901 | 2019-03-27 | LEAD | 1874 | N MIRO |  | WOLK | MI-LEAK ON SIDEWALK ** CUST STATES NEAR FENCE** OUTLET SERVICE LEAK IN SIDEWALK CONSTANT REGISTRATION ON METER /** 1) MN: C021943 SN: 0149023, *TAP: SIZE: C LOC: 46 FEET FROM P LINE AT ALLEN, *MB: CODE: CEH LOC: 46FT FRIN OK ALLEN 8FT OUTSIDE PL 3' INSIDE CURB O ****/ | 2019-03-29 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK ON 1 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900501501 | 2019-03-27 | LEAD | 2138-40 | PAUGER | N ROBERTSON | WILK | MI - CUT SERVICE CUT BY- GRADY CRAWFORD LLC 1000 LNA ROAD METAIRIE LA 70001 CUT INLET SERVICE BY GRADY CRAWFORD LLC CUSTOMER OUT OF WATER **DAMAGE CLAIM** **CHANGED FROM 2140 PAUGER** /** AT 2138: 1) MN: A346641 SN: 0050498, *TAP: SIZE: A LOC: 55 FEET FROM P LINE AT BOURBON, *MB: CODE: BDHL LOC: ON N ROBERTSON 56' FROM URPL BOURBON ** AT 2140: 2) MN: 000000 SN: 0050498, *TAP: SIZE: B LOC: 56 FEET FROM P LINE AT PAUGER, *MB: CODE: BDHL LOC: ON N ROBERTSON 54FT PL PAUGER 10' OUTSIDE 2' IN- ****/ | 2019-03-27 | ARRIVED AT ABOVE LOCATION + FOUND A CUT 3/4 INCH INLET SERVICE LINE BY GRADY / CRAWFORD CON COMPANY MADE REPAIR ON 3/4 INCH INLET SERVICE FORCE ACCOUNT GRADY/CRAWFORD CON COMPANY FOR REPAIR
201900502301 | 2019-03-27 | LEAD | 1635 | ST MAURICE AV | N CLAIBORNE AV | WILK | WM- LEAK BETWEEN SIDEWALK AND CURB INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A276204 SN: 0128205, *TAP: SIZE: B LOC: 271 FEET FROM P LINE AT NO. CLAIBORNE AVE., *MB: CODE: CDN1 LOC: ON ST. MAURICE AVE., 271' FROM P.L. NO. CLAIBORNE ****/ | 2019-04-13 | EXAMINED JOB AT ABOVE LOCATION FOUND LEAK ON 5/8 INCH BROKEN HANDWHEEL REPLACE HANDWHEEL AND WASHERS
201900503101 | 2019-03-27 | LEAD | 2124 | ONZAGA |  | WILK | WM-- LEAK BETWEEN SIDEWALK AND STREET EXAMINE INLET SERVICE LEAK IN ASPHALT STREET /** 1) MN: A266950 SN: 0067851, *TAP: SIZE: B LOC: 200 FEET FROM P LINE AT GALVEZ S, *MB: CODE: BDMN LOC: ON ONZAGE 200' FROM PL OF GALVEZ S ****/ | 2019-04-04 | MADE 6 X 6 STREET CUT IN SERVERE HEAVY RAINNING CONDITION AND MADE REPAIR ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201900505101 | 2019-03-28 | LEAD | 2721 | REPUBLIC |  | WOLK | ML METERLEAK MTR#A329185 LOC/CUST#136791-714426 CONS REG ON METER. /** 1) MN: A329185 SN: 0067334, *TAP: SIZE: A LOC: 160 FEET FROM P LINE AT INDUSTRY, *MB: CODE: BDK LOC: ON REPUBLIC, 160' FROM L.R.P.L. INDUSTRY ****/ | 2019-04-10 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900505201 | 2019-03-28 | LEAD | 1738 | N DORGENOIS |  | WOLK | ACCOUNT #109872-713808 METER #A423200 CONS REG ON METER LEAK AT WHEEL /** 1) MN: A116500 SN: 0006329, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT AUBRY, *MB: CODE: CF LOC: 42FT FROM USPL AUBRY ****/ | 2019-04-05 | EXAMINE JOB AT ABOVE LOCATION FOUND LEAK INSIDE OF METER BOX REPLACE 5/8 INCH BROKEN HANDWHEEL AND WASHERS NO CON REG ON METER
201900505301 | 2019-03-28 | LEAD | 1324 | LESSEPS |  | WILK | LOCATIONID#133320-511536 METER#A191465 BLEEDER LEAK /** 1) MN: A191465 SN: 0064169, *TAP: SIZE: A LOC: 205 FEET FROM P LINE AT URQUHART, *MB: CODE: OOO LOC: ON LESSEPS ST 205' FROM URQUHART ST 1' FROM CURB ****/ | 2019-04-09 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900505601 | 2019-03-28 | LEAD | 1039 | MAZANT |  | WMTLK | LOCATIONID#149761-719034 METER#A316449 LEAK INSIDE METERBOX /** 1) MN: A334944 SN: 0082424, *TAP: SIZE: __ LOC: 261 FEET FROM P LINE AT RAMPART N, *MB: CODE: BDF LOC: ON MAZANT 261FT FROM PL N RAMPART ****/ | 2019-04-09 | EXCAVATED 4 X 4 LIMESTONES GUTTER BOTTOM FOUND LEAK ON 5/8 INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201900505701 | 2019-03-28 | LEAD | 1025 | ALVAR |  | WMTLK | LOCATIONID#110514-424559 METER#A260965 LEAK INSIDE METERBOX /** 1) MN: A260965 SN: 0060928, *TAP: SIZE: B LOC: 185 FEET FROM P LINE AT RAMPART N, *MB: CODE: CDL3 LOC: ON ALVAR 185.5' FROM LSPL N RAMPART ****/ | 2019-04-03 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201900505801 | 2019-03-28 | LEAD | 1035 | DESIRE |  | WMTLK | LOCATIONID#114884-727590 METER#A283374 LEAK INSIDE METERBOX /** 1) MN: A283374 SN: 0017833, *TAP: SIZE: A LOC: 148 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: CELM LOC: 151FT FROM LRPL ST CLAUDE ON DESIRE ****/ | 2019-04-09 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900505901 | 2019-03-28 | LEAD | 1041 | INDEPENDENCE |  | WMTLK | LOCATIONID#122362-427762 METER#A415926 LEAK INSIDE METERBOX /** 1) MN: A337488 SN: 0040968, *TAP: SIZE: A LOC: 77 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: CDLM LOC: 77FT FROM URPL ST CLAUDE METER ON INDEPENDENCE ****/ | 2019-04-09 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL CHANGE ADDRESS FROM 1041 TO 1043 INDEPENDENCE ST
201900506001 | 2019-03-28 | LEAD | 925 | GALLIER |  | WMTLK | LOCATIONID#117848-525546 METER#A181287 LEAK INSIDE METERBOX /** 1) MN: A181287 SN: 0056364, *TAP: SIZE: A LOC: 123 FEET FROM P LINE AT RAMPART N, *MB: CODE: CELM LOC: BY FENCE 123' P.L. N RAMPART ****/ | 2019-04-03 | EXCAVATED 2 X 4 CONCRTE SIDEWALK FOUND LEAK ON 5/8 INCH SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201900507101 | 2019-03-28 | LEAD | 2709 | ST CLAUDE AV |  | WMTLK | 140430/479885 METER#A402816 AREA FLOODING/METER LEAK /** 1) MN: A115367 SN: 0005706, *TAP: SIZE: B LOC: 89 FEET FROM P LINE AT PORT, *MB: CODE: CDM1 LOC: 89' P.L. PORT ****/ | 2019-04-12 | REMOVED BRICK BASE CEMENT GARDEN BASE AND MADE REPAIR ON WHEEL INSIDE METER BOX BACKFILLED AREA. JOB COMPLETE
201900507202 | 2019-04-15 | LEAD | 2339 | URQUHART |  | WMTBG | EXCAVATED 4 X 4 LIMESTONE DRIVEWAY WAS UNABLE TO LOCATE METER BOX REFER TO ZONE 4 TO LOCATE METER BOX ON (SPAIN ) MARKED WITH BLUE PAINT IN THE STREET /** 1) MN: A308967 SN: 0057988, *TAP: SIZE: A LOC: 46 FEET FROM P LINE AT URQUHART, *MB: CODE: BFHK LOC: ON SPAIN ST 46' FROM URPL URQUHART ST ****/ | 2019-04-24 | EXCAVATED IN LIMESTONE DRIVEWAY + LOCATED 5/8 INCH METER BOX MARKED WITH BLUE PAINT
201900507303 | 2019-05-01 | LEAD | 1301 | PRESS |  | WMTBG | EXCAVATED 4 X 6 LIMESTONE NEAR POLE REFER TO ZONE 4 FOR A MACHINE MEASUREMENT GIVEN BY S+ WB WAS UNABLE TO LOCATE METER /** 1) MN: C024929 SN: 0055930, *TAP: SIZE: C LOC: 3 FEET FROM P LINE AT PRESS DR, *MB: CODE: DZ7 LOC: ON OPPOSITE SIDE OF STREET AT CORNER OF PRESS AND ****/ | 2019-05-09 | LOCATED AND RAISE METER BOX UP TO GRADE AT ABOVE LOCATION ALSO REPLACE BROKEN 1 INCH WATER METER OLD METER INFO: C0345959 FACT: 15508921 MAKE: HERSEY READ: 9960
201900507401 | 2019-03-28 | LEAD | 1338 | ARTS |  | WMTBG | 130523-481897 METER#A323366 METER BURIED/CANT LOCATE /** 1) MN: A211450 SN: 0060340, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT ARTS, *MB: CODE: BDH3 LOC: ON N VILLERE 65' FROM PL ARTS ****/ | 2019-04-14 | EXCAVATED AND LOCATED METER BOX IN BRICK GUTTER BOTTOM REPLACED BROKEN METER BOX CASING AND MARKED IN STREET WITH BLUE PAINT METER IS 5 FT INSIDE FROM CURB. JOB COMPLETE
201900511201 | 2019-03-28 | LEAD | 2231 | ARTS | N MIRO | WMTLK | WM-LEAK ON THE SIDEWALK CHANGED FROM 2227 ARTS EXAMINE INLET/OUTLET SERVICE INSIDE METER BOX FOR A LEAK UNABLE TO PUMP DOWN /** 1) MN: A284274 SN: 0079403, *TAP: SIZE: A LOC: 233 FEET FROM P LINE AT MIRO N, *MB: CODE: BDMN LOC: 233FT FROM PL N MIRO 4FT FROM CURB ****/ | 2019-04-12 | EXCAVATED IN MUD PLOT AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BEHIND METER BOX BACKFILLED AREA. JOB COMPLETE
201900512501 | 2019-03-28 | LEAD | 424 | N GALVEZ | ST LOUIS | WMTLK | ML: METER LEAK METER# A372073 ACCT# 304511-422054 CHANGED FROM 434 N GALVEZ EXAMINE INLET/OUTLET SERVICE FOR A LEAK METER BOX UNDER WATER /** 1) MN: A272726 SN: 0050097, *TAP: SIZE: A LOC: 85 FEET FROM P LINE AT ST LOUIS, *MB: CODE: BDK LOC: METER ON N GALVEZ 86.3 FT FROM PL ST LOUIS ****/ | 2019-04-02 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900518101 | 2019-03-29 | LEAD | 1726 | TRICOU | N DERBIGNY | WILK | ML: METER LEAK ACCT #168223-724027 MTR# A428160 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A114173 SN: 0125579, *TAP: SIZE: A LOC: 198 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: DLM LOC: RES ON TRICOU 198FT FROM PL DERBIGNY 7' OUTSIDE PL ****/ | 2019-04-03 | PUMPED DOWN GUTTER BOTTOM + STOPPED LEAK IN METER BOX
201900518401 | 2019-03-29 | LEAD | 2225 | MARAIS |  | WOLK | WM-LEAK ON THE SIDEWALK CHECK FOR LEAK AT PROPERTY LINE CONSTANT REGISTRATION ON METER FLOODING SIDEWALK *CHANGED FROM 2221-23 MARAIS /** AT 2221: 1) MN: A118858 SN: 0024105, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT MARAIS, *MB: CODE: BF7 LOC: 112' P.L. MARIGNY ****/ | 2019-04-10 | EXCAVATED 4 X 4 BRICK SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201900518801 | 2019-03-29 | LEAD | 2645 | GOV NICHOLLS |  | WILK | ML--METER LEAK ACCOUNT #235467-412481 METER #A306651 INLET SERVICE LEAK IN METER BOX CURBCOCK LEAKING /** 1) MN: A300357 SN: 0043963, *TAP: SIZE: A LOC: 147 FEET FROM P LINE AT BROAD N, *MB: CODE: BF LOC: ON GOV NICHOLLS 147FT FROM BROAD N ****/ | 2019-04-12 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900519001 | 2019-03-29 | LEAD | 1638 | N TONTI | ONZAGA | WMTLK | ML: METER LEAK ACCT#128690-487544 MTR#A417868 EXAMINE INLET/OUTLET SERVICE FOR LEAK INSIDE METER BOX UNABLE TO PUMP OUT METER /** 1) MN: A330538 SN: 0066821, *TAP: SIZE: __ LOC: 56 FEET FROM P LINE AT TONTI N, *MB: CODE: HL LOC: SIDE ST EDGE OF 4TH WINDOW ON ONZAGA 56' P.L. ****/ | 2019-04-05 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION. JOB COMPLETE
201900524901 | 2019-04-01 | LEAD | 2216 | D"ABADIE |  | WILK | ML METER LEAK ACCOUNT #172367-488953 METER#A392120 EXAMINE INLET SERVICE FOR LEAK INSIDE BOX ON SIDEWALK /** 1) MN: A313658 SN: 0058564, *TAP: SIZE: A LOC: 127 FEET FROM P LINE AT MIRO N, *MB: CODE: ADKN LOC: 127FT FROM PL N MIRO 9' OUTSIDE ****/ | 2019-04-04 | MADE 2 X 4 CUT IN SIDEWALK NEWLY PAVED AND REPLACED 5/8 INCH CURB COCK IN SEVERE HEAVY RAIN BACKFILLED AREA
201900525001 | 2019-04-01 | LEAD | 859 | OLGA |  | WMTLK | LOCATIONID#103321-520828 METER#A175136 METERBOX OVERFLOWING /** 1) MN: A175136 SN: 0029274, *TAP: SIZE: A LOC: 160 FEET FROM P LINE AT DUMAINE, *MB: CODE: BD LOC: ON OLGA 160FT FROM USPL OF DUMAINE ****/ | 2019-04-05 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900525101 | 2019-04-01 | LEAD | 857 | OLGA |  | WMTLK | LOCATIONID#103320-701578 METER#A301724 METERBOX OVERFLOWING /** 1) MN: A301724 SN: 0029274, *TAP: SIZE: A LOC: 160 FEET FROM P LINE AT DUMAINE, *MB: CODE: BD LOC: 160FT FROM USPL DUMAINE ****/ | 2019-04-06 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900525202 | 2019-04-02 | LEAD/PLASTIC | 161 | MIDDLE PARK PL |  | WMTLK | WATER METER LEAKING IN MUD PLOT /** 1) MN: A264203 SN: 0110146, *TAP: SIZE: A LOC: 668 FEET FROM P LINE AT CENTRAL PARK PL, *MB: CODE: BDM5 LOC: 668FT PL CENTRAL PARK PL 6' OUTSIDE 2' INSIDE CURB ****/ | 2019-04-08 | EXCAVATED IN MUD PLOT TO REPAIR A INLET LEAK BEHIND THE BOX HAD TO GO IN TO STREET TO MAKE A 10 X 4 STREET CUT GOUND LEAD ON LEAD AND PLASTIC ON OUTLET
201900527101 | 2019-04-01 | LEAD | 3303 | ST CLAUDE AV |  | WMTLK | LOCATIONID#115136-708149 METER#A398444 LEAK INSIDE METERBOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-09 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900529401 | 2019-04-01 | LEAD | 1676 | N MIRO | D"ABADIE | WILK | ML- METER LEAK ACCT# 119218-531771 METER # A325318 INLET SERVICE LEAK IN GUTTER BOTTOM /** 1) MN: SN: 0063586, *TAP: SIZE: A LOC: 58 FEET FROM P LINE AT D'ABADIE, *MB: CODE: __ LOC: ****/ | 2019-04-09 | EXCAVATED IN GUTTER BOTTOM + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900529901 | 2019-04-01 | LEAD | 2546 | COLUMBUS | N BROAD | WILK | MI- LEAK ON THE SIDEWALK ***** LEAK IS LOCATED ON THE SIDE OF ABOVE PROPERTY ***** INLET SERVICE LEAK IN SIDEWALK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-09 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900531302 | 2019-04-15 | LEAD | 1436 | ARTS | ROBERTSON | WILK | EXAMINED JOB AT ABOVE LOCATION FOUND LEAK IN THE STREET REFER TO ZONE 4 FOR REPAIR TO BE MADE /** 1) MN: A341279 SN: 0052991, *TAP: SIZE: A LOC: 274 FEET FROM P LINE AT VILLERE N, *MB: CODE: AD1 LOC: ON ARTS ST 273.5' FROM PL N VILLERE ****/ | 2019-04-17 | EXCAVATED IN ASPHALT STREET + GUTTER BOTTOM + REPLACED 3/4 INCH INLET SERVICE LINE FROM WATER MAIN TO METER BOX COMPACTED BACKFILLED + DRESSED UP AREA
201900531501 | 2019-04-02 | LEAD | 2641 | ABUNDANCE | EADS | ECLS | MI-CLOSED FOR OUTSIDE REPAIR ACCT#158834-474606 METER#A153823 **********C ROSS 10:17********** EMGCY CLOSE SERVICE @ THE METER UNABLE TO CLOSE OFF FROZEN CURB COCK WATER PASSING. ***PLUMBER ON SITE*** /** 1) MN: A153823 SN: 0096715, *TAP: SIZE: B LOC: 43 FEET FROM P LINE AT EADS, *MB: CODE: ADK2 LOC: 54FT FROM PL EADS 11FT LSPL CURB 8' OUTSIDE P/L ****/ | 2019-04-02 | EXAMINED JOB FOUND LEAK ON METER BOX COCK. FOUND LEAD ON THE INLET AND PLASTIC ON OUTLET. REPAIRED METERBOX COCK 5/8. HAND DUG IN MUDPLOT TO MAKE REPAIRS.
201900531502 | 2019-04-03 | LEAD | 2641 | ABUNDANCE | EADS | WILK | REMOVE LEAD FROM INLET /** 1) MN: A153823 SN: 0096715, *TAP: SIZE: B LOC: 43 FEET FROM P LINE AT EADS, *MB: CODE: ADK2 LOC: 54FT FROM PL EADS 11FT LSPL CURB 8' OUTSIDE P/L ****/ | 2019-04-17 | EXCAVATED IN MUDPLOT OVER 3/4 INLET FOUND LEAD LINE ON INLET SERVICE. CAN NOT REPLACE LEAD LINE BECAUSE OF CONTRACTOR IS REPLACING WATER MAIN ALSO CONTRACTOR IS REPALCING DRAIN LINE TOO. BACKFILL MUDPLOT
201900532201 | 2019-04-02 | LEAD | 2108 | LOUISA | N GALVEZ | WMTLK | WM: LEAK IN THE SIDEWALK EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN STREET /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-15 | EXAMINED JOB AT ABOVE LOCATION FOUND NO LEAK ON INLET OR OUTLET LEAK COMING FROMWATERMAIN AT (LOUISA AND N GALVEZ REFER TO ZONE 4 FOR REPAIRS TO BE MADE
201900532501 | 2019-04-02 | LEAD | 1401 | PAULINE |  | WMTLK | INSP L UDUEBOR STATES INLET AND OUTLET ARE NOT LINING UP AND CAUSING BAD LEAK. CUSTOMER IS WAITING ON WATER. PLEASE REPAIR METER A436046 LOC 307274 INLET AND OUTLET SERVICE NO LINING UP PROPERLY, HOUSE UNDER RENOVATION /** 1) MN: A314843 SN: 0074114, *TAP: SIZE: A LOC: 30 FEET FROM P LINE AT VILLERE N, *MB: CODE: ADKL LOC: 30' FROM VILLERE ON PAULINE ****/ | 2019-04-11 | MADE 2 X 2 SIDEWALK CUT THAT ALREADY BROKEN UP AND REPLACED WHEEL BACKFILLED AREA
201900532601 | 2019-04-02 | LEAD | 818-16 | IDA | ORLEANS AV | WMTLK | ML: METER LEAK ACCT#101533-514572 MTR# A157871 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** AT 816: 1) MN: A282721 SN: 0032337, *TAP: SIZE: B LOC: 121 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: CFL1 LOC: ON IDA,121' FROM P.L. ORLEANS AVE. ** AT 818: 2) MN: A157871 SN: 0032337, *TAP: SIZE: B LOC: 121 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: CFL1 LOC: ON IDA,121' FROM P.L. ORLEANS AVE. ****/ | 2019-04-18 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND. JOB COMPLETE
201900533801 | 2019-04-02 | LEAD | 3010 | PAUGER | N TONTI | WILK | ML- METER LEAK METER# A416229 ACCT# 268419-720838 INLET SERVICE LEAK, ALSO METER BOX BOTTOM BROKEN CAUSING BOX TOO EXPAND 04/08/19 PER K GRIFFIN SPOKE TO J GILLIAM ABOUT JOB. GIVE OUT **********J GILLIAM 11:15********** UPGRD TO AN A /** 1) MN: A114907 SN: 0060870, *TAP: SIZE: A LOC: 87 FEET FROM P LINE AT TONTI N, *MB: CODE: CDLM LOC: ON PAUGER 86.6' FROM LPL N TONTI ****/ | 2019-04-08 | EXCAVATED 2 X 4 MUD PLOT FOUND 5/8 INCH BOTTOM BROKEN REPLACE BROKEN 5/8 INCH BOTTOM BACKFIL;LED JOB WITH RIVERSAND
201900535101 | 2019-04-02 | LEAD | 700 | CANAL | ROYAL | WILK | **********PICK UP********** INLET SERVICE LEAK IN THE SIDEWALK LEAKING FROM METER BOX COCK, NO METER IN THE BOX. LEAK COMING FROM 2ND METER BOX FROM CANAL STREET ON ST CHARLES AVE /** 1) MN: SN: 0000000, *TAP: SIZE: C LOC: 41 FEET FROM P LINE AT CANAL, *MB: CODE: BV9 LOC: ON CANAL ST 73' FROM UPL CANAL 47' UPL CARONDELET ** 2) MN: SN: 0000000, *TAP: SIZE: B LOC: 104 FEET FROM P LINE AT COR. P.L. ST. CHARLES, *MB: CODE: C LOC: ON THE SOUTH SIDE OF CANAL ST. 143'FROM THE CORNER THERE ARE 9 MORE NOT LISTED. ****/ | 2019-05-06 | EXCAVATED IN BRICK SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900535801 | 2019-04-03 | LEAD | 1328 | KERLEREC | N VILLERE | WILK | INELT SERVICE LEAK /** 1) MN: A246310 SN: 0025775, *TAP: SIZE: A LOC: 198 FEET FROM P LINE AT VILLERE N, *MB: CODE: AFLM LOC: ON KERLEREC 198FT FROM VILLERE ****/ | 2019-04-02 | EXCAVATED 4 X 4 BRICK SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900536101 | 2019-04-03 | LEAD | 6100 | N DERBIGNY |  | WMTBG | 182351-725461 METER#C035407 AREA FLOODED/CANT LOCATE /** 1) MN: C023109 SN: 0131971, *TAP: SIZE: B LOC: 47 FEET FROM P LINE AT TUPELO, *MB: CODE: ADLM LOC: ON NO. DERBIGNY, 47' FROM P.L. TUPELO, 2' OUTSIDE ****/ | 2019-04-11 | EXAMINED 4 X 4 MUD PLOT FOUND LEAK ON 1 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND
201900536301 | 2019-04-03 | LEAD | 1476 | N ROBERTSON |  | WMTBG | 130473-721637 METER#A314108 METER BURIED/CANT LOCATE /** 1) MN: A314108 SN: 0060251, *TAP: SIZE: A LOC: 40 FEET FROM P LINE AT COLUMBUS, *MB: CODE: __ LOC: ON NO. ROBERTSON,41.5' FROM P.L. COLUMBUS ****/ | 2019-04-12 | EXCAVATED 4 X 4 ,UD PLOT LOCATED METER BOX AND RAISE UP TO GRADE BACKFILLED JOB WITH RIVERSAND AND MARKED WITH BLUE PAINT IN STREET
201900538701 | 2019-04-03 | LEAD | 1259 | TENNESSEE |  | WMRE | INSP L UDUEBOR STATES SERVICE IS BURIED. PLEASE RAISE TO GRADE AND SET 5/8 METER. LOC 307257 LOCATE, RASIE TO GRADE AND SET 5/8 METER, HOUSE UNDER CONSTRUCTION /** 1) MN: A288746 SN: 0106979, *TAP: SIZE: A LOC: 70 FEET FROM P LINE AT URQUHART, *MB: CODE: BDL LOC: MTR 70FT FROM PL URQUHART ON TENNESSEE 9FT OUTSIDE ****/ | 2019-04-15 | MADE 4 X 12 TRENCH SIDEWALK CUT AND MADE NEW TAP AND SET METER BOX CASING IN SIDEWALK AND 5/8 INCH METER BACKFILLED AREA
201900541801 | 2019-04-03 | LEAD | 3125 | N GALVEZ | LOUISA | WILK | ML- METER LEAK ACCT# 134478-433258 MTR# A349042 INLET LEAK (CURB COCK) INSIDE METER BOX, /** 1) MN: SN: 0083821, *TAP: SIZE: A LOC: 289 FEET FROM P LINE AT LOUISA, *MB: CODE: CDL LOC: ON GALVEZ 289' FROM UPL LOUISA ****/ | 2019-04-17 | ARRIVED AT ABOVE LOCATION FOUND BROKEN 5/8 INCH HANDWHEEL LEAKING REPLACED BROKEN HANDWHEEL ON 5/8 INCH OUTLET SERVICE
201900542001 | 2019-04-03 | LEAD | 1436 | GALLIER DR | N ROBERTSON | WILK | ML- METER LEAK METER #A409643 ACCT # 170283-429930 INLET LEAK IN THE MUDPLOT /** 1) MN: A316676 SN: 0112776, *TAP: SIZE: A LOC: 265 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: CDM4 LOC: ON GALLIER 268' FROM PL N ROBERTSON 8' OUTSIDE PL ****/ | 2019-04-26 | EXAMINED JOB AT ABOVE LOCATION FOUND LEAK ON BROKEN 5/8 INCH HANDWHEEL MADE REPAIR ON OUTLET SERVICE
201900543901 | 2019-04-03 | LEAD | 331 | N GALVEZ |  | WILK | LOCATIONID#116404-522783 METER#A404484 BLEEDER LEAK /** 1) MN: A128548 SN: 0064281, *TAP: SIZE: A LOC: 220 FEET FROM P LINE AT BIENVILLE, *MB: CODE: AEN LOC: 219' P.L. BIENVILLE ****/ | 2019-04-12 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL JOB COMPLETE
201900545001 | 2019-04-03 | LEAD | 936 | N DUPRE |  | WMTLK | LOCATIONID#131494-521109 METER#A290831 LEAK INSIDE METERBOX /** 1) MN: A290831 SN: 0079170, *TAP: SIZE: A LOC: 83 FEET FROM P LINE AT ST PHILIP, *MB: CODE: AE LOC: ON NO. DUPRE,81.5' FROM P.L. ST. PHILIP ****/ | 2019-04-18 | EXAMINE FOUND LEAK ON 5/8 INCH WASHER REPLACE BOTH INLET AND OUTLET WASHER AT ABOVE LOCATION
201900545101 | 2019-04-03 | LEAD | 2805 | DUMAINE |  | WMTLK | LOCATIONID#122189-520959 METER#A360726 LEAK INSIDE METERBOX /** 1) MN: A312464 SN: 0046658, *TAP: SIZE: A LOC: 33 FEET FROM P LINE AT WHITE N, *MB: CODE: BFKL LOC: SIDE OF STEPS AT 2805 ON DUMAINE 33 FT PL S WHITE ****/ | 2019-04-18 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMLL. JOB COMPLETE
201900545201 | 2019-04-03 | LEAD | 2736 | DUMAINE |  | WMTLK | LOCATIONID#102219-706047 METER#A117646 LEAK INSIDE METERBOX /** 1) MN: A279381 SN: 0004959, *TAP: SIZE: A LOC: 178 FEET FROM P LINE AT WHITE N, *MB: CODE: AFK1 LOC: ON DUMAINE 178FT URPL OF N WHITE ****/ | 2019-04-12 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 CURB COCK BACKFILLED + DRESSED UP AREA JOB COMPLETE
201900545301 | 2019-04-03 | LEAD | 2738 | DUMAINE |  | WMTLK | LOCATIONID#102218-520787 METER#A338364 LEAK INSIDE METERBOX /** 1) MN: A269821 SN: 0004904, *TAP: SIZE: A LOC: 279 FEET FROM P LINE AT N BROAD, *MB: CODE: ADK1 LOC: ON DUMAINE 280FT FROM PL OF N BROAD ****/ | 2019-04-12 | REPLACED 5/8 INCH HAND WHEEL + GUTS IN METER BOX JOB COMPLETE
201900546001 | 2019-04-03 | LEAD | 1427 | N CLAIBORNE AV |  | WOLK | LOCATION ID-107221 MTR-B042077 UNDERGROUND LEAK BETWEEN MTR AND STOP & WASTE/CONS REG ON MTR /** 1) MN: B023428 SN: 0017200, *TAP: SIZE: B LOC: 138 FEET FROM P LINE AT KERLEREC, *MB: CODE: ADK LOC: 138' P.L. KERLEREC ****/ | 2019-04-12 | EXAMINED JOB AT ABOVE LOCATION FOUND LEAK IS ON PROPERTY AT THE STOP-N-WASTE VALVE REFER TO (P.O.P) FOR REPAIRS TO MADE JOB COMPLETE
201900548001 | 2019-04-04 | LEAD | 1621 | PORT |  | WMRE | LOCATION: 307189 INSP UDUEBOR STATES METER BOX IS BURIED. PLEASE LOCATE, RAISE AND SET A 5/8 METER. HOUSE UNDER RENOVATIONS AND VACANT. LOCATE, RAISE TO GRADE AND SET 5/8 METER, HOUSE UNDER RENOVATION /** 1) MN: SN: 0073455, *TAP: SIZE: A LOC: 171 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BDL1 LOC: 171FT FROM LRPL DERBIGNY ****/ | 2019-04-17 | EXCAVATED IN CONCRETE SIDEWALK + MUD PLOT LOCATED BURIED METER BOX RASIED 5/8 INCH METER BOX BOTTOM TO GRADE + SET 5/8 INCH METER BACKFILLED + DRESSED UP AREA
201900552201 | 2019-04-05 | LEAD | 532 | CHARTRES |  | WOLK | LOCATION ID-116408 MTR-A428401 UNDERGROUND LEAK BETWEEN MTR AND STOP & WASTE/CONS REG ON MTR /** 1) MN: A245235 SN: 0021632, *TAP: SIZE: A LOC: 99 FEET FROM P LINE AT TOULOUSE, *MB: CODE: BEL1 LOC: APTS AND STORE 94' P.L. TOULOUSE ****/ | 2019-04-18 | EXCAVATEDIN FLAG STONE SIDEWALK + FOUND NO LEAK IN CUT BACKFILLED + DRESSED UP AREA REFER BACK TO PROPERTY OWNER FOR REPAIR. JOB COMPLETE
201900552301 | 2019-04-05 | LEAD | 3341 | DELACHAISE | S JOHNSON | WMTLK | LOCATIONID#212743-572857 METER#A400596 LEAK INSIDE METERBOX /** 1) MN: A295456 SN: 0065535, *TAP: SIZE: A LOC: 27 FEET FROM P LINE AT JOHNSON, *MB: CODE: CD LOC: ON DELACHAISE 27FT FROM JOHNSON 8FT OUTSIDE 8FT ****/ DOTTIE READY 4-10-19 EXP 4-30-19 | 2019-04-11 | ARRIVED ON JOB SITE. EXAMINED THE JOB. FOUND IT WAS A WASHER LERAK, CHANGED WASHER BACKFILLED AND CLEAN THE AREA.
201900552501 | 2019-04-05 | LEAD | 2517 | ORLEANS AV |  | WMTLK | LOCATIONID#145178-722351 METER#A407716 LEAK INSIDE METERBOX /** 1) MN: 000000 SN: 0076770, *TAP: SIZE: A LOC: 132 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: ADK4 LOC: ON ORLEANS AVE., 133.5' FROM P.L. NO. ROCHEBLAVE ****/ | 2019-04-12 | EXCAVATED 2 X 4 CONCRETE DRIVEWAY FOUND LEAK ON ABANDON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201900555201 | 2019-04-05 | LEAD | 2456 | N ROMAN |  | WMTLK | ML-METER LEAK ACCT#128117-546790 METER#A421381 EXAMINE INLET/OUTLET SERVICE FOR LEAK INSIDE METER BOX /** 1) MN: A235243 SN: 0042491, *TAP: SIZE: A LOC: 161 FEET FROM P LINE AT MUSIC, *MB: CODE: CDL7 LOC: 900 2455 XXX ON WALL CURB - 160' P.L. MUSIC ****/ | 2019-04-17 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA. JOB COMPLETE
201900556801 | 2019-04-05 | LEAD | 1018 | CAFFIN AV | ST CLAUDE AV | WILK | PP-POOR PRESSURE METER#C378862 ACCT#141171-425417 INLET SERVICE LEAK IN MUDPLOT 30 PSI AT OUTSIDE FAUCET **1ST AM** /** 1) MN: A296111 SN: 0072021, *TAP: SIZE: A LOC: 145 FEET FROM P LINE AT RAMPART N, *MB: CODE: CD LOC: CURB ON CAFFIN AVE 145 FT FROM PL N RAMPART ****/ | 2019-04-08 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND
201900558801 | 2019-04-06 | LEAD | 3326 | CASTIGLIONE | ROMULUS | WILK | METER LEAK METER#A430792 LOC:166561-713939 INLET SERVICE LEAK AT CURB /** 1) MN: A291066 SN: 0090780, *TAP: SIZE: A LOC: 260 FEET FROM P LINE AT ROMULUS, *MB: CODE: ADK2 LOC: 260FT PL ROMULUS ****/ | 2019-05-02 | EXAMINED AND FOUND NOTHING WRONG WITH ABOVE LOCATION
201900560801 | 2019-04-08 | LEAD | 3300 | DUMAINE |  | WMTLK | LOCATION# 143003 CUSTOMER# 709480 METER# A275531 INSPECTOR DID AN OUTSIDE INSPECTION FOUND LEAK INSIDE METER BOX......PLEASE REPAIR /** 1) MN: A275531 SN: 0047851, *TAP: SIZE: B LOC: 63 FEET FROM P LINE AT DUMAINE, *MB: CODE: __ LOC: SIDE BY POST - 63' P.L. DUMAINE ****/ | 2019-04-15 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL. JOB COMPLETE
201900561201 | 2019-04-08 | LEAD | 1128 | CONGRESS | MARAIS | WOLK | ML-INSPECTOR FOUND CONS ON METER ACCT#107403-730398 MTR#A415930 /** 1) MN: A312108 SN: 0083146, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT CONGRESS ON MARAIS, *MB: CODE: BFHN LOC: SIDE NEAR GATE ON MARAIS 73' P.L. CONGRESS ****/ | 2019-04-16 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION ALSO REPAIRS ON 5/8 INCH BROKEN HANDWHEEL
201900565601 | 2019-04-08 | LEAD | 1513 | N ROMAN | COLUMBUS | WOLK | ML: METER LEAK ACCT#130639-487767 MTR#A354783 EXAMINE OUTLET SERVICE FOR A LEAK WITH CONSTANT REGISTRATION ON THE METER. NO S&WV VISIBLE /** 1) MN: A133336 SN: 0060513, *TAP: SIZE: A LOC: 96 FEET FROM P LINE AT COLUMBUS, *MB: CODE: ADEK LOC: ON NO. ROMAN,97.5' FROM L.P.L. COLUMBUS ****/ | 2019-04-18 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIRS ON OUTLET METER STOP REQISTRATION ON IT BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900567501 | 2019-04-08 | LEAD | 2467 | N GALVEZ |  | WMTAMP | **********PICKUP JOB************ WATER COMING STRAIGHT FROM INLET /** 1) MN: A341355 SN: 0068963, *TAP: SIZE: A LOC: 236 FEET FROM P LINE AT MUSIC, *MB: CODE: BDLN LOC: ON GALVEZ 236' FROM PL OF MUSIC ****/ | 2019-04-15 | EXCAVATED IN MUD PLOT+ DISCONNECTED ILLEGAL WATER CONNECTION AT ABOVE LOCATION BACKFILLED + DRESED UP AREA
201900567601 | 2019-04-08 | LEAD | 2314 | DELERY | N TONTI | WILK | MI- LEAK IN STREET INLET SERVICE LEAK IN EMPTY LOT NEXT TO ABOVE ADDRESS /** 1) MN: A275351 SN: 0135929, *TAP: SIZE: A LOC: 192 FEET FROM P LINE AT TONTI N, *MB: CODE: ADM1 LOC: RES ON DELERY 188FT P/L N TONTI 7' OUTSIDE ****/ | 2019-04-13 | EXAMINE JOB AT EMPTY LOT FOUND NO LEAK
201900567801 | 2019-04-08 | LEAD | 2507 | ANDRY | N DORGENOIS | WMTLK | WM-LEAK ON THE SIDEWALK EXAMINE INLET/OUTLET SERVICE FOR A LEAK, SIDEWALK FLOODED ALSO UNALBE TO PUMP METER BOX DOWN /** 1) MN: 000000 SN: 0133743, *TAP: SIZE: A LOC: 55 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: AD24 LOC: RES ON ANDRY 55FT PL N DORGENOIS 6' OUTSIDE ****/ | 2019-04-13 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900570601 | 2019-04-09 | LEAD | 731 | ESPLANADE AV | BOURBON | WILK | PP- POOR PRESSURE ACCT# 107374-719501 MTR# C036522 *************PLEASE CALL UPON ARRIVAL****************** EXAMINE INLET SERVICE IN LARGE TREE ROOTS CUSTOMER EXPERIENCING LOW PRESSURE /** 1) MN: C025128 SN: 0018798, *TAP: SIZE: C LOC: 103 FEET FROM P LINE AT BOURBON, *MB: CODE: ADK1 LOC: RIGHT SIDE OF HOUSE OPP PL 1FT FROM 727 ****/ | 2019-04-17 | MADE 4 X 6 SIDEWALK CUT EXCAVATED IN LARGE TREE ROOTS AND MADE REPAIRS ON 1 INCH SERVICE BACKFILLED AREA UNKNOWN GROUND WIRE CABLE WAS SNAP IN HALF ENBEDDED IN TREE ROOTS
201900570801 | 2019-04-09 | LEAD | 721 | DESIRE |  | WOLK | ML- METER LEAK AT METER# A 351149 ACCT# 101169 - 732166 EXAMINE OUTLET SERVICE @ PROPERTY LINE WITH CONSTANT REGISTRATION /** 1) MN: A280977 SN: 0047886, *TAP: SIZE: B LOC: 188 FEET FROM P LINE AT ROYAL, *MB: CODE: AFKN LOC: 188FT FROM LSPL ROYAL ****/ | 2019-04-15 | EXAMINE AND FOUND 5/8 INCH BROKEN HANDWHEEL LEAKING REPLACE HANDWHEEL AND WASHERS AT ABOVE LOCATION. JOB COMPLETE
201900571901 | 2019-04-09 | LEAD | 2904 | BRUXELLES |  | WILK | ML METER LEAK ACCOUNT #116292-703761 METER #A421960 INLET SERVICE LEAK IN THE MUD PLOT NEAR METER BOX /** 1) MN: A328242 SN: 0072170, *TAP: SIZE: A LOC: 35 FEET FROM P LINE AT AGRICULTURE, *MB: CODE: CDM2 LOC: ON BRUXELLES 55.5FT FROM AGRICULTURE ****/ | 2019-04-15 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH SERVICE MADE REPAIRS ON INLET BACKFILL JOBWITH RIVERSAND
201900572001 | 2019-04-09 | LEAD | 2908 | BRUXELLES |  | WILK | ML METER LEAK ACCOUNT #140964-492304 METER#A364544 INLET SERVICE LEAK IN THE MUD PLOT NEAR METER BOX /** 1) MN: A335835 SN: 0071859, *TAP: SIZE: B LOC: 100 FEET FROM P LINE AT AGRICULTURE, *MB: CODE: CDL1 LOC: ON BRUXELLES ST 99' FROM PL AGRICULTURE ****/ | 2019-04-15 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND
201900572101 | 2019-04-09 | LEAD | 122 | S DORGENOIS | CANAL | WMTLK | MI: LEAK IN THE SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK INSIDE METER BOX SATURATING SIDEWALK /** 1) MN: A219261 SN: 0022225, *TAP: SIZE: B LOC: 176 FEET FROM P LINE AT CANAL, *MB: CODE: CEL LOC: 176' P.L. CANAL ****/ | 2019-04-15 | EXCAVATED 2 X4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201900573501 | 2019-04-09 | LEAD | 1515 | TUPELO |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 307154-705859 METER NUMBER - A433653 EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A317789 SN: 0095305, *TAP: SIZE: A LOC: 98 FEET FROM P LINE AT NO. ROBERTSON, *MB: CODE: BDLM LOC: ON TUPELO, 98' FROM P.L. NO. ROBERTSON, 8' OUTSIDE ****/ | 2019-04-13 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET RAISE METER BOX UP TO GRADE BACKFILL JOB WITH RIVERSAND + COLDMILL
201900573801 | 2019-04-09 | LEAD/PLASTIC | 5112 | CLARA |  | WMRE | INSP S BIBBINS SAID HE IS UNABLE TO LOCATE SERVICE. PLEASE LOCATE AND CHANGE METER A346365 LOC 172234 LOCATE SERVICE AND CHANGE METER, HOUSE UNDER RENOVATION /** 1) MN: A282924 SN: 0115379, *TAP: SIZE: A LOC: 94 FEET FROM P LINE AT SONIAT, *MB: CODE: OOOO LOC: ON CLARA, 91' FROM P.L. SONIAT, 5' OUTSIDE P.L. ****/ | 2019-04-27 | EXCVATED IN MUDPLOT TO FIND METER BOX .REMOVE METER AND SET NEW METER RAISED TO GRADE. OLD METER INFO: A346365 FACT: 62114384 MAKE: SENSUS READ: 6265
201900574201 | 2019-04-09 | LEAD | 5600BLK | N DORGENOIS | CAFFIN AV | WILK | MI-LEAK IN STREET ****LEAKING AGAIN**** INLET SERVICE LEAK IN MUDPLOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-20 | MADE 8 X 8 CUT IN NEW BLACK TOP STREET AND MADE REPAIR ON 1 INCH COPPER LINE FOR ABANDON LOT BACKFILLED AREA
201900578701 | 2019-04-10 | LEAD | 1743 | LAMANCHE |  | WMRE | LOCATION: 171518 INSP UDUEBOR STATES METER BOX SERVICE IS BURIED. PLEASE LOCATE, RAISE AND CHANGE METER# A 293915 LOCATE, RAISE TO GRADE & CHANGE METER /** 1) MN: A293915 SN: 0145038, *TAP: SIZE: A LOC: 27 FEET FROM P LINE AT NO. ROMAN, *MB: CODE: BDL LOC: ON LAMANCHE, 27' FROM P.L. NO. ROMAN, 7' OUTSIDE ****/ | 2019-04-13 | EXCAVATED 4 X 4 MUD PLOT RAISE METER BOX UP TO GRADE REPLACE 5/8 INCH METER WITH NEW METER BACKFILL JOB WITH RIVERSAND OLD METER INFO: A293915 FACT: 50195488 MAKE: SENSUS READ: 15037
201900585201 | 2019-04-11 | LEAD | 2900 | BANKS | S DUPRE | WMTLK | ML: METER LEAK ACCT#153725-531092 MTR# A399272 EXAMINE INLET & OUTLET SERVICE FOR A LEAK INSIDE METER BOX THE MUD PLOT /** 1) MN: A292765 SN: 0056670, *TAP: SIZE: B LOC: 5 FEET FROM P LINE AT DUPRE S, *MB: CODE: AFL LOC: FRONT 7' P.L. S DUPRE 3' OUTSIDE P/L ****/ | 2019-05-25 | EXCAVATED IN MUD PLOT THROUGH HEAVY TREE ROOTS + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA ALSO REPLACED BROKEN 5/8INCH METER BOX BOTTOM
201900586201 | 2019-04-11 | LEAD | 1332 | SPAIN | N VILLERE | WILK | INLET SERVICE LEAK /** 1) MN: A127899 SN: 0018391, *TAP: SIZE: A LOC: 58 FEET FROM P LINE AT VILLERE N, *MB: CODE: BFK2 LOC: METER IN DRIVE ON SPAIN 58FT FROM PL OF N VILLERE ****/ | 2019-04-11 | EXCAVATED IN CONCRETE SIDEWALK + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA. JOB COMPLETE
201900588201 | 2019-04-11 | LEAD/PLASTIC | 1210 | POLAND AV | MARAIS | WILK | WM-LEAK IN THE STREET INLET SERVICE LEAK IN MUDPLOT ON SIDE OF TREE /** 1) MN: A309885 SN: 0075111, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT MARAIS, *MB: CODE: BDL2 LOC: ON POLAND AVE 98' FORM MARAIS 8' OUTSIDE PL 3' ****/ | 2019-04-21 | WE EXCAVATED BY HAND IN TREE ROOTS TO MAKE REPAIRS TO 2IN CONTROLLING LINE WE BACKFILL PLUUS CLEAN UP THE LINE HAD BROKEN 3 TIMES DUE TO IT BEING CRYSTALLIZE WE ALSO HAVE DOWN TIME WAITING FOR TRAIN TO PASS
201900589401 | 2019-04-12 | LEAD | 3669 | GENTILLY BL |  | WMTLK | LOCATIONID#171554-478749 METER#C016791 LEAK INSIDE METERBOX /** 1) MN: C016791 SN: 0114381, *TAP: SIZE: C LOC: 51 FEET FROM P LINE AT GENTILLY BLVD, *MB: CODE: ADHM LOC: SIDE ON VENUS 51FT P/L GENTILLY BL 8' OUTSIDE 3' ****/ | 2019-04-29 | EXCAVATE IN MUDPLOT AND MADE REPAIR ON INLET SERVICE LEAK AND ALSO LEAD ON INLET AND OUTLET BACKFILL JOB COMPLETE
201900591301 | 2019-04-12 | LEAD | 1415 | DESIRE |  | WMTLK | LOCATION: 256872 MTR# A 429317 WATER LEFT ON INSP UDUEBOR STATES DOUBLE OUTLET WASHER LEAK. INLET AND OUTLET SERVICE NOT LINING UP. PLEASE REPAIR. EXAMINE INLET & OUTLET SERVICE FOR A LEAK SERVICE NOT LINING UP CORRECTLY /** 1) MN: A328863 SN: 0082067, *TAP: SIZE: A LOC: 4 FEET FROM P LINE AT VILLERE, *MB: CODE: CD LOC: ON DESIRE 4FT FROM DIV P/L VILLERE ****/ | 2019-04-23 | EXCAVATED INMUD PLOT AND REPLACED WASHERS ON INLET AND OUTLET INSIDE METER BOX REPLACED CASING JOB COMPLETE
201900592101 | 2019-04-12 | LEAD | 1040 | ST MAURICE | N RAMPART | WMTLK | LEAK ON THE SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-29 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900593001 | 2019-04-12 | LEAD | 2122 | N BROAD |  | WMTLK | ML- METER LEAK METER #A409106 ACCT #152944-490381 EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN LARGE TREE TRUNK /** 1) MN: A324704 SN: 0065953, *TAP: SIZE: C LOC: 173 FEET FROM P LINE AT DUELS, *MB: CODE: BDK LOC: ON NO. BROAD, 173' FROM P.L. DUELS,10' OUTSIDE PL ****/ | 2019-04-24 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900593601 | 2019-04-12 | LEAD/PLASTIC | 2634 | ST ANDREW | MAGNOLIA | WILK | ************************PICKUP******************* INLET SERVICE LEAK IN CONCRETE STREET, FLOODING STREET AND GUTTER BOTTOM /** 1) MN: SN: 0142347, *TAP: SIZE: A LOC: 38 FEET FROM P LINE AT MAGNOLIA, *MB: CODE: AEKS LOC: 38FT FROM URPL MAGNOLIA ON MAGNOLIA ****/ DOTTIE READY 5-17-19 EXP 6-6-19 | 2019-05-25 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 1 1/2 CONTROLLING LINE.REPLACED 8FT. OF 1 1/2 TUBING.( 8FT. X 12 FT. CONCRETE STREET.
201900594201 | 2019-04-12 | LEAD | 811 | N JEFFERSON DAVIS PK | ELAINE PL | WMTLK | WM - LEAK ON THE SIDEWALK - LEAK ON THE SIDE OF THE PROPERTY - ELAINE PL EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** 1) MN: A296120 SN: 0079832, *TAP: SIZE: A LOC: 53 FEET FROM P LINE AT JEFF DAVIS PKWY N, *MB: CODE: BDH3 LOC: ON ELAINE PL 64FT. PL JEFF DAVIS 1ST METR ****/ | 2019-05-01 | EXCAVATED IN MUD PLOT AND MADE REPAIR ON 1 INCH CONTROLLING LINE BACKFILLED AREA CAR ROLLING IN GRASS
201900595501 | 2019-04-13 | LEAD | 1905 | SPAIN |  | WILK | MI- LEAK ON SIDEWALK ***FLOODING LOT**** INLET SERVICE LEAK BY VACANT LOT GETTING OFF IN DCB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-25 | EXCAVATED IN ASPHALT STREET + REPLACED 3/4 INCH BEND ADAPTER ON WATER MAIN COMPACTED BACKFILLED + DRESSED UP AREA. JOB COMPLETE
201900597201 | 2019-04-14 | LEAD | 1525 | DESIRE | N ROBERTSON | WILK | ML METER LEAK MTR#A402944 LOC#184347 INLET SERVICE LEAK (SIDEWALK & ST UNDER CONSTRUCTION) /** AT 1523: 1) MN: SN: 0078414, *TAP: SIZE: B LOC: 195 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: BEK2 LOC: FIRST METER ON DESIRE 195 FT FROM PL N ROBERTSON ** AT 1525: 2) MN: A282733 SN: 0078414, *TAP: SIZE: __ LOC: 198 FEET FROM P LINE AT NO. ROBERTSON, *MB: CODE: BEN2 LOC: ON DESIRE, 199' FROM P.L. NO. ROBERTSON, 3' OUT- ****/ | 2019-04-22 | EXCAVATED 2 X 4 MUD PLOT IN SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900597501 | 2019-04-15 | LEAD | 732 | TOULOUSE | BOURBON | WOLK | ML LOC & CUST# 113464-527316 MTR# A308602 SERVICE ADDRESS: 732 TOULOUSE ST. INSP COMM: F/ON-L/ON RD. 8775.... STOP AND GO CONS REG ON MTR EVERY 3-5 MINS, NO VISIBLE S&W. CHECK FIXTURE, UNABLE TO LOCATE LEAK /** 1) MN: A308602 SN: 0031766, *TAP: SIZE: A LOC: 93 FEET FROM P LINE AT BOURBON, *MB: CODE: AELK LOC: REST 90' P.L. BOURBON ****/ | 2019-05-24 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX JOB COMPLETE
201900597801 | 2019-04-15 | LEAD | 936 | N RAMPART |  | WMTLK | LOCATIONID#107317-485693 METER#A383061 LEAK INSIDE METERBOX /** 1) MN: A283302 SN: 0023958, *TAP: SIZE: A LOC: 41 FEET FROM P LINE AT ST PHILIP, *MB: CODE: AFK LOC: FRNT 41'FRM URPL ST PHILIP ****/ | 2019-04-25 | EXCAVATED 2 X 4 CONCRETE DRIVEWAY FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201900598501 | 2019-04-15 | LEAD | 2465 | CUMBERLAND CT |  | WILK | ML METER LEAK ACCOUNT #234520-410676 METER #C021860 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: C021860 SN: 0155385, *TAP: SIZE: C LOC: 89 FEET FROM P LINE AT GEN MEYER AVE, *MB: CODE: AF LOC: ON CUMBERLAND 89FT FROM P.L. GEN MEYER AVE 10' OUT ****/ | 2019-04-19 | ARRIVED ON JOB SITE EXAMINED LEAK IN MUD PLOT EXCAVATED IN M UD PLOT MADE REPAIR ON INLET SERVICE AND SET UP NEW METER BOX COMPLETE BACKFILL DRESS UP WORK SITE. JOB COMPLETE
201900599501 | 2019-04-15 | LEAD | 2630 | CLOUET | FLORIDA AV | WMLK | ***********************PICKUP******************** LEAK ON THE MAIN ON CLOUET /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-29 | EXCACATED IN ASPHALT STREET + REPLACED 3/4 INCH CORPORATION COCK ON WATER MAIN COMPACTED BACKFILLED + DRESSED UP AREA SERVICE WAS ABANDONED WITH NO INLET
201900600201 | 2019-04-15 | LEAD | 3612 | ELAINE PL |  | WILK | WM-LEAK BETWEEN STREET AND SIDEWALK INLET SERVICE LEAK IN MUDPLOT METER UNDER WATER /** 1) MN: A319582 SN: 0074801, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT JEFF DAVIS PKWY N, *MB: CODE: ADK2 LOC: ON ELAINE 129' FROM PL OF JEFF DAVIS PKWY N ****/ | 2019-04-24 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIR ON OUTLET BACKFILL JOB WITH RIVERSAND
201900601301 | 2019-04-15 | LEAD | 2017 | MUSIC | N GALVEZ | WMTLK | WATER METER LEAK. LEAK IS VISIBLE. LEAK IS UNDERNEATH SIDEWALK. ECHOLOGICS REPORTED AND MARKED LEAK. /** 1) MN: A337173 SN: 0092381, *TAP: SIZE: A LOC: 149 FEET FROM P LINE AT JOHNSON N, *MB: CODE: BDNK LOC: ON MUSIC,149' FROM P.L. NO. JOHNSON,8' OUTSIDE ****/ | 2019-04-25 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA (NO METER) JOB COMPLETE
201900603001 | 2019-04-15 | LEAD/PLASTIC | 7709 | OAK | ADAMS | WILK | ML: METER LEAK ACCT#131186-583238 MTR#A317682 INLET SERVICE LEAK BAD BLEEDER VALVE /** 1) MN: A317682 SN: 0061815, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT ADAMS, *MB: CODE: BFL LOC: ON OAK,77.6' FROM U.P.L. ADAMS ****/ | 2019-04-30 | EXCAVATED IN MUD PLOT TO REPAIR A BAD 5/8" METER BOX COCK AND BROKEN BOTTOM HAD TO MAKE A 4 X 4 SIDEWALK CUT FOUND LEAD ON INLET
201900604501 | 2019-04-15 | LEAD | 1901 | ALMONASTER AV |  | WMTLK | LOCATIONID#124810-479296 METER#A375588 LEAK INSIDE METERBOX EXAMINE INLET/OUTLET SERVICE FOR LEAK INSIDE METER BOX /** 1) MN: A286154 SN: 0169017, *TAP: SIZE: A LOC: 2 FEET FROM P LINE AT PRIEUR NO., *MB: CODE: CDLM LOC: ON ALMONASTER AVE.,11' FROM U.S.P.L. NO. PRIEUR ****/ | 2019-04-24 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX ALSO REPLACED DAMAGED 5/8 INCH WATER METER OLD METER INFO: A375588 FACT: 73268009 MAKE: SENSUS READ: 186145
201900604801 | 2019-04-15 | LEAD | 2200 | ST PHILIP |  | WMRE | INSP L UDUEBOR SAID SERVICE IS BURIED. PLEASE RAISE TO GRADE AND SET 5/8 METER. LOC 307186 LOCATE/RAISE/SET 5/8 METER NEW CONSTRUCTION /** 1) MN: A235357 SN: 0054175, *TAP: SIZE: A LOC: 74 FEET FROM P LINE AT ST PHILIP, *MB: CODE: AFHO LOC: 73FT FROM USPL ST PHILIP SIDE ST ON N GALVEZ ****/ | 2019-04-26 | EXCAVATED IN MUD PLOT + LOCATED METETR BOX ALSO SET 5/8 INCH WATER METER MARKED METER BOX WITH BLUE PAINT
201900604901 | 2019-04-15 | LEAD | 2419 | N JOHNSON |  | WILK | INSP L UDUDBOR SAYS THERE IS NO WATER COMING FROM MAIN. PLEASE REPAIR METER A439046 LOC 307034 DRY INLET CUSTOMER OUT OF WATER HOUSE UNDER CONSTRUCTION /** 1) MN: A312869 SN: 0040455, *TAP: SIZE: A LOC: 120 FEET FROM P LINE AT MUSIC, *MB: CODE: CF LOC: ON NO. JOHNSON,121' FROM U.S.P.L. MUSIC ****/ | 2019-04-25 | EXCAVATED IN CONCRETE SIDEWALK + MUD PLOT + MADE REPAIR ON INLET UNDER CURB TO RESTORE WATER BACK TO ABOVE LOCATION REPLACED 3/4 INCH INLET FROM CURB TO PROPERTY BACKFILLED + DRESSED UP AREA
201900605101 | 2019-04-15 | LEAD | 1436 | FRANCE |  | WOLK | WM--LEAK BETWEEN SIDEWALK AND STREET OUTLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A306439 SN: 0111561, *TAP: SIZE: A LOC: 282 FEET FROM P LINE AT VILLERE N, *MB: CODE: BDL3 LOC: ON FRANCE 285' FROM PL N VILLERE 9' OUTSIDE PL 1' ****/ | 2019-04-26 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900608001 | 2019-04-16 | LEAD | 5432 | N TONTI | CHOCTAW | WILK | WATER INLET SERVICE LEAK /** 1) MN: A145446 SN: 0159706, *TAP: SIZE: B LOC: 190 FEET FROM P LINE AT FLOOD, *MB: CODE: BD LOC: MTR ON TONTI 191FT FROM PL FLOOD 2FT INSD CURB ****/ | 2019-04-14 | REMOVE WATER FROM FLOODED AREA EXCAVATED 3 X 3 MUD PLOT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201900608301 | 2019-04-16 | LEAD | 1809 | AUBRY | OLD ROMAN | WILK | WATER INLET SERVICE /** 1) MN: 000000 SN: 0070135, *TAP: SIZE: A LOC: 77 FEET FROM P LINE AT OLD ROMAN, *MB: CODE: ADN4 LOC: ON AUBRY 78' FROM PL OLD ROMAN 10' OUTSIDE PL 2' ****/ | 2019-04-14 | EXCAVATED 2 X 4 MUD PLOT FOUND LEAK ON 5/8 INJCH SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND JOB COMPLETE
201900611701 | 2019-04-16 | LEAD | 2040 | CONGRESS |  | WMTLK | ML - METER LEAK ACCOUNT NUMBER - 172077-432281 METER NUMBER - B019554 EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN BOX /** 1) MN: B019554 SN: 0115081, *TAP: SIZE: B LOC: 16 FEET FROM P LINE AT NO. GALVEZ, *MB: CODE: __ LOC: ON CONGRESS, 16' FROM P.L. NO. GALVEZ, 8' OUTSIDE ****/ | 2019-04-26 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION. JOB COMPLETE
201900612401 | 2019-04-16 | LEAD | 835 | MAZANT |  | WILK | LOCATION ID-211915 LEAK IN MTR BOX/NO MTR IN BOX INLET SERVICE LEAK BAD CURBCOCK /** 1) MN: A309644 SN: 0028003, *TAP: SIZE: B LOC: 50 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CD LOC: ON MAZANT 50' FROM P.L. BURGUNDY 6' OUTSIDE 2' ****/ | 2019-04-26 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON ABANDON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL. JOB COMPLETE
201900613901 | 2019-04-17 | LEAD | 1031 | TOURO |  | WMTLK | LOCATIONID#156262-486060 METER#C0312224 LEAK INSIDE METERBOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-30 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 1 INCH INCH SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900615201 | 2019-04-17 | LEAD | 1561 | N MIRO |  | WILK | ML - METER LEAK MTR# A345047 ACCT# 153458-488918 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A117081 SN: 0069866, *TAP: SIZE: A LOC: 138 FEET FROM P LINE AT LAHARPE, *MB: CODE: ADMN LOC: ON NO. MIRO,140.4' FROM P.L. LAHARPE,11' OUTSIDE ****/ | 2019-04-29 | EXAMINED JOB AND PUMP METER BOX CASING DOWN AND REPLACED 5/8 INCH WASHERS ON INLET AND OUTLET INSIDE METER BOX
201900616001 | 2019-04-17 | LEAD | 2222 | CLOUET | N MIRO | WILK | ML-METER LEAK ACCT#149693-433601 METER#A287576 INLET SERVICE LEAK IN BOX, CARS ROLLING OVER METER /** 1) MN: A287576 SN: 0085981, *TAP: SIZE: A LOC: 200 FEET FROM P LINE AT MIRO N, *MB: CODE: BDM1 LOC: 180'FT FROM P.L. N.MIRO 7' OUTSIDE PL ****/ | 2019-04-29 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900616401 | 2019-04-17 | LEAD | 1500-02 | CAFFIN AV |  | WOLK | ML-METER LEAK ACCT#147473-423653 MTR#A320029 EXAMINE OUTLET SERVICE FOR LEAK @ PROPERTY LINE CON REG /** AT 1502: 1) MN: A320029 SN: 0102338, *TAP: SIZE: A LOC: 56 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: BDK LOC: ON CAFFIN AVE 56' FROM PL N ROBERTSON ****/ | 2019-04-29 | REPLACE BOTH INLET AND OUTLET WASHER AT ABOVE LOCATION
201900618001 | 2019-04-17 | LEAD | 1912 | FELICIANA |  | WMBK | LOCATION ID-207596 MTR-A430779 NEED MTR BOX CASING /** 1) MN: A288863 SN: 0168117, *TAP: SIZE: B LOC: 12 FEET FROM P LINE AT NO. PRIEUR, *MB: CODE: __ LOC: ON FELICIANA, 12' FROM D.P.L. NO. PRIEUR, 9' OUT- ****/ | 2019-04-30 | EXCAVATED 4 X 4 LIMESTONE SIDEWALK RAISE METER BOX TO GRADE BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900618701 | 2019-04-17 | LEAD | 2017 | DUMAINE | N PRIEUR | WILK | ML- METER LEAK METER#A399268 ACCT#116516-524788 INLET SERVICE LEAK ON SIDEWALK /** 1) MN: A227208 SN: 0022041, *TAP: SIZE: A LOC: 135 FEET FROM P LINE AT PRIEUR N, *MB: CODE: CFL1 LOC: 135' P.L. N PRIEUR ****/ | 2019-04-26 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900618801 | 2019-04-17 | LEAD | 940 | ST ANN |  | WILK | BAD BLEEDER VALVE LEAK PER L UDUEBOR. PLEASE REPAIR AND CHANGE METER B028828 LOC 107804 INLET SERVICE LEAK INSIDE METER BOX COMING FROM BAD BLEEDER VALVVE /** 1) MN: B028828 SN: 0024407, *TAP: SIZE: B LOC: 34 FEET FROM P LINE AT ST ANN ON BURGUNDY, *MB: CODE: BEHL LOC: ON BURGUNDY 34FT FROM URPL ST ANN ****/ | 2019-06-13 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 3/4 INCH INLET SERVICE MADE REPAIR ON ONLET REPLACE /34 INCH METER WITH NEW ONE AT ABOVE LOCATION BACKFILL JOB WITH RIVERSAND AND COLDMILL ************OLD METER INFO********* METER:B028828 FAC:44389545 MAKE:SENSUS READ:74669
201900619301 | 2019-04-17 | LEAD | 2222 | N ROBERTSON | MARIGNY | WILK | WM- LEAK IN STREET INLET SERVICE LEAK IN CONCRETE STREET /** 1) MN: 000000 SN: 0046174, *TAP: SIZE: A LOC: 122 FEET FROM P LINE AT MARIGNY, *MB: CODE: CFM LOC: ON N ROBERTSON 121.6' FROM URPL MARIGNY ****/ | 2019-05-02 | EXAMINED JOB AT ABOVE LOCATION AND FOUND NO LEAK
201900621301 | 2019-04-18 | LEAD | 527 | ST JOSEPH | CAMP | WMLK | LEAK ON THE MAIN IN THE STREET MARK BY ECHOLOGICS /** 1) MN: G002317 SN: 0176746, *TAP: SIZE: G LOC: 142 FEET FROM P LINE AT CAMP, *MB: CODE: OOO LOC: IN M.H. ON ST JOSEPH-144'FROM P.L. CAMP ** 2) MN: SN: 0000000, *TAP: SIZE: H LOC: 137 FEET FROM P LINE AT CAMP, *MB: CODE: __ LOC: ****/ | 2019-04-27 | ARRIVED ON JOB SITE EXAMINE LEAK IN SIDEWALK CUT OUT SIDEWALK AND STREET BY HAND EXCAVATED IN MUD PLOT BY HAND MADE REPAIR ON ABANDON SERVICE AT MAIN BACKFILLED DRESS UP WORK SITE
201900621602 | 2019-04-18 | LEAD | 4242 | CHEF MENTEUR HW |  | WILK | PLEASE REPAIR 3/4 ADAPTER WITH A 5/8 BASE UNABLE TO SET A METER BAD LEAK COMING FOR THE CURB COCK CUSTOMER IS WITHOUT WATER LOCATION#223655 INLET & OUTLET SERVICE NEED TO BE REDUCE FROM A 3/4 TO A 5/8, ALSO SET METER **********CUSTOMER OUT OF WATER********** C ROSS 13:19 *******METER ON OLD GENTILLY BEHIND NURSERY****** /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-19 | ARRIVED ON JOB SITE EXCAVATED IN MUD PLOT BY HAND REMOVE 3/4 INCH SET UP AND REPLACE WITH 5/8 INCH METER BOX COMPLETE ALSO SET METER BACKFILL DRESSED UP WORK SITE LEFT METER OFF
201900622501 | 2019-04-18 | LEAD | 2604 | CLEVELAND AV | S DORGENOIS | WILK | ML METER LEAK METER # A428338 ACCT#124846-530918 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A225240 SN: 0047884, *TAP: SIZE: A LOC: 42 FEET FROM P LINE AT DORGENOIS S, *MB: CODE: AF LOC: ON CLEVELAND AVE.,42' FROM U.S.P.L. SO. DORGENOIS ****/ | 2019-05-01 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900623401 | 2019-04-18 | LEAD | 5408 | FLORIDA AV |  | WMTLK | ACCOUNT# 184837-719352 METER# A396841 METER LEAKS AREA FLOODED, THE LEAK IS AFFECTING THE CUSTOMER WATER PRESSURE. EXAMINE INLET/OUTLET SERVICE FOR POOR PRESSURE **1ST AM** /** 1) MN: A333845 SN: 0138366, *TAP: SIZE: B LOC: 68 FEET FROM P LINE AT ANDRY, *MB: CODE: BD36 LOC: ON FLORIDA AVE., 68' FROM P.L. ANDRY, 7' OUTSIDE ** 2) MN: A330407 SN: 0138366, *TAP: SIZE: B LOC: 68 FEET FROM P LINE AT ANDRY, *MB: CODE: BD36 LOC: RES ON FLORIDA 69FT FROM PL ANDRY 7' OUTSIDE PL ****/ | 2019-04-19 | ARRIVED ON JOB SITE EXAMINE LEAK IN MUD PLOT EXCAVATED IN MUD PLOT MADE REPAIRS ON INLET SERVICE BACKFILL DRESS UP WORK SITE
201900623501 | 2019-04-19 | LEAD | 6815 | MILNE BL |  | WMLK | WM- LEAK IN STREET CUST WITHOUT WATER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ BROKEN WATER MAIN IN STREET FLOODING THE AREA, NEEDING IMMEDIATE ATTENTION. GAVE JOB TO H. GUSMAN ZONE 7 CUSTOMER OUT OF WATER. | 2019-04-19 | ARRIVED ON JOB EXAMINED LEAK ON WATER MAIN IN MUD PLOT EXCAVATED IN MUD PLOT MADE REPAIR ON 6 INCH WATER MAIN BACKFILL DRESSED UP WORK SITE
201900623701 | 2019-04-19 | LEAD | 2623 | ESPLANADE AV |  | WMTLK | LOCATIONID#100797-491019 METER#B014101 LEAK INSIDE METERBOX /** 1) MN: B014101 SN: 0020449, *TAP: SIZE: B LOC: 209 FEET FROM P LINE AT BROAD N, *MB: CODE: BDI4 LOC: ON DESOTO 20FT FROM CATCH BASIN 211' FROM U.S.P.L. ****/ | 2019-04-22 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION JOB COMPLETE
201900624101 | 2019-04-19 | LEAD | 3106 | PAUGER | N ROCHEBLAVE | WILK | INET SERVICE LEAK /** 1) MN: SN: 0068297, *TAP: SIZE: A LOC: 53 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: CDKN LOC: ON BOURBON ST 52.5' FROM USPL N ROCHEBLAVE ****/ | 2019-04-17 | MADE 4 X 4 STREET CUT AND MADE REPAIR ON 3/4 INCH INLET SERVICE FOR ABANDON LOT BACKFILLED AREA
201900624301 | 2019-04-19 | LEAD | 3004 | PAUGER | N TONTI | WILK | INET SERVICE LEAK /** 1) MN: A282715 SN: 0055283, *TAP: SIZE: A LOC: 45 FEET FROM P LINE AT TONTI N, *MB: CODE: BEKO LOC: ON PAUGER 45.8' FROM USPL N TONTI ****/ | 2019-04-17 | EXAMINED PUMP METER BOX DOWN AND REPLACED WASHERS ON INLET AND OUTLET INSIDE METER BOX
201900624501 | 2019-04-19 | LEAD | 3129 | PAUGER | N DORGENOIS | WILK | INLET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-17 | MADE 4 X 4 CUT IN SIDEWALK AND REPLACED 5/8 INCH CURB COCK FOR ABANDON LOT BACKFILLED AREA
201900624701 | 2019-04-19 | LEAD | 727 | ESPLANADE AV | BOURBON | WILK | INLER SERVICE LEAK /** 1) MN: A295602 SN: 0040080, *TAP: SIZE: A LOC: 107 FEET FROM P LINE AT BOURBON LRPL, *MB: CODE: ADK1 LOC: 103.5' FROM LRPL BOURBON &5.O INSIDE CURB ****/ | 2019-04-17 | EXCAVATED IN TREE ROOTS AND REPLACED BOTTOM AND SET NEW 5/8 INCH METER BACKFILLED AREA METERAND CASING BOTTOM WAS DAMAGED WHILE EXCAVATING IN LARGE TREE ROOTS
201900625501 | 2019-04-19 | LEAD | 2443 | N GALVEZ | MUSIC | WMBK | WM-LEAK IN SIDEWALK MISSING METER BOX CASING PLEASE RESET METER BOX CASING, ALSO CHANGE OUTLET WASHER LEAK. LEFT 1 CONE FOR PROTECTION /** 1) MN: A285653 SN: 0079923, *TAP: SIZE: C LOC: 14 FEET FROM P LINE AT MUSIC, *MB: CODE: ADK2 LOC: 16' P/L MUSIC 8' OUTSIDE 2' INSIDE CURB ** 2) MN: SN: 0058435, *TAP: SIZE: A LOC: 15 FEET FROM P LINE AT MUSIC, *MB: CODE: CDM1 LOC: FRONT 15' P.L. MUSIC ****/ | 2019-04-25 | EXCAVATED 2 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIR ON OUTLET BACKFILL JOB WITH RIVERSAND. JOB COMPLETE
201900625601 | 2019-04-19 | LEAD | 722 | INDEPENDENCE | ROYAL | WILK | ML-METER LEAK ACCT#152953-428460 METER#A227603 INLET SERVICE LEAK IN THE SIDEWALK, ALSO CHANGE BROKEN METER BOX CASING /** 1) MN: A227603 SN: 0051703, *TAP: SIZE: A LOC: 168 FEET FROM P LINE AT ROYAL, *MB: CODE: AEKL LOC: ON INDEPENDENCE, 165' FROM P.L. ROYAL,8' OUTSIDE ****/ | 2019-05-14 | EXCAVATED 2 X 6 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET RELOCATED METER INTO SIDEWALK AND RAISE METER BOX UP TO GRADE BACKFILLED JOB WITH RIVERSAND COLDMILL (JOB COMPLETE)
201900625901 | 2019-04-19 | LEAD/PLASTIC | 916-18 | CHEROKEE | FRERET | WILK | ML-METER LEAK METER#A403502 ACC#121867-715349 CHANGED FROM 912 CHEROKEE INLET SERVICE LEAK BEHIND CURB COCK FLOODING SIDEWALK & GRASS /** AT 916: 1) MN: A308087 SN: 0030345, *TAP: SIZE: A LOC: 147 FEET FROM P LINE AT BURTHE, *MB: CODE: BEK4 LOC: 147' P.L. BURTHE ****/ | 2019-04-30 | EXCAVTED IN MUD PLOT AND TREE ROOTS TO REPAIR A BAD 5/8" METER BOX COCK FOUND LEAD ON INLET AND PLASTIC ON OUTLET
201900628901 | 2019-04-21 | LEAD | 1721 | ABUNDANCE | REPUBLIC | WILK | INLET SERVICE LEAK /** 1) MN: A271183 SN: 0072877, *TAP: SIZE: A LOC: 129 FEET FROM P LINE AT REPUBLIC, *MB: CODE: ADN2 LOC: ON ABUNDANCE,131.2' P.L. REPUBLIC,10' OUTSIDE P.L. ****/ | 2019-04-16 | EXCAVATED IN MUD PLOT AND REPLACED 3/4 INCH CURB COCK FOR ABANDON HOUSE NO METER INSDIE BOX BACKFILLED AREA. JOB COMPLETE
201900630501 | 2019-04-22 | LEAD | 2823 | D"ABADIE |  | WMTLK | WM-LEAK IN SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER LOCATED IN TREE ROOTS METER UNDER WATER /** 1) MN: A153635 SN: 0071590, *TAP: SIZE: B LOC: 168 FEET FROM P LINE AT DUPRE N, *MB: CODE: CDLN LOC: 165FT FROM LPL DUPRE ON D ABADIE ****/ | 2019-04-26 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INLET SERVICE LINE BACKFILLED + DRESSED UP AREA ALSO REPLACED 5/8 INCH METER BOX BOTTOM JOB COMPLETE
201900631301 | 2019-04-22 | LEAD | 1407 | FELICIANA |  | WMTLK | L UDUEBOR SAID THERE IS A BAD LEAK COMING FROM BLEEDER VALVE. PLEASE REPAIR METER A379646 LOC 119713 EXAMINE INLET & OUTLET SERVICE FOR A LEAK /** 1) MN: A130219 SN: 0072773, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT VILLERE N, *MB: CODE: AE LOC: BY FENCE 6TH FROM GATE 82' P.L. N VILLERE ****/ | 2019-05-03 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201900631501 | 2019-04-22 | LEAD | 2518 | N TONTI | MUSIC | WMTLK | PP-POOR PRESSURE ACCT#217579-484835 METER#A406431 **********CUSTOMER OUT OF WATER********** J GILLIAM 10:01 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER BOX SHIFTED UNABL TO EXAMINE PROPERLY /** 1) MN: A116214 SN: 0083719, *TAP: SIZE: B LOC: 137 FEET FROM P LINE AT MUSIC, *MB: CODE: CDMN LOC: METER ON N TONTI 137 FT FROM PL MUSIC 2FT FRM CURB ****/ | 2019-04-22 | REPLACED CHOKE 5/8 INCH WATER METER AT ABOVE LOCATION CUSTOMER HAS WATER NOW OLD METER INFO: A282721 FACT: 47144615 MAKE: SENSUS READ: 90
201900633501 | 2019-04-22 | LEAD | 1331 | LESSEPS |  | WMRE | INSP M FRAZIER SAID SERVICE IS BELOW GRADE. PLEASE RAISE TO GRADE AND CHANGE METER A270184 LOC 126072 LOCATE, RAISE TO GRADE AND CHANGE METER /** 1) MN: A270184 SN: 0048941, *TAP: SIZE: A LOC: 119 FEET FROM P LINE AT VILLERE N, *MB: CODE: BEL2 LOC: ON LESSEPS,121' FROM L.R.P.L. NO. VILLERE ****/ | 2019-04-29 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIR ON OUTLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201900633601 | 2019-04-22 | LEAD | 2328 | IBERVILLE |  | WOLK | INSP L UDUEBOR SAID SERVICE IS LEAKINK FROM OUTLET, NOT WASHERS. PLEASE REPAIR AND CHANGE METER A407532 LOC 113491 EXAMINE OUTLET SERVICE FOR LEAK AND CHANGE METER /** 1) MN: A293183 SN: 0055737, *TAP: SIZE: A LOC: 107 FEET FROM P LINE AT TONTI N, *MB: CODE: DKN LOC: BY STPS ON IBERVILLE 106.6' FROM URPL N TONTI ****/ | 2019-05-01 | EXCAVATED 2 X 4 MUD PLOT FOUND LEAK ONJ 5/8 INCH OUTLET SERVICE MADE REPAIR ON OUTLET BACKFILLED JOB WITH RIVERSAND ALSO CHANGE OUT 5/8 INCH METER AT ABOVE LOCATION ******************OLD METER INFO********* METER:A407532 FAC:14113294 MAKE:HERSEY READ:265
201900634201 | 2019-04-22 | LEAD | 1572 | N PRIEUR | LAPEYROUSE | WILK | WM-LEAK ON THE SIDEWALK INLET SERVICE LEAK IN MUDPLOT IN FRONT OF VACANT HOUSE, NO METER IN BOX /** 1) MN: A224477 SN: 0049207, *TAP: SIZE: A LOC: 90 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: BE LOC: 90FT FROM USPL LAPEYROUSE ****/ | 2019-05-01 | EXCAVATED 4 X 4 CONCRETE DRIVEWAY FOUND LEAK ON 3/4 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL ALSO RAISE METER BOX UP TO GRADE
201900636301 | 2019-04-23 | LEAD | 2241 | N GALVEZ |  | WMRE | LOCATION: 144041 MTR# A 434926 INSP UDUEBOR STATES METER BOX IS BELOW GRADE. PLEASE RAISE TO GRADE LEVEL. LOCATE & BRING METER TO GRADE /** 1) MN: A146216 SN: 0075433, *TAP: SIZE: A LOC: 49 FEET FROM P LINE AT MARIGNY, *MB: CODE: CDLN LOC: ON NO. GALVEZ, 48.5' FROM P.L. MARIGNY ****/ | 2019-05-06 | EXCAVATED 2 X 2 MUD PLOT AROUND METER BOX RAISED METER BOX TO GRADE BACKFILLED AND CLEANED THE AREA
201900636401 | 2019-04-23 | LEAD | 1326 | PORT |  | WOLK | LOCATION: 117205 MTR# A 351614 INSP UDUEBOR STATES OUTLET SERVICE IS LEAKING. PLEASE REPAIR. EXAMINE OUTLET SERVICE FOR A LEAK /** 1) MN: A351614 SN: 0044737, *TAP: SIZE: A LOC: 142 FEET FROM P LINE AT VILLERE N, *MB: CODE: CFM1 LOC: 142' P.L. N VILLERE ****/ | 2019-05-03 | EXAMINED PUMPED METER BOX CASING DOWN AND REPLACED WASHERS ON INLET AND OUTLET INSIDE NETER BOX
201900636901 | 2019-04-23 | LEAD | 1003 | TRICOU | RAMPART | WMTLK | ML-METER LEAK ACCT#142107-426407 METER#A408073 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-02 | EXCAVATED INMUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESED UP AREA
201900638801 | 2019-04-23 | LEAD | 2828 | ELYSIAN FIELDS AV |  | WMTLK | ML- METER LEAK ACCT# 182298-500758 METER # D008095 EXAMINE INLET & OUTLET SERVICE FOR A LEAK ON A LARGE METER IN THE MANHOLE IN THE SIDEWALK /** 1) MN: D003244 SN: 0131853, *TAP: SIZE: D LOC: 105 FEET FROM P LINE AT FLORIDA AVE, *MB: CODE: CE LOC: ON ELYSIAN FIELDS AVE., 100' FROM P.L. FLORIDA AVE ** 2) MN: C025601 SN: 0131853, *TAP: SIZE: H LOC: 183 FEET FROM P LINE AT FLEUR DE LIS DR, *MB: CODE: CERP LOC: 188FT FROM PL FLORIDA 3FT OUTSD CURB IN STREET ****/ | 2019-05-14 | EXAMINED JOB FOUND OUTLET LEAK ON UNION. LEAD ON OUTLET AND PLASTIC WAS ON THE INLET. REPLACED 1 1/2 UNION MAYBE PIN LEAK ON LEAD OUTLET
201900640101 | 2019-04-23 | LEAD | 2722 | PALMYRA |  | WMRE | INSP M FRAZIER STATES SERVICE NEEDS TO BE LOCATED OR RAISED TO GRADE. PLEASE SET 5/8 METER. LOC 307414 LOCATE, MARK, SET 5/8 METER, ALSO RENEW OULET SERVICE *****NEW CONSTRUCTION***** /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-03 | EXCAVATED MUD PLOT + LOCATED 5/8 INCH METER BOX RAISED METER BOX BOTTOM TO GRADE + SET METER BACKFILLED + DRESSED UP AREA
201900640701 | 2019-04-23 | LEAD | 2649 | N ROCHEBLAVE | ARTS | WOLK | ML: METER LEAK, MTR # A430965, ACCT # 219019-485001 CHECK FOR LEAK @ PROPERTY LINE, CONSTANT REG /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-19 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION NO CONSTRANT REG FOUND ON METER
201900640801 | 2019-04-23 | LEAD | 1617 | ARTS |  | WILK | LOCATION ID-307260 MTR-A439403 MTR ON/CUST NOT GETTING WATER/UNDER RENOVATION DRY INLET, HOUSE UNDER RENOVATION /** 1) MN: A257244 SN: 0056615, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: CEM1 LOC: INS 130' P.L. N CLAIBORNE AVE ****/ | 2019-04-30 | EXAMINED JOB AT ABOVE LOCATION FOUND WATER ON INLET CUSTOMER HAS WATER NOW
201900643301 | 2019-04-24 | LEAD | 3244 | CLOUET | HUMANITY | WILK | INLET SERVICE LEAK IN THE MUDPLOT FLOODINGTHE STREET /** 1) MN: SN: 0100403, *TAP: SIZE: A LOC: 49 FEET FROM P LINE AT HUMANITY, *MB: CODE: AKO LOC: ON CLOUET 34FT FROM PL OF HUMANITY 2FT OUTSIDE PL ****/ | 2019-04-23 | EXAMINED JOB, LOCATED METERBOX UNDER TALL GRASS IN MUDPLOT. FOUND LEAD ON INLET SERVICE AND STOP LEAK ON INLET SERVICE.
201900644201 | 2019-04-24 | LEAD | 3318 | N DORGENOIS |  | WOLK | LOCATION# 175084 CUSTOMER# 433945 METER# B029054 INSPECTOR DID AN OUTSIDE INSPECTION FOUND CONSTANT STOP & GO CAN'T DETERMINE WHERE LEAK IS COMING FORM.....PLEASE REPAIR /** 1) MN: SN: 0118474, *TAP: SIZE: B LOC: 139 FEET FROM P LINE AT PIETY, *MB: CODE: ADN2 LOC: BET DESIRE & PIETY 138FT PL PIETY 8' OUTSIDE ****/ | 2019-05-08 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION NO CONSTANT REGISTATION ON METER JOB COMPLETE
201900645901 | 2019-04-24 | LEAD | 1873 | AGRICULTURE |  | WMTLK | LOCATIONID#183176-451135 METER#A263903 LEAK INSIDE METERBOX /** 1) MN: A263903 SN: 0099961, *TAP: SIZE: CCC LOC: 50 FEET FROM P LINE AT ALLEN, *MB: CODE: BEDK LOC: ON AGRICULTURE ST.50' FROM PL OF ALLEN 7' OUTSIDE ****/ | 2019-05-06 | MADE REPAIR ON INLET SERVICE LINE INSIDE MANHOLE
201900647201 | 2019-04-24 | LEAD | 2500-02 | DUMAINE | N DORGENOIS | WILK | **********PICK UP********** INLET SERVICE LEAK IN METER BOX WATER RUNNING AROUND THE CORNER /** AT 2500: 1) MN: A275937 SN: 0012091, *TAP: SIZE: B LOC: 49 FEET FROM P LINE AT DUMAINE, *MB: CODE: CFHM LOC: SIDE ST BY STEPS ON N ROCHEBLAVE 49' P.L. DUMAINE ****/ | 2019-05-30 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900647501 | 2019-04-24 | LEAD | 1413 | DESIRE |  | WOLK | ML METER LEAK ACCOUNT #256872-711506 METER #A429317 EXAMINE OUTLET SERVICE FOR A LEAK /** 1) MN: 000000 SN: 0082067, *TAP: SIZE: A LOC: 84 FEET FROM P LINE AT VILLERE N, *MB: CODE: BDK2 LOC: ON DESIRE 84FT FROM VILLERE ****/ | 2019-05-07 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH HANDWHEEL BACKFILLED + DRESSED UP AREA. JOB COMPLETE
201900649201 | 2019-04-24 | LEAD | 1237 | LOUISA DR |  | WILK | ML- METER LEAK ACCT#160391-521622 METER# A397414 EXAMINE INLET SERVICE FOR A LEAK INSIDE METER BOX /** 1) MN: A283045 SN: 0098745, *TAP: SIZE: A LOC: 77 FEET FROM P LINE AT URQUHART, *MB: CODE: BD25 LOC: 61FT FROM PL URQUHART ON LOUISA 7FT OUTSIDE PL 3FT ****/ | 2019-05-03 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201900650501 | 2019-04-24 | LEAD | 3226 | ORLEANS AV | N RENDON | WMTLK | ML: METER KLEAK ACCT#307108-488376 MTR# A433257 EXAMINE INLET/OUTLET SERVICE FOR A LEAK, METER BOX UNDER WATER /** 1) MN: SN: 0082381, *TAP: SIZE: B LOC: 104 FEET FROM P LINE AT HAGAN AVE, *MB: CODE: CDN2 LOC: ON ORLEANS AVE 104' FROM PL HAGAN AVE ****/ | 2019-04-30 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK ON INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900651201 | 2019-04-24 | LEAD | 2566 | JONQUIL | FRANKLIN AV | WILK | MI- LEAK IN THE SIDEWALK INLET SERVICE LEAK IN MUDPLOT FLOODING CURB GETTING OFF IN DCB /** 1) MN: A252363 SN: 0087584, *TAP: SIZE: A LOC: 56 FEET FROM P LINE AT FRANKLIN AVE, *MB: CODE: __ LOC: ****/ | 2019-05-07 | EXCAVATED DOWN O INELT SERVICE FROM METER TO UNDERNEATH CURB. FOUND LEAD AND SERVICE WAS LEAKING UNDERNEATH CURB MADE REPAIRS BY REPLACING COCK WASHERS, AND 3 FT INLET BACKFILLED. (JOB COMPLETE)
201900653201 | 2019-04-25 | LEAD/PLASTIC | 4918 | HAIK DR |  | WMTLK | LOCATIONID#300628-710194 METER#A430027 METERBOX OVERFLOWING /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-02 | EXCAVATED IN TREE ROOTS BY HAND TO REPAIR A BAD 5/8" METER COCK FOUND LEAD ON INLET
201900654101 | 2019-04-25 | LEAD | 1829 | FRENCHMEN | N PRIEUR | WILK | INLET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-25 | MADE 4 X 4 SIDEWALK AND MADE REPAIR ON 3/4 INCH OUTLET SERVICE BACKFILLED AREA
201900654201 | 2019-04-25 | LEAD | 1912 | FRENCHMEN | N PRIEUR | WILK | INLET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-24 | EXCAVATEDE IN MUD PLOT AND MADE REPAIRS ON ABANDON 3/4 INCH SERVICE FOR ABANDON LOT BACKFILLED AREA
201900655001 | 2019-04-25 | LEAD | 2644 | BRUXELLES | N BROAD | WOLK | OUTLET SERVICE LEAK /** 1) MN: A122782 SN: 0065761, *TAP: SIZE: A LOC: 102 FEET FROM P LINE AT BROAD N, *MB: CODE: BDE2 LOC: 102' P.L. N BROAD ****/ | 2019-05-02 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIR ON OUTLET RAISE METER BOX UP TO GRADE BACKFILLED JOB WITH RIVERSAND
201900656401 | 2019-04-25 | LEAD | 3337 | ST ANN | HAGAN AV | WMTLK | ML- METER LEAK METER# A425923 ACCT# 149346-520484 EXAMINE INLET/OUTLET SERVICE FOR A LEAK, METER BOX UNDER WATER /** 1) MN: A268798 SN: 0026730, *TAP: SIZE: B LOC: 284 FEET FROM P LINE AT HAGAN AVE, *MB: CODE: CDLM LOC: HAGAN/MOSS METER ON ST ANN 284 FT FROM PL N HAGAN ****/ | 2019-05-02 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900658901 | 2019-04-26 | LEAD | 2300 | ALVAR | N TONTI | WILK | INLET SERVICE LEAK /** 1) MN: A229975 SN: 0094246, *TAP: SIZE: A LOC: 7 FEET FROM P LINE AT TONTI N, *MB: CODE: ADK LOC: ON ALVAR, 7' FROM P.L. NO. TONTI,7.5' OUTSIDE P.L. ****/ | 2019-04-25 | EXCAVATED 2 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND JOB COMPLETE
201900659001 | 2019-04-26 | LEAD | 2614 | ST CLAUDE AV | FRANKLIN AV | WILK | INLET SERVICE LEAK /** 1) MN: A319789 SN: 0028339, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT LAFAYETTE, *MB: CODE: AFLM LOC: ON ST. CLAUDE AVE.,134' FROM L.R.P.L. ALMONASTER ****/ | 2019-04-25 | REMOVE JUMPER FROM INSIDE OF METER BOX ALSO REMOVE HANDWHEEL
201900659101 | 2019-04-26 | LEAD | 1901 | ALMONASTER AV | N PRIEUR | WILK | INET SERVICE LEAK /** 1) MN: A286154 SN: 0169017, *TAP: SIZE: A LOC: 2 FEET FROM P LINE AT PRIEUR NO., *MB: CODE: CDLM LOC: ON ALMONASTER AVE.,11' FROM U.S.P.L. NO. PRIEUR ****/ | 2019-04-25 | REPLACE BOTH INLET AND OUTLET WASHERS AAT ABOVE LIOCATION. JOB COMPLETE
201900659201 | 2019-04-26 | LEAD | 2217 | FELICIANA | N MIRO | WILK | INLET SERVICE LEAK /** 1) MN: A253630 SN: 0102914, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT MIRO N, *MB: CODE: AEL1 LOC: ON FELICIANA, 150' FROM P.L. NO. MIRO, 5' OUTSIDE ****/ | 2019-04-25 | EXCAVATED 2 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH ABANDON INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900659801 | 2019-04-26 | LEAD | 3063 | DAUPHINE |  | WMTLK | BAD MTR LEAK/AREA FLOODED /** 1) MN: A242402 SN: 0015561, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT CLOUET, *MB: CODE: OOO LOC: 75' P.L. CLOUET ****/ | 2019-05-03 | MADE 4 X 4 CUT IN SIDEWALK AND REPLACED 5/8 INCH CURB COCK AND MADE REPAIR ON 3/4 8INCH INLET SERVICE BACKFILLED AREA
201900662101 | 2019-04-26 | LEAD | 1370 | ANNETTE | N VILLERE | WILK | ML: METER LEAK ACCT#120645-486674 MTR#A344302 INLET SERVICE LEAK IN THE SIDEWALK /** 1) MN: A333898 SN: 0036676, *TAP: SIZE: A LOC: 125 FEET FROM P LINE AT VILLERE N, *MB: CODE: AF5 LOC: INSIDE RS STEPS - 125' P.L. N VILLERE ****/ | 2019-05-03 | EXCAVATED 2 X 4 MUD PLOT IN SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900662601 | 2019-04-26 | LEAD | 2219 | N DERBIGNY |  | WILK | LOCATION ID-213422 MTR-A406562 METER LEAK BAD CURB COCK INSIDE METER BOX /** 1) MN: A318993 SN: 0047247, *TAP: SIZE: A LOC: 14 FEET FROM P LINE AT ELY FIELDS, *MB: CODE: CD LOC: ON DERBIGNY 14FT FROM DIV P/L ELY FIELDS 8FT ** 2) MN: C025955 SN: 0047247, *TAP: SIZE: C LOC: 167 FEET FROM P LINE AT ELYSIAN FIELDS AVE, *MB: CODE: CDM3 LOC: ON N DERBIGNY 140FT FROM PL OF ELYSIAN FIELDS AVE ****/ | 2019-05-07 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900662701 | 2019-04-26 | LEAD | 1527 | ST ROCH AV | N CLAIBORNE AV | WILK | ML: METER LEAK ACCT#122016-482222 MTR#A386468 BAD CURB COCK LEAKING INSIDE METER BOX /** 1) MN: SN: 0057667, *TAP: SIZE: A LOC: 90 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: CFL LOC: ON ST. ROCH AVE.,90' FROM L.R.P.L. NO. CLAIBORNE ****/ | 2019-05-03 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900663001 | 2019-04-26 | LEAD | 4246 | DALE |  | WMTLK | ML-METER LEAK ACCT#185297-441691 MTR#A389646 EXAMINE INLET/OUTLET SERVICE FOR A LEAK FLOODING CURB GETTING OFF IN DCB 4/27/19 CAUSING POOR PRESSURE. JOB GIVEN TO J, MORGAN /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-27 | EXCAVATED AROUND METER BOX TO EXPOSE COPPER OUTLET EXCAVATED THROUGH SIDEWALK BY HAND TO EXPOSE OUTLET MADE REPAIR ON OUTLET TO STOP LEAK HOLE WAS BACKFILLED AND DRESSED UP. (JOB COMPLETE)
201900663701 | 2019-04-27 | LEAD | 2521 | ORLEANS | N ROCHEBLAVE | WILK | INLET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-04-26 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900664101 | 2019-04-27 | LEAD/PLASTIC | 4330 | RANDOLPH | MANDOLIN | WILK | ML- METER LEAK METER# B019713 ACCT# 166837-498446 INLET LEAK (BAD CURB COCK) /** 1) MN: B021757 SN: 0107069, *TAP: SIZE: B LOC: 307 FEET FROM P LINE AT MANDOLIN, *MB: CODE: CDLM LOC: 2ND WINDOW 307' P/L MANDOLIN 7' OUTSIDE 3' INSIDE ****/ | 2019-05-02 | EXCAVATED IN MUD PLOT TO REPAIR AND BAD 3/4" COCK AND RAISE TO GRADE FOUND LEAD ON INLET
201900667201 | 2019-04-29 | LEAD | 634 | ESPLANADE AV |  | WOLK | LOCATION ID-101016 MTR-BO32414 UNDERGROUND LEAK BETWEEN MTR AND STOP & WASTE/CONS REG ON MTR /** 1) MN: B032414 SN: 0003110, *TAP: SIZE: B LOC: 65 FEET FROM P LINE AT ROYAL, *MB: CODE: D LOC: ON ESPLANADE AVE.,65' FROM R.P.L. ROYAL ** 2) MN: G001704 SN: 0053110, *TAP: SIZE: G LOC: 73 FEET FROM P LINE AT ROYAL, *MB: CODE: R LOC: ON ESPLANADE 69' P/L ROYAL 23' OUTSD PL ****/ | 2019-05-06 | REPLACED 3/4 INCH HANDWHEEL + GUTS IN METER BOX
201900668502 | 2019-05-07 | LEAD | 200 | S BROAD | CLEVELAND AV | WMTLK | EXAMINE JOB AT ABOVE LOCATION FOUND LEAK ON 2 INCH INLET SERVICE UNABLE TO MAKE REPAIR DUE TO DOCTOR"S OFFICE ON LINE BEST TO MAKE REPAIR ON (SUNDAY) WEEKEND /** 1) MN: E004227 SN: 0047648, *TAP: SIZE: E LOC: 78 FEET FROM P LINE AT BROAD S, *MB: CODE: AEHP LOC: ON CLEVELAND AVE.,77' FROM P.L. SO. BROAD,7' ****/ | 2019-05-26 | EXCAVATED IN MUD PLOT + REPLACED 2 INCH INLET SERVICE LINE FROM CURB TO MANHOLE BACLFILLED + DRESSED UP AREA
201900670001 | 2019-04-29 | LEAD | 1312 | GORDON | N VILLERE | WILK | ML- METER LEAK METER# A415120 ACCT# 305639-705859 INLET SERVICE LEAK INTERFERING WITH CONTRACTORS WORK /** 1) MN: SN: 0088622, *TAP: SIZE: A LOC: 111 FEET FROM P LINE AT URQUHART, *MB: CODE: CD LOC: RES ON GORDON 111FT FROM PL URQUHART ****/ | 2019-05-07 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201900670201 | 2019-04-29 | LEAD | 2442 | ST BERNARD AV | N ROCHEBLAVE | WOLK | ML- METER LEAK METER# A372092 ACCT# 144371-489868 ***FLOODING AREA***** OUTLET SERVICE LEAK IN TREE ROOTS /** 1) MN: A230157 SN: 0075850, *TAP: SIZE: A LOC: 296 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: AD LOC: ON ST BERNARD 296FT FROM ROCHEBLAVE N ****/ | 2019-05-06 | EXCAVATED IN CONCRETE DRIVEWAY THROUGH LARGE TREE ROOTS + MADE REPAIR ON 3/4 INCH OUTLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201900671801 | 2019-04-29 | LEAD | 1327 | LESSEPS |  | WMTLK | ML - METER LEAK ACCOUNT NUMBER - 144755-430862 METER NUMBER - A419476 EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX FLOODED /** 1) MN: A210915 SN: 0076258, *TAP: SIZE: A LOC: 193 FEET FROM P LINE AT URQUHART, *MB: CODE: CEL1 LOC: ON LESSEPS ST 200' FROM PL URQUHART ST ****/ | 2019-05-07 | EXCAVATED IN LIMESTONE GUTTER BOTTOM + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA JOB COMPLETE
201900672001 | 2019-04-29 | LEAD | 1324 | LESSEPS |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 1333320-511536 METER NUMBER - A191465 INLET SERVICE LEAK BAC CURBCOCK /** 1) MN: A191465 SN: 0064169, *TAP: SIZE: A LOC: 205 FEET FROM P LINE AT URQUHART, *MB: CODE: OOO LOC: ON LESSEPS ST 205' FROM URQUHART ST 1' FROM CURB ****/ | 2019-05-07 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA JOB COMPLETE
201900673001 | 2019-04-29 | LEAD | 2333 | PAUGER |  | WILK | MI- LEAK IN STREET INLET SERVICE LEAK IN ASPHALT STREET /** 1) MN: A115255 SN: 0053542, *TAP: SIZE: B LOC: 92 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: OOOO LOC: ON PAUGER 93FT FROM PL N DERBIGNY 7FT OUTSD PL ****/ | 2019-05-08 | EXCAVATED 8 X 6 STREET CUT MADE REPAIR ON INLET AT WATER MAIN BACKFILLED AND CLEAN ED THE AREA. *WORK WAS DONE FOE 2333 PAUGER* (JOB COMPLETE)
201900675001 | 2019-04-30 | LEAD | 1635 | FRANCE |  | WMBK | LOCATIONID#136553-432850 METER#A360544 CASING SHIFTED OVER METER /** 1) MN: A334696 SN: 0083839, *TAP: SIZE: A LOC: 285 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: BDK1 LOC: ON FRANCE, 285' FROM P.L. NO. CLAIBORNE AVE. ****/ | 2019-05-08 | REPLACE UPPER METER BOX CASING AND BROKEN 5/8 INCH WATER METER AT ABOVE LOCATION OLD METER INFO A360544 FACT:70688253 MAKE: SENSUS READ: 35647
201900675501 | 2019-04-30 | LEAD | 719 | N DORGENOIS |  | WILK | ML METER LEAK ACCOUNT #118763-523292 METER A422182 INLET SERVICE LEAK /** 1) MN: A264117 SN: 0029271, *TAP: SIZE: A LOC: 77 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: BFH4 LOC: SIDE/END HSE INS PL/ST ANN 75 FT PL N DORGENOIS ****/ | 2019-05-06 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900676201 | 2019-04-30 | LEAD | 414 | S SALCEDO |  | WILK | WM--LEAK IN STREET INLET SERVICE LEAK BETWEEN CURB AND STREET /** 1) MN: A249435 SN: 0051078, *TAP: SIZE: A LOC: 129 FEET FROM P LINE AT BANKS, *MB: CODE: BFW2 LOC: ON S SALCEDO 129FT FROM PL OF BANKS ****/ | 2019-05-20 | MADE A 8 X 10 CUT IN ASPHALT STREET + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE COMPACTED BACKFILLED + DRESSED UP AREA
201900677801 | 2019-04-30 | LEAD | 2243 | CLOUET | N TONTI | WILK | INLET SERVICE LINE /** 1) MN: A331016 SN: 0175541, *TAP: SIZE: A LOC: 27 FEET FROM P LINE AT CLOUET, *MB: CODE: BDH6 LOC: ON N TONTI 27' PL CLOUET BET 1ST WIND & DOOR ****/ | 2019-04-29 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA. JOB COMPLETE
201900678501 | 2019-04-30 | LEAD | 1511 | DESIRE |  | WMTLK | LOCATIONID#145813-712037 METER#A407208 LEAK INSIDE METERBOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-07 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900683401 | 2019-05-01 | LEAD | 1809-11 | FRENCHMEN | N ROMAN | WILK | WM-LEAK IN STREET INLET SERVICE LAAK IN ASPHALT STREET /** AT 1809: 1) MN: A282005 SN: 0027889, *TAP: SIZE: A LOC: 60 FEET FROM P LINE AT ROMAN, *MB: CODE: CD LOC: ON FRENCHMEN 60FT FROM ROMAN ** AT 1811: 2) MN: A281463 SN: 0027889, *TAP: SIZE: A LOC: 18 FEET FROM P LINE AT ROMAN, *MB: CODE: CD LOC: ON FRENHMEN 18FT FROM ROMAN 5FT OUTSIDE ****/ | 2019-05-15 | EXCAVAGE IN ASPHALT STREET + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE COMPACTED BACKFILLED + DRESSED UP AREA JOB COMPLETE
201900686901 | 2019-05-02 | LEAD | 1600BLK | LAPEYROUSE | N CLAIBORNE AV | WMLK | MI: LEAK IN THE SIDEWALK ***************B LEAVE IN SYSTEM*************** CHANGED FROM 1600 ST BERNARD AV AND N DERBIGNY LEAK ON THE MAIN ON SIDEWALK BEHIND BUILDING /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-18 | EXCAVATED 6 X 10 CONCRETE SIDEWALK FOUND LEAK ON ABANDON 3/4 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900687201 | 2019-05-02 | LEAD | 3108 | BIENVILLE |  | WILK | ML-METER LEAK ACCT#142417-531532 MTR#A363424 EXAMINE INLET SERVICE FOR LEAK IN BOX /** 1) MN: A145787 SN: 0073596, *TAP: SIZE: B LOC: 71 FEET FROM P LINE AT SALCEDO N, *MB: CODE: ADK LOC: ON BIENVILLE 71FT FROM PL SALCEDO UPPER SD DR ****/ | 2019-05-13 | EXCAVATED IN CONCRETE DRIVEWAY + REPLACED CURB COCK BACKFILLED + DRESSED UP AREA
201900687501 | 2019-05-02 | LEAD | 5908 | BURGUNDY |  | WILK | MI LEAK ON THE SIDEWALK /AND STREET EXAMINE INLET SERVICE FOR LEAK IN BOX /** 1) MN: A260564 SN: 0070820, *TAP: SIZE: B LOC: 41 FEET FROM P LINE AT ALABO, *MB: CODE: AD LOC: ON BURGUNDY 43FT FROM PL ALABO ****/ | 2019-05-07 | EXCAVATED 2 X 2 MUD PLOT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900687601 | 2019-05-02 | LEAD | 1417 | LESSEPS | N VILLERE | WOLK | INSP L UDUEBOR SAID INLET AND OUTLET IS NOT LINING UP. CUSTOMER IS WAITING ON WATER. PLEASE REPAIR METER A435488 LOC 145092 *********************J.GILLIAM @ 11:46AM*************** INLET AND OUTLET SERVICE NOT LINIG UP, CUSTOMER WAITING ON WATER /** 1) MN: A312474 SN: 0076671, *TAP: SIZE: B LOC: 122 FEET FROM P LINE AT VILLERE N, *MB: CODE: BDL1 LOC: ON LESSEPS 122' FROM PL OF VILLERE N ****/ | 2019-05-02 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND 5/8 INCH OUTLET SERVICE NOT LINING UP WITH CURB COCK MADE REPAIR ON OUTLET BACKFILL JOB WITH RIVERSAND AND COLDMILL LEFT OFF IN THE METER BOX
201900688401 | 2019-05-02 | LEAD | 119 | BARONNE | CANAL | WILK | INLET SERVICE LEAK. LEAK UNDERNEATH DRIVEWAY CURB CUT. ECHOLOGICS REPORTED AND MARKED LEAK. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-25 | EXCAVATED 4 X 3 DRIVEWAY CUT MADE REPAIR ON ABANDONINLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201900688901 | 2019-05-02 | LEAD | 719 | TOURO | DAUPHINE | WMTLK | WATER METER LEAK. LEAK UNDERNEATH SIDEWALK..ECHOLOGICS REPORTED AND MARKED LEAK. /** 1) MN: A295805 SN: 0055317, *TAP: SIZE: B LOC: 148 FEET FROM P LINE AT ROYAL, *MB: CODE: CEND LOC: ON TOURO ST 149' FROM PL ROYAL ****/ | 2019-05-13 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201900689101 | 2019-05-02 | LEAD | 2260 | N ROMAN |  | WILK | LOCATION: 307499 INSP L MITCHELL UNABLE TO SET A METER, CURB COCK NOT LINING UP WITH WHEEL. PLEASE REPAIR AND SET A 3/4 METER. CUSTOMER WAITING ON WATER. CURB COCK & WHEEL NOT LINING UP ***HOUSE VACANT NO ELECTRIAL METER IN BOX*** /** 1) MN: B033187 SN: 0065576, *TAP: SIZE: B LOC: 204 FEET FROM P LINE AT MARIGNY, *MB: CODE: CDM1 LOC: 207FT FROM PL MARIGNY ****/ | 2019-05-08 | EXCAVATED 5 X 3 MUD PLOT GROUND METER BOX REPLACED CURB COCK AND SET 3/4 INCH METER BACKFILLED AND CLEANED THE AREA
201900689401 | 2019-05-02 | LEAD | 2262 | N ROMAN | MARIGNY | WILK | **********PICK UP********** UNABLE TO LOCATE CURB COCK, ALSO UPPER METER BOX IS BROKEN 5/2/19 PER SR#12874607 LSO SET METER (AJR) /** 1) MN: A278948 SN: 0065576, *TAP: SIZE: B LOC: 16 FEET FROM P LINE AT MARIGNY, *MB: CODE: __ LOC: ON N ROMAN 17FT FROM PL MARIGNY, 9' OUTSIDE ****/ | 2019-05-08 | EXCAVATED 5 X 3 MUD PLOT MADE REPAIR ON INLET SERVICE TO METER BOX BACKFILLED AND CLEANED THE AREA
201900691501 | 2019-05-02 | LEAD | N/A | CHEF MENTEUR HW | PAPANIA DR | WMLK | LEAK IN THE SIDEWALK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-03 | EXCAVATED IN MUDPLOT AND 4X6 SIDEWALK OVER WATER MAIN AND 2 INCH SERVICE FOUND 2 INCH LEAD LINE LEAKING.ON ABNANDIT SERVICE. MADE REPAIR ON 2 INCH INLET SERVICE BACKFILL MUD PLOT AND SIDEWALK.
201900691601 | 2019-05-02 | LEAD | 325 | N GAYOSO |  | WILK | ML-METER LEAK ACCT#152271-442386 METER#A275886 INLET SERVICE LEAK IN MUD PLOT /** 1) MN: SN: 0059769, *TAP: SIZE: A LOC: 205 FEET FROM P LINE AT BIENVILLE, *MB: CODE: ADM LOC: ON NO. GAYOSO,205' FROM P.L. BIENVILLE,11' OUTSIDE ****/ | 2019-05-15 | REPLACE BROKEN 5/8 INCH WATER METER AT ABOVE LOCATION OLD METER INFO: A275886 FACT: 45179256 MAKE: SENSUS READ: 4076
201900693401 | 2019-05-03 | LEAD | 2442-44 | LAMANCHE |  | WMRE | LOCATION: 213472 INSP UDUEBOR STATES METER SERVICE IS BURIED. PLEASE LOCATED AND RAISE TO GRADE. LOCATE SERVICE AND RAIS TO GRADE /** AT 2442: 1) MN: A316819 SN: 0140887, *TAP: SIZE: A LOC: 46 FEET FROM P LINE AT DORGENOIS, *MB: CODE: CD LOC: ON LAMANCHE 46F FROM DORGENOIS 6FT OUTSIDE 4FT ** AT 2444: 2) MN: SN: 0140887, *TAP: SIZE: B LOC: 45 FEET FROM P LINE AT NO. DORGENOIS, *MB: CODE: AFM LOC: ON LAMANCHE, 45' FROM P.L. NO. DORGENOIS, 6' OUT- ****/ | 2019-05-08 | EXCAVATED 4 X 4 MUD PLOT RAISE METER BOX UP TO GRADE BACKFILLED JOB WITH RIVERSAND NO METER IN BOX
201900694501 | 2019-05-03 | LEAD | 1638 | N TONTI |  | WMTLK | ML - METER LEAK ACCOUNT NUMBER - 198155-488990 METER NUMBER - A396686 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER /** 1) MN: A330538 SN: 0066821, *TAP: SIZE: __ LOC: 56 FEET FROM P LINE AT TONTI N, *MB: CODE: HL LOC: SIDE ST EDGE OF 4TH WINDOW ON ONZAGA 56' P.L. ****/ | 2019-05-10 | EXCAVATED IN LIMESTONE GUTTER BOTTOM + MADE REPAIR ON 3/4 INLET SERVICE LINE ALSO RAISED TWO 5/8 INCH METER BOX BOTTOM TO GRADE BACKFILLED + DRESSED UP AREA
201900694601 | 2019-05-03 | LEAD | 2040 | CONGRESS | N GALVEZ | WILK | ML- METER LEAK METER # B019554 ACCT# 172077-432281 INLET SERVICE LEAK IN BOX /** 1) MN: B019554 SN: 0115081, *TAP: SIZE: B LOC: 16 FEET FROM P LINE AT NO. GALVEZ, *MB: CODE: __ LOC: ON CONGRESS, 16' FROM P.L. NO. GALVEZ, 8' OUTSIDE ****/ | 2019-05-16 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 3/4 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900698301 | 2019-05-04 | LEAD | 4735 | CERISE AV |  | WMTLK | LOCATIONID#174517-446586 METER#A364077 LEAK INSIDE METERBOX /** 1) MN: A246883 SN: 0119858, *TAP: SIZE: A LOC: 397 FEET FROM P LINE AT HYDT AT HAMMOND HWY., *MB: CODE: BD2 LOC: ON CERISE AVE., 397' FROM HYDT. AT HAMMOND HWY., ****/ | 2019-05-09 | MADE A 4X3 CUT IN DRIVEWAY EXCAVATED DOWN ON INLET AND OUTLET SERVICES. FOUND LEAD SERVICES AND METER BOTTOM WAS BROEKN. MADE REPAIRS BY USING A METER BOX COMPLETE ALSO RAISED METER. BACKFILLED. (JOB COMPLETE)
201900699101 | 2019-05-04 | LEAD | 3134 | LAW | CLOUET | WOLK | ML METER LEAK MTR#C036621 ACCT#160380-433892 CHURCH ON THE CORNER - INSP FOUND CONSTANT REGISTRATION ON METER - UNABLE TO PERFORM S&W TEST /** AT 3134: 1) MN: C023416 SN: 0159496, *TAP: SIZE: C LOC: 248 FEET FROM P LINE AT CLOUET, *MB: CODE: BDL6 LOC: ON LAW 257FT FROM PL CLOUET OPP 3127 ****/ | 2019-05-14 | EXAMINED JOB AT ABOVE LOCATION FOUND NO CONSTANT REGISTRATION ON 1 INCH METER FOR ABOVE LOCATION
201900700501 | 2019-05-04 | LEAD | 2932 | URSULINES AV |  | WMTLK | LOCATIONID#109231-520843 METER#A379035 LEAK INSIDE METERBOX /** 1) MN: A309026 SN: 0026279, *TAP: SIZE: A LOC: 51 FEET FROM P LINE AT GAYOSO N, *MB: CODE: CD LOC: ON URSULINES 51FT FROM GAYOSO ****/ | 2019-05-15 | REPLACE BROKEN 5/8 INCH WATER METER AT ABOVE LOCATION OLD METER INFO: A379035 FACT: 73273466 MAKE: SENSUS READ: 46446
201900704601 | 2019-05-06 | LEAD | 2775 | GLADIOLUS | PEOPLES AV | WILK | WM-LEAK BETWEEN SIDEWALK AND STREET INLET SERVICE LEAKING FROM CURB COCK IN CONCRETE DRIVEWAY @ CURB /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-31 | MADE A 4X4 CUT IN DRIVEWAY. EXCACATED DOWN ON INLET AND OUTLET SERVICES. FOUND LEAD AND COCK ASLO HANDWHEEL WAS LEAKING. MADE REPAIRS BY USING A METER BOX COMPLETE. BACKFILLED. JOB COMPLETE
201900705701 | 2019-05-06 | LEAD | 1848 | N ROCHEBLAVE | GEORGE NICK CONNOR DR | WILK | ML: METER LEAK, MTR # A367346, ACCOUNT # 120377-490075 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: 000000 SN: 0061493, *TAP: SIZE: A LOC: 78 FEET FROM P LINE AT NO. ROCHEBLAVE, *MB: CODE: AFH LOC: ON HAVANA,91' FROM U.R.P.L. NO. ROCHEBLAVE ****/ | 2019-05-16 | CUSTOMER MOVE CAR FROM OVER METER IN DRIVEWAY EXAMINED AND PUMPED METER BOX DOWN AND REPLACED WASHERS ON INLET AND OUTLET INSIDE METER BOX
201900706501 | 2019-05-06 | LEAD | 2415 | N CLAIBORNE AV | ST ROCH AV | WMTLK | WM-LEAK IN SIDEWALK EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER IN LOW LYING AREA /** 1) MN: A328615 SN: 0051534, *TAP: SIZE: A LOC: 115 FEET FROM P LINE AT ST ROCH AVE, *MB: CODE: CDN1 LOC: ON NO. CLAIBORNE AVE., 116.4' FROM L.S.P.L. ****/ | 2019-05-16 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900707501 | 2019-05-06 | LEAD | 1861 | N TONTI |  | WILK | ML- METER LEAK AT METER # A 236429 ACCT# 141703 - 490255 EXAMINE INLET SERVICE LEAK IN BOX IN TREE ROOTS /** 1) MN: A321705 SN: 0061263, *TAP: SIZE: B LOC: 139 FEET FROM P LINE AT LONDON AVE, *MB: CODE: BD LOC: ON N TONTI 139' FROM PL OF LONDON AVE ****/ | 2019-05-23 | EXCAVATED IN TREE ROOTS AND MADE REPAIRS ON 3/4 INCH INLET SERVICE BEHIND METER BOX BACKFILLED AREA. JOB COMPLETE
201900708401 | 2019-05-06 | LEAD | 819 | N VILLERE | ST ANN | WOLK | MI- READY FOR TIE IN HOLE EXPOSED METER# A437589 ACCT# 307489-529506 CUSTOMER REQUEST TIE IN ***HOUSE UNDER RENOVATIONS*** /** 1) MN: 000000 SN: 0043355, *TAP: SIZE: A LOC: 155 FEET FROM P LINE AT ST ANN, *MB: CODE: BFK2 LOC: BY GATE 155' P.L. ST ANN ****/ | 2019-06-24 | CONTRACTOR HAS DEBRIS AND MOUNDS OF MUD ON TOP OF METER LOCATION
201900708701 | 2019-05-06 | LEAD | 2526 | CONGRESS |  | WILK | ML- METER LEAK LEAKING METER ON PREVIOUS REPAIRS SEE W/O# 201801813601 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A136424 SN: 0104924, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT LAW, *MB: CODE: BDK1 LOC: ON CONGRESS, 95' FROMP.L. LAW, 7' OUTSIDE P.L. ****/ | 2019-05-14 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900709401 | 2019-05-06 | LEAD | 1906 | ANDRY |  | WILK | PP: POOR PRESSURE ACCT#307437-711825 MTR#C036342 NO WATER ON THE INLET. HOUSE UNDER RENOVATIONS (C) /** 1) MN: 000000 SN: 0128916, *TAP: SIZE: C LOC: 58 FEET FROM P LINE AT PRIEUR N, *MB: CODE: BDL2 LOC: 58' P/L N PRIEUR IN DRIVEWAY 6' OUTSIDE 2 APTS ****/ | 2019-05-14 | EXCAVATED IN ASPHALT STTREET + CONCRETE DRIVEWAY + REPLACED 1 INCH INLET SERVICE LINE FROM WATER MAIN TO METER BOX RESTORING WATER TO ABOVE LOCATION COMPACTED BACKFILL + DRESSED UP AREA. (JOB COMPLETE)
201900711701 | 2019-05-07 | LEAD | 1220 | DAUPHINE |  | WMTBG | LOCATION# 301173 CUSTOMER# 529007 METER# C036291 INSPECTOR DID AN OUTSIDE INSPECTION, CAN'T LOCATE METER........PLEASE LOCATE METER AND RAISE TO GRADE CUSTOMER NEED AN ACTUAL READING NOT ESTIMATES CAN'T COMPLETE INVESTIGATION /** 1) MN: E004784 SN: 0107230, *TAP: SIZE: E LOC: 124 FEET FROM P LINE AT GOV NICHOLLS, *MB: CODE: OOOO LOC: MTR ON DAUPHINE 119FT FRM PL GOV NICHOLLS 5FT OUT ****/ | 2019-05-30 | FOUND METER INSIDE MANHOLE ALSO METER IS UP TO GRADE MARK ED MANHOLE COVER WITH BLUE PAINT. JOB COMPLETE
201900713101 | 2019-05-07 | LEAD | 2334 | MANDEVILLE | N TONTI | WILK | WM- LEAK IN THE STREET INLET SERVICE LEAK IN AN ASPHALT STREET /** 1) MN: A232031 SN: 0098650, *TAP: SIZE: A LOC: 258 FEET FROM P LINE AT TONTI, *MB: CODE: ADLK LOC: ON MANDEVILLE 261' FROM PL N TONTI 7' OUTSIDE PL ****/ | 2019-05-17 | EXCAVATED IN ASPHLAT STREET + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE COMPACTED BACKFILLED + DRESSED UP AREA
201900713601 | 2019-05-07 | LEAD | 3605 | ELAINE PL | N JEFFERSON DAVIS PK | WILK | WM- LEAK ON THE SIDEWALK - CUST STATED PREVIOUS LEAK REPAIRED AND LEAKING AGAIN CHANGED FROM 811 N JEFFERSON DAVIS PK INLET SERVICE LEAK @ THE MAIN ***CARS PARKING ON SERVICE*** /** 1) MN: A312385 SN: 0074409, *TAP: SIZE: A LOC: 78 FEET FROM P LINE AT JEFFERSON DAVIS PKWY., *MB: CODE: CDN2 LOC: ON ELAINE PL., 36' FROM P.L. JEFFERSON DAVIS PKWY ****/ | 2019-06-11 | MADE 3X 3 MUD PLOTWAS EXCAVATED MADE REPAIR ONI INLET SERVICE LINE TO STOP LEAK BACKFILLED AND CLEANED THE AREA. JOB COMPLETE
201900713801 | 2019-05-07 | LEAD | 2205 | ROFFIGNAC |  | WILK | INELT SERVICE LEAK /** 1) MN: A258152 SN: 0136821, *TAP: SIZE: A LOC: 89 FEET FROM P LINE AT MIRO N, *MB: CODE: BDM2 LOC: RES ON ROFFIGNAC 89FT FROM PL MIRO N 6' OUTSIDE PL ****/ | 2019-05-02 | ARRIVED AT ABOVE LOCATION + FOUND AREA FLOODED + LEAK COMING OFF PROPERTY OF ABANDONED LOT PUMPED DOWN GUTTER BOTTOM + LOCATED METER TURNED METER OFF STOPPING LEAK AT ABOVE LOCATION
201900713901 | 2019-05-07 | LEAD | 1639 | GENTILLY BL |  | WILK | INLET SERVICE LINE /** 1) MN: C024491 SN: 0054757, *TAP: SIZE: C LOC: 21 FEET FROM P LINE AT CRETE, *MB: CODE: BDKH LOC: ON FORTIN ST 21' P/L CRETE 7' OUTSIDE ****/ | 2019-05-01 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 1 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900714001 | 2019-05-07 | LEAD | 6330 | N DORGENOIS |  | WILK | INLET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-01 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA NO METER
201900714301 | 2019-05-07 | LEAD | 1121 | ST ANTHONY AV |  | WILK | INLET SERVICE LEAK /** 1) MN: A339216 SN: 0041655, *TAP: SIZE: A LOC: 0 FEET FROM P LINE AT , *MB: CODE: AFK LOC: ON ST ANTHONY ST 159' FROM LSPL N RAMPART ST ** 2) MN: SN: 0041655, *TAP: SIZE: A LOC: 146 FEET FROM P LINE AT RAMPART N, *MB: CODE: CEL LOC: 146FT PL N RAMPART 3RD METER 7' OUTSIDE 4' INSIDE ****/ | 2019-05-02 | EXCAVATED IN MUD PLOT AND MADE REPAIR ON 5/8 INCH INLET SERVICE BACKFILLED AREA
201900714401 | 2019-05-07 | LEAD | 1231 | BOURBON | BARRACKS | WILK | INLET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-02 | MADE REPAIR ON 1 INCH INLET SERVICE INSIDE OF MANHOLE
201900714601 | 2019-05-07 | LEAD | 2718 | PALMYRA | N BROAD | WILK | INLET SERVICE LEAK /** 1) MN: A328203 SN: 0080677, *TAP: SIZE: A LOC: 144 FEET FROM P LINE AT BROAD S, *MB: CODE: BF LOC: 145FT FROM PL BROAD ****/ | 2019-05-03 | EXCAVATED IN MU D PLOT + MADE REPAIR ON 5/8 INCH INLET + REPLACED 5/8 INCH WATER METER BACKFILLED + DRESSED UP AREA ****************OLD METER INFO*************** METER:A437268 FAC:19005705 MAKE:HERSEY READ:188
201900714801 | 2019-05-07 | LEAD | 5905 | BURGUNDY |  | WILK | ML-METER LEAK ACCT#300443-426277 METER#A426574 INLET SERVICE LEAK @ VACANT HOUSE NO 1 LIVE THERE /** 1) MN: A158557 SN: 0083134, *TAP: SIZE: C LOC: 46 FEET FROM P LINE AT ALABO, *MB: CODE: CF LOC: ON BURGRUNDY 54 FT FROM PL ALABO ****/ | 2019-05-20 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900716101 | 2019-05-07 | LEAD | 3117 | DAUPHINE | CLOUET | WILK | ML: METER LEAK ACCT#121982-704263 MTR# A341951 INLET SERVICE LEAK BAD BLEEDER VALVE ON THE SIDEWALK LEAKING IN THE ON POSITION IN THE METER BOX /** 1) MN: A122343 SN: 0040071, *TAP: SIZE: A LOC: 93 FEET FROM P LINE AT CLOUET, *MB: CODE: AFKO LOC: ON DAUPHINE,93' FROM L.S.P.L. CLOUET ****/ | 2019-05-16 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900716201 | 2019-05-07 | LEAD | 1331 | EGANIA | URQUHART | WMTLK | ML-METER LEAK ACCT#170112-423240 METER#A198677 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** 1) MN: A198677 SN: 0105564, *TAP: SIZE: A LOC: 246 FEET FROM P LINE AT VILLERE N, *MB: CODE: ADK LOC: RES ON EGANIA 246FT FROM PL N.VILLERE 8' OUTSIDE P ****/ | 2019-05-14 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH HAND WHEEL EXCAVATED FUTHER BACK AND MADE REPAIR ON 3/4 INCH OUTLET SERVICE BACKFILLED AREA
201900716301 | 2019-05-07 | LEAD | 1512 | ST LOUIS | N VILLERE | WILK | MI-LEAK AT CURB ABANDON INLET SERVICE @ THE MAIN 05/08/19 PER S/R 12875121 LEAK AT CURB FLOODING AREA (KSW) /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-10 | EXCAVATED IN MUD PLOT + MADE REPAIR ON ABANDONED 2 INCH INLET SERVICE LINE UNDER CURB AT ABOVE LOCATION BACKFILLED + DRESSED UP AREA
201900716601 | 2019-05-07 | LEAD | 834 | WILSON DR |  | WILK | ML- METER LEAK MTR# C026274 ACCT#149374-514419 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: C009027 SN: 0076670, *TAP: SIZE: Y LOC: 8 FEET FROM P LINE AT ELAINE, *MB: CODE: CDM3 LOC: 12FT. FRM LPL CURB 50FT FRM PL ELAINE METER ON ****/ | 2019-05-15 | EXCAVATED 4 X6 MUD PLOT FOUND LEAK ON 1 INCH OUTLET SERVICE MADE REPAIR ON OUTLET BACKFILLED JOB WITH RIVERSAND
201900718901 | 2019-05-07 | LEAD | 3337 | ST ANN | HAGAN AV | WILK | ML: METER LEAK ACCT#149346-520484 MTR#A425923 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A268798 SN: 0026730, *TAP: SIZE: B LOC: 284 FEET FROM P LINE AT HAGAN AVE, *MB: CODE: CDLM LOC: HAGAN/MOSS METER ON ST ANN 284 FT FROM PL N HAGAN ****/ | 2019-06-14 | EXCAVATED 4 X 4 MUD PLOT IN TREE ROOTS FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900721801 | 2019-05-08 | LEAD | 1734 | CONGRESS | N DERBIGNY | WILK | ML-METER LEAK ACCT# 305494-723667 METER# A413275 EXAMINE INLET SERVICE FOR A LEAK IN THE ROCKS /** 1) MN: A312678 SN: 0084453, *TAP: SIZE: A LOC: 249 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BDK LOC: ON CONGRESS, 249' FROM P.L. NO. DERBIGNY ****/ | 2019-05-16 | EXCAVATED 4 X 4 LIMESTONE GUTTER BOTTOM FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900722502 | 2019-05-25 | LEAD | 5808 | HAMLIN | ALABO | WILK | EXAMINE JOB AT ABOVE LOCATION FOUND FROM IN STREET REFER TO ZONE 4 TO MAKE REPAIR IN STREET /** 1) MN: A174932 SN: 0141281, *TAP: SIZE: B LOC: 87 FEET FROM P LINE AT ALABO, *MB: CODE: AEK4 LOC: RES ON HAMLIN 87FT LPL ALABO 8' OUTSIDE 2' INSIDE ****/ | 2019-05-29 | REMOVE WATER FROM FLOODED AREA EXCAVATED 3 X 3 MUD PLOT AROUND METER MADE REPAIR ON OUTLET SERVICE LINE BACKFILLED AND CLEANED THE AREA. (REFERRED TO BILLING VIA EMAIL TO N. HOLIDAY(PET) (JOB COMPLETE)
201900722801 | 2019-05-08 | LEAD | 2138 | ANNETTE | N MIRO | WMTLK | WATER METER LEAK. LEAK UNDERNEATH SIDEWALK. ECHOLOGICS REPORTED AND MARKED LEAK ON 12/26/2018. /** 1) MN: 000000 SN: 0067405, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT ANNETTE, *MB: CODE: CEH LOC: ON NO. MIRO, 54' FROM P.L. ANNETTE ****/ | 2019-05-16 | EXAMINED JOB AT ABOVE LOCATION FOUND JOB WAS COMPLETE AT AN EARLIER
201900724301 | 2019-05-08 | LEAD | 847 | TAFT PL | DUMAINE | WILK | ML- METER LEAK METER# A312379 ACCT# 143807-716090 INLET SERVICE LEAK IN THE MUD PLOT ***HOUSE UNDER CONSTRUCTION*** /** 1) MN: A312379 SN: 0075130, *TAP: SIZE: B LOC: 332 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: BE LOC: ON TAFT PL., 332' FROM P.L. ORLEANS AVE. ****/ | 2019-05-15 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900727401 | 2019-05-09 | LEAD | 2509 | CAFFIN AV | LAW | WILK | INLET SERVICE LEAK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-08 | EXCAVATED 4 X 6 MUD PLOT FOUND LEAK ON 3/4 INCH ABANDON INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900727801 | 2019-05-09 | LEAD | 2036 | FELICIANA | N GALVEZ | WILK | INLET SERVICE LEAK /** 1) MN: A260962 SN: 0000000, *TAP: SIZE: B LOC: 287 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CD LOC: ON FELICIANA 287 FT FROM PL N JOHNSON ****/ | 2019-05-07 | EXCAVATED 4 X 4 MUD PLOT IN GUTTER BOTTOM RAISE 5/8 INCH METER BOX UP TO GRADE BACKFILLED JOB WITH RIVERSAND
201900729301 | 2019-05-09 | LEAD | 1425 | ARTS | N ROBERTSON | WILK | WM-LEAK IN BETWEEN STREET AND SIDEWALK EXAMINE INLET SERVICE FOR A LEAK BETWEEN STREET & SIDEWALK /** 1) MN: 000000 SN: 0062192, *TAP: SIZE: B LOC: 202 FEET FROM P LINE AT VILLERE N, *MB: CODE: CDLM LOC: BET N VILLERE & N ROBERTSON 202FT FROM N VILLERE ****/ | 2019-05-29 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900729501 | 2019-05-09 | LEAD | 832 | SPAIN |  | WOLK | ML METERLEAK MTR#A423900 LOC/CUST#125712-480912 CONS REG ON METER. 05/09/19 PER 12875256 INSP L UDUEBOR STATES SERVICE IS LEAKING BEHIND THE WHEEL. PLEASE REPAIR METER A423900 LOC 125712 (KSW) /** 1) MN: A263716 SN: 0048173, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CD LOC: ON SPAIN 49' FROM URPL BURGUNDY ****/ | 2019-05-21 | MADE 4 X 4 SIDEWALK CUT AND MADE REPAIR ON 3/4 INCH OUTLET SERVICE BEHIND METER BOX REPLACED HANDWHEEL NO CONSTANT ON METER BACKFILLED AREA. JOB COMPLETE
201900730001 | 2019-05-09 | LEAD | 3318 | CASTIGLIONE |  | WILK | LOCATION ID-168160 MTR-A295842 MTR LEAK AT CURB COCK /** 1) MN: A295842 SN: 0109881, *TAP: SIZE: A LOC: 229 FEET FROM P LINE AT ROMULUS, *MB: CODE: ADM3 LOC: 229FT PL ROMULUS 7' OUTSIDE ****/ | 2019-05-28 | EXCAVATED IN 3 X 3 SIDEWALK CUT AND REPAIRED 5/8 INCH CURB COCK BACKFILLED AND CLEANED THE ARE
201900730601 | 2019-05-09 | LEAD | 2044 | TREASURE | PAUGER | WILK | ML-METER LEAK ACCT#157761-732350 METER#A417111 INLET SERVICE LEAK IN BOX, CARS ROLLING OVER METER /** 1) MN: A125816 SN: 0095122, *TAP: SIZE: A LOC: 69 FEET FROM P LINE AT PAUGER, *MB: CODE: AD LOC: ON TREASURE 69FT FROM PL PAUGER 9FT OUTSIDE PL 3FT ****/ | 2019-05-21 | MADE A 3X2 CUT IN DRIVEWAY. EXCAVATED DOWN ON INLET SERVICE. FOUND LEAD AND CURB COCK WAS LEAKING ALSO HANDWHEEL, WAS HARD OPERATE. MADE REPAIRS BY REPLACING COCK WAHSERS HANDWHEEL. BACKFILLED.
201900733101 | 2019-05-10 | LEAD | 1909 | CONGRESS | N PRIEUR | WILK | LOCATION# 149695-496037. METER#A386477. THE AREA AROUND THE METER IS FLOODED. POSSIBLE LEAK AT METER /** 1) MN: A269525 SN: 0084388, *TAP: SIZE: B LOC: 77 FEET FROM P LINE AT PRIEUR N, *MB: CODE: CD LOC: ON CONGRESS ST 76.5' FROM PL N PRIEUR ****/ | 2019-05-23 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900733701 | 2019-05-10 | LEAD | 816 | ST PHILIP |  | WMTLK | LOCATIONID#107802-529120 METER#B028861 LEAK INSIDE METERBOX /** 1) MN: B028861 SN: 0056314, *TAP: SIZE: A LOC: 127 FEET FROM P LINE AT BOURBON, *MB: CODE: AE4 LOC: APTS 127' P.L. BOURBON ****/ | 2019-05-29 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 3/4 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSNAD AND COLDMILL
201900733801 | 2019-05-10 | LEAD | 1848 | BURGUNDY | PAUGER | WOLK | ML- ACCT#197147-485653 MTR# A330675 CONST. REG FOUND ON METER /** 1) MN: A330675 SN: 0011007, *TAP: SIZE: B LOC: 148 FEET FROM P LINE AT PAUGER, *MB: CODE: CFL LOC: ON BURGUNDY 146FT PL PAUGER 2' OUTSIDE 8' INSIDE ****/ | 2019-05-16 | EXAMINED JOB AT ABOVE LOCATION FOUND LEAK ON OUTLET SERVICE NO CONSTANT REG ON 5/8 INCH WATER METER
201900733901 | 2019-05-10 | LEAD | 1015 | DAUPHINE |  | WILK | LOCATIONID#106911-529442 METER#A424800 LEAK INSIDE METERBOX /** 1) MN: A307072 SN: 0029291, *TAP: SIZE: A LOC: 115 FEET FROM P LINE AT ST PHILIP, *MB: CODE: CE LOC: 2ND METER AT 1017 115' FROM LSPL ST PHILIP ****/ | 2019-05-17 | EZXCAVATED 2 X 4 BRICK SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL LEFT ONE SAFETY CONE ON JOB SITE
201900734001 | 2019-05-10 | LEAD | 919 | GOV NICHOLLS |  | WILK | LOCATIONID#105182-529377 METER#A243921 LEAK INSIDE METERBOX /** 1) MN: A243921 SN: 0028285, *TAP: SIZE: A LOC: 1384 FEET FROM P LINE AT DAUPHINE, *MB: CODE: BE LOC: ON GOV. NICHOLLS, 138.4' FROM P.L. DAUPHINE ****/ | 2019-05-17 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET SERVICE BACKFILLED JOB WITH RIVERSAND AND COLDMILL LEFT ONE SAFETY CONE ON JOB SITE
201900734701 | 2019-05-10 | LEAD | 3125 | N ROBERTSON | CLOUET | WILK | INLET WATER LEAK /** 1) MN: A299788 SN: 0068693, *TAP: SIZE: A LOC: 217 FEET FROM P LINE AT CLOUET, *MB: CODE: CD1 LOC: 217' P.L. CLOUET ****/ | 2019-05-09 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900737801 | 2019-05-10 | LEAD | 2632 | LAPEYROUSE | PAUL MORPHY | WMLK | WM- LEAK ON SIDEWALK EXAMINE LEAK ON WATER MAIN @ CURB /** 1) MN: A249297 SN: 0038114, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: BFHK LOC: SIDE BY GARAGE ON PAUL MORPHY 110' P.L.LAPEYROUSE ****/ | 2019-05-24 | EXCAVATED IN UD PLOT AND CURB COCK BLEEDER WAS BAD REPLACED 5/8 INCH CURB COCK AND 5/8 INCH BOTTOM BACKFILLED AREA. JOB COMPLETE
201900743401 | 2019-05-12 | LEAD | 1808 | ELYSIAN FIELDS AV | N ROMAN | WILK | MI LEAK ON SIDEWALK INLET IN THE MUDPLOT /** 1) MN: SN: 0060298, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT ELYSIAN FIELDS AVE, *MB: CODE: __ LOC: 76 FT FROM USPL OF ELYSIAN FIELDS AVE. ** 2) MN: A256101 SN: 0060298, *TAP: SIZE: B LOC: 68 FEET FROM P LINE AT NO. ROMAN, *MB: CODE: __ LOC: ON ELYSIAN FIELDS AVE., 70' FROM P.L. NO. ROMAN, ****/ | 2019-05-17 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON ABANDON 5/8 INCH INLET SERVICE BACKFILLED JOB WITH RIVERSAND
201900744301 | 2019-05-13 | LEAD | 2446 | DAUPHINE | SPAIN | WOLK | LOCATION#116243-480772. METER#A372151. THE METER HAS A CON REG. NO S&W TO PERFORM TEST. /** 1) MN: A283042 SN: 0021338, *TAP: SIZE: A LOC: 39 FEET FROM P LINE AT SPAIN, *MB: CODE: BFKN LOC: ON DAUPHINE 38.5FT FROM PL OF SPAIN ****/ | 2019-06-03 | EXAMINED JOB AT ABOVE LOCATION FOUND NO CON REG ON METER
201900744402 | 2019-06-05 | LEAD | 4224 | PRENTISS AV |  | WILK | BAD CURB COCK AND REROUTED METER BOX OUT OF TREE ROOTS /** 1) MN: B030407 SN: 0128053, *TAP: SIZE: B LOC: 295 FEET FROM P LINE AT PRESS DR, *MB: CODE: CDLM LOC: ON PRENTISS AVE., 295' FROM P.L. PRESS DR., 7' ****/ | 2019-06-06 | EXCAVATED DOWN ON TREE ROOTS FOUN LEAK ON INLET MADE REPAIRS BY RELACING METER BOX WITH A METER BOX COMPLETE, 10FT OF 3/4 PLASTIC. LEAD NEEDS TO BE REMOVED FROM WATER MAIN TOWARD METER BOX. METER WAS MARKED.
201900745001 | 2019-05-13 | LEAD | 2236 | D"ABADIE |  | WMTLK | LOCATION ID-116271 MTR-A414603 MTR LEAK/MTR BOX FILLING UP WHEN PUMP OUT /** 1) MN: SN: 0060216, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT D'ABADIE, *MB: CODE: FHM LOC: ON TONTI 64FT FROM URPL DABADIE ****/ | 2019-05-20 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900745501 | 2019-05-13 | LEAD/PLASTIC | 3021 | JENA | S CLAIBORNE AV | WILK | WM-LEAK IN STREET **********L THOMPSON 08:39********** INLET SERVICE LEAK IN A CONCRETE STREET FLOODING STREET & GUTTER BOTTOM WITH SOME WATER GETTING OFF IN THE DCB 05/15/19 CUST NOW HAS POOR PRESSURE AND CAN'T LIVE AT THE HOUSE DUE TO LEAK (KSW) **********M ROBINSON 08:53********** 05/16/19 PER INSP L GOMEZ GIVE OUT AGAIN PER CUSTOMER HAS POOR PRESSURE ***S/R #12875494 05/13/19*** /** 1) MN: A124028 SN: 0063766, *TAP: SIZE: A LOC: 103 FEET FROM P LINE AT DERBIGNY S, *MB: CODE: BDL1 LOC: ON JENA,102' FROM L.R.P.L. SO. DERBIGNY ****/ | 2019-05-16 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 3/4 LEAD LEAKING .REPLACED 7FT. OF 3/4 TUBING TIED INTO LEAD.(SOC7FT. X 7 FT. CONCRETE) OLD METER INFO: A124028 FACT: 17985556 MAKE: ROCKWELL READ: 2783
201900746601 | 2019-05-13 | LEAD | 2814-16 | CONTI | N WHITE | WILK | MI-LEAK IN THE STREET INLET SERVICE LEAK CARS PARKING ON METER /** AT 2814: 1) MN: A322922 SN: 0057794, *TAP: SIZE: B LOC: 110 FEET FROM P LINE AT NO. WHITE, *MB: CODE: CDLM LOC: ON CONTI, 110' FROM P.L. NO. WHITE, 8' OUTSIDE ****/ | 2019-05-20 | REPLACE BOTH INLET AND OUTLET SERVICE WAHERS AT ABOVE LOCATION
201900748901 | 2019-05-13 | LEAD | 935-37 | JOSEPH | CHESTNUT | WILK | **********PICK UP********** INLET SERVICE LEAK BEHIND CURB COCK METER SITS ON CHESTNUT /** AT 935: 1) MN: A279545 SN: 0082996, *TAP: SIZE: B LOC: 34 FEET FROM P LINE AT JOSEPH, *MB: CODE: OOO LOC: MTR ON CHESTNUT 34FT FRM PL JOSEPH 3FT INSD CURB ** AT 937: 2) MN: C013486 SN: 0082996, *TAP: SIZE: C LOC: 35 FEET FROM P LINE AT JOSEPH, *MB: CODE: ADHL LOC: ON CHESTNUT 34.6FT FROM JOSEPH ****/ DOTTIE READY 5-30-19 EXP 6-19-19 | 2019-05-27 | EXCAVTED IN MUDPLOT OVER 5/8 METER BOX FOUND 5/8 STOP COCK AND TWO WASHERS BACKFILLED . JOB COMPLETE
201900749301 | 2019-05-13 | LEAD | 1425 | ARTS | N ROBERTSON | WILK | INLET SERVICE LEAK /** 1) MN: 000000 SN: 0062192, *TAP: SIZE: B LOC: 202 FEET FROM P LINE AT VILLERE N, *MB: CODE: CDLM LOC: BET N VILLERE & N ROBERTSON 202FT FROM N VILLERE ****/ | 2019-06-28 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900749401 | 2019-05-13 | LEAD | 1425 | ARTS | N ROBERTSON | WILK | INLET SERVICE LEAK /** 1) MN: 000000 SN: 0062192, *TAP: SIZE: B LOC: 202 FEET FROM P LINE AT VILLERE N, *MB: CODE: CDLM LOC: BET N VILLERE & N ROBERTSON 202FT FROM N VILLERE ****/ | 2019-05-09 | EXCAVATED IN GUTTER BOTTOM + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESED UP AREA
201900750301 | 2019-05-13 | LEAD | 2118 | MUSIC |  | WILK | ML- METER LEAK METER# A418589 ACCT# 306412-500555 INLET SERVICE LEAK BAD CURBCOCK /** 1) MN: A310712 SN: 0054603, *TAP: SIZE: A LOC: 16 FEET FROM P LINE AT MIRO, *MB: CODE: CD LOC: ON MUSIC 16FT FROM MIRO 7FT OUTSIDE 3FT INSIDE ****/ | 2019-05-19 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900751901 | 2019-05-13 | LEAD | 2824 | ST ANN | N DUPRE | WMTLK | MI- LEAK BETWEEN SIDEWALK AND STREET EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: A325759 SN: 0053984, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT DUPRE N, *MB: CODE: ADL LOC: ON ST ANN 82.3' FROM URPL N DUPRE ****/ | 2019-05-20 | REPLACE BOTH INLET AND OUTLET SERVICE WASHERS AT ABOVE LOCATION
201900752401 | 2019-05-14 | LEAD | 1615 | N TONTI | LAPEYROUSE | WOLK | ML-METER LEAK ACCT#142091-488855 METER#A313681 OULTLET SERVICE LEAK BEHIND HAND WHEEL IN MUDPLOT CON REG /** 1) MN: A313681 SN: 0073149, *TAP: SIZE: B LOC: 87 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: AD LOC: METER ON N TONTI,87 FT FROM PL LAPEYROUSE ****/ | 2019-05-20 | EXCAVATED 4 X 4 MUD PLOT LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIR ON OUTLET BACKFILLED JOB WITH RIVERSAND
201900756201 | 2019-05-14 | LEAD | 2018 | MAZANT | N JOHNSON | WILK | ML: METER LEAK METER # A270370 INLET SERVICE LEAK BAD CURB COCK IN MUDPLOT ACCT# 12875379-433033 /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-07-03 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA
201900757901 | 2019-05-15 | LEAD | 1115 | GORDON | ST CLAUDE AV | WMTLK | LOCATION#184943-422605. METER#A347271. THE METER HAS A LEAK AT THE INLET AND OUTLET. /** 1) MN: A231497 SN: 0138568, *TAP: SIZE: B LOC: 160 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: AD LOC: ON GORDON 146FT FROM PL ST CLAUDE ****/ | 2019-05-24 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH SERVICE MADE REPAIR ON INLET SERVICE BACKFILLED JOB WITH RIVERSAND
201900758401 | 2019-05-15 | LEAD | 1855 | ROSIERE | CASTIGLIONE | WOLK | ML- METER LEAK ACCT# 154151-482493 MTR# A428409 INSPECTOR FOUND CONS. REG. ON METER /** 1) MN: A285366 SN: 0090255, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT CASTIGLIONE, *MB: CODE: CD LOC: ON ROSIERE,132' FROM P.L. CASTIGLIONE,8.5' OUTSIDE ****/ | 2019-05-28 | EXCAVATED IN MUD PLOT FROM METER BOX TO PROPERTY FOUND NO LEAK
201900758501 | 2019-05-15 | LEAD | 1441 | BARTHOLOMEW | N ROBERTSON | WILK | WM-LEAK IN THE STREET FLOODING AREA INLET SERVICE LEAK @ CURB GETTING OFF IN DCB, AREA NOT FLOODED /** 1) MN: A339247 SN: 0073129, *TAP: SIZE: B LOC: 121 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: BDK1 LOC: ON BARTHOLOMEW 40' FROM PL N ROBERTSON 7' OUTSIDE ****/ | 2019-05-25 | EXCAVATED IN ASPHALT STREET + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE COMPACTED BACKFILL + DRESSED UP AREA
201900759001 | 2019-05-15 | LEAD | 1838 | INDEPENDENCE |  | WOLK | LOCATION: 307487 INSP UDUEBOR STATES OUTLET SERVICE WHEEL NEED REPAIRS AND OUTLET TIE IN. ALSO, INLET SERVICE NEED REPAIRS. PLEASE MAKE REPAIRS AND SET A 5/8 METER. ********* HOUSE UNDER RENOVATIONS AND VACANT ******** REPLACE MISSING HANDWHEEL, RASIE TO GRADE AND SET METER, HOUSE UNDER RENOVATION /** 1) MN: A251093 SN: 0094496, *TAP: SIZE: A LOC: 267 FEET FROM P LINE AT ROMAN N, *MB: CODE: ADK LOC: BY POST 267' P.L. N ROMAN 7' OUTSIDE P/L 3' INSIDE ****/ | 2019-05-24 | EXCAVATED IN MUD PLOT THROUGH HEAVY TREE ROOT + IN CONCRETE SIDEWALK REROUTED METER BOX FROM TREE ROOTS REPLACED WATER SERVICE FROM CURB TO PROPERTY + SET 5/8 INCH WATER METER BACKFILLED DRESSED UP AREA
201900759101 | 2019-05-15 | LEAD | 2208 | ALABO |  | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A309488 SN: 0129975, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT MIRO N, *MB: CODE: CDN1 LOC: RES ON ALABO 82' PL N MIRO OPP 2ND DOOR 7' OUTSIDE ****/ | 2019-05-29 | EXCAVATED 3 X 3 MUD PLOT MADE REPAIR ON INLET SERVICE TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900759201 | 2019-05-15 | LEAD | 1421 | N JOHNSON |  | WILK | LOCATION: 135396 MTR# C 035795 INSP UDUEBOR STATES INLET SERVICE NEED REPAIRS, BAD BLEEDER VALVE. PLEASE REPAIR BAD BLEEDER VALVE IN BOX /** 1) MN: C023228 SN: 0066032, *TAP: SIZE: C LOC: 179 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: BDN LOC: ON N JOHNSON ST 179' FROM PL ESPLANADE AVE ****/ | 2019-05-29 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 1 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900759501 | 2019-05-15 | LEAD | 1012 | GOV NICHOLLS |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 106490-529430 METER NUMBER - A158606 BAD BLEEDER VALVE IN BOX /** 1) MN: A158606 SN: 0001929, *TAP: SIZE: A LOC: 125 FEET FROM P LINE AT BURGUNDY, *MB: CODE: BFKO LOC: ****/ | 2019-05-23 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION. JOB COMPLETE
201900759801 | 2019-05-15 | LEAD | 1942 | ALABO |  | WOLK | ML METERLEAK MTR#A400639 LOC/CUST#173901-422131 CONS REG ON METER. /** 1) MN: A318570 SN: 0129720, *TAP: SIZE: B LOC: 37 FEET FROM P LINE AT JOHNSON N, *MB: CODE: ADKO LOC: RES ON ALABO 33FT PL N JOHNSON 6' OUTSIDE ****/ | 2019-05-24 | EXAMINED JOB AT ABOVE LOCATION FOUND NO CONS REG ON METER
201900760401 | 2019-05-15 | LEAD | 1417 | GOV NICHOLLS |  | WILK | ML METER LEAK METER # E008474 LOCATION #222738-526182 INLET SERVICE LEAK IN BOX, FOUND OFF LEFT OFF /** 1) MN: A127963 SN: 0005958, *TAP: SIZE: CC LOC: 172 FEET FROM P LINE AT MARAIS, *MB: CODE: BDLM LOC: XXX IN BOARD FENCE GUTTER EDGE 127' P.L. N VILLERE ** 2) MN: A326893 SN: 0005958, *TAP: SIZE: CC LOC: 119 FEET FROM P LINE AT MARAIS, *MB: CODE: BDLM LOC: ON GOV. NICHOLLS, 120' FROM P.L. MARAIS, 10' OUT- ****/ | 2019-05-29 | EXAMINE JOB AT ABOVE LOCATION FOUND NO LEAK LEFT OFF IN BOX
201900762101 | 2019-05-15 | LEAD | 3705 | N GALVEZ |  | WMTLK | ML- METER LEAK AT METER A 340315 ACCT# 150874 - 432101 EXAMINE INLET AND OUTLET SERVICE FOR LEAK AREA SATURATED /** 1) MN: A340315 SN: 0083761, *TAP: SIZE: A LOC: 52 FEET FROM P LINE AT INDEPENDENCE, *MB: CODE: CDL LOC: 74'FROM PL INDEPENDENCE 9'OUTSIDE PL ****/ | 2019-05-24 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900762201 | 2019-05-15 | LEAD | 3219 | BAUDIN |  | WMTLK | ML - METER LEAK ACCOUNT NUMBER - 108127 - 548151 METER NUMBER - B040854 EXAMINE INLET AND OUTLET SERVICE FOR LEAK IIN BOX, METER UNDER WATER /** 1) MN: B031898 SN: 0049916, *TAP: SIZE: B LOC: 175 FEET FROM P LINE AT LOPEZ S, *MB: CODE: CELM LOC: ON BAUDIN 175' FROM LSPL S LOPEZ ****/ | 2019-06-03 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900764201 | 2019-05-16 | LEAD | 2306 | ST BERNARD AV |  | WOLK | ML METERLEAK MTR#A359571 LOC/CUST#120447-488634 CONS REG ON METER. /** 1) MN: A334748 SN: 0049182, *TAP: SIZE: A LOC: 203 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BFN LOC: ON ST. BERNARD AVE.,203' FROM U.R.P.L. NO. ****/ | 2019-05-29 | EXAMINE JOB AT ABOVE LOCATION FOUND NO LEAK ON INLET OR OUTLET JOB COMPLETE
201900764501 | 2019-05-16 | LEAD | 1626 | CONGRESS | N CLAIBORNE AV | WMTBG | ************************PICKUP*********************** METER BOX BELOW GRADE CAUSING METER BOX COVER TO NOT FIT PROPERLY /** 1) MN: A218669 SN: 0084224, *TAP: SIZE: B LOC: 215 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: CDN5 LOC: 215'FROM N CLAIBORNE AV CURB ****/ | 2019-05-24 | EXCAVATED IN LIMESTONE GUTTER BOTTOM + REPLACED BROKEN 5/8 INCH METER BOX CASING BACKFILLED + DRESSED UP AREA
201900766401 | 2019-05-16 | LEAD | 2730 | BANKS | S BROAD | WILK | MI- LEAK ON THE SIDEWALK ( THERE ARE 2 NO PARKING SIGNS AROUND LEAK) INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A337402 SN: 0062181, *TAP: SIZE: A LOC: 232 FEET FROM P LINE AT BROAD S, *MB: CODE: AFK2 LOC: BY FENCE NEAR DRIVE 231FT FR USPL BROAD ****/ | 2019-06-04 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900767301 | 2019-05-16 | LEAD | 1306 | OCTAVIA | PITT | WILK | WM - LEAK ON THE SIDEWALK - ON THE PITT SIDE OF THE PROPERTY INLET SERVICE LEAK BEHIND CURB COCK /** 1) MN: A285275 SN: 0039059, *TAP: SIZE: B LOC: 12 FEET FROM P LINE AT , *MB: CODE: BEH3 LOC: ON PITT, 12' FROM LSPL OCTAVIA ** 2) MN: C026747 SN: 0000000, *TAP: SIZE: C LOC: 15 FEET FROM P LINE AT PITT, *MB: CODE: CD LOC: ON OCTAVIA 15FT FROM PITTS 3FT OUTSIDE ****/ DOTTIE READY 5-30-19 EXP 6-19-19 | 2019-05-27 | EXCAVTED IN THE 4 X 6 SIDEWALK OVER 5/8 METER BOX AND FOUND METER BOX STOP COCK.LEAKING .REPLACE 5/8 STOP COCK AND TWO 5/8 WASHERS BACKFILL. JOB COMPLETE
201900770003 | 2019-06-05 | LEAD | 1918 | CONTI |  | WILK | EXCAVATED 4 X 4 MUD PLOT FOUND NO WATER ON INLET REFER TO ZONE 4 FOR REPAIR TO BE MADE IN STREET AND ALSO SET A 5/8 INCH METER /** 1) MN: A194225 SN: 0064195, *TAP: SIZE: A LOC: 144 FEET FROM P LINE AT ROMAN N, *MB: CODE: ADK6 LOC: ON CONTI,142' FROM U.S.P.L. NO. ROMAN ****/ | 2019-06-07 | EXCAVATED BY HAND IN MUD PLOT FIND A 5/8 INCH STOP COCK OFF REPLACED IT WITH NEW ONE SET A NEW METER NO METER WAS IN BOX WE ALSO SET A WHOLE NEW METER BOX COMPLETE BACKFILLED AND CLEANED UP AN RAISE TO GRADE
201900776301 | 2019-05-18 | LEAD | 1731 | DUMAINE | N DERBIGNY | WILK | WM-LEAK ON THE SIDEWALK INLET LEAK IN EMPTY LOT /** 1) MN: A315223 SN: 0023579, *TAP: SIZE: A LOC: 60 FEET FROM P LINE AT DUMAINE, *MB: CODE: FHL LOC: ON NO. DERBIGNY,61' FROM L.R.P.L. DUMAINE ****/ | 2019-05-24 | REMOVED CONCRETE ALREADY BROKEN UP AND MADE REPAIR ON 3/4 INCH INLET ABANDON SERVICE BACKFILLED AREA JOB COMPLETE
201900776401 | 2019-05-18 | LEAD | 2527 | ST BERNARD AV |  | WILK | LOCATIONID#178027-489972 METER#D008144 BLEEDER LEAK /** 1) MN: D005198 SN: 0067043, *TAP: SIZE: D LOC: 183 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: E2 LOC: ON ST BERNARD AVE LEFT SIDE IN SIDEWALK 179' P/L ** 2) MN: D004061 SN: 0163219, *TAP: SIZE: D LOC: 137 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: OOO LOC: ON ST BERNARD AVE 142' FROM PL N DORGENOIS 13' THERE ARE 4 MORE NOT LISTED. ****/ | 2019-06-04 | ARRIVED AT ABOVE LOCATION FOUND LEAK ON 1 INCH OUTLET SERVICE MADE REPAIR ON OUTLET INSIDE OF MANHOLE
201900776501 | 2019-05-18 | LEAD | 1668 | ABUNDANCE |  | WMTLK | LOCATIONID#144677-492396 METER#A395593 METERBOX OVERFLOWING /** 1) MN: A330241 SN: 0076139, *TAP: SIZE: B LOC: 181 FEET FROM P LINE AT BRUXELLES, *MB: CODE: CDL1 LOC: 183' P.L. BRUSELLES ****/ | 2019-05-28 | EXCAVATED IN MUD PLOT MADE REPAIR ON CURB COCK BACKFILLED AND CLEANED THE AREA
201900776601 | 2019-05-18 | LEAD | 3012 | BRUXELLES |  | WMTLK | LOCATIONID#204383-492666 METER#A419783 METERBOX OVERFLOWING /** 1) MN: 000000 SN: 0065017, *TAP: SIZE: C LOC: 110 FEET FROM P LINE AT ABUNDANCE, *MB: CODE: OOO LOC: ON BRUXELLES 110FT FROM PL ABUNDANCE ** 2) MN: A333753 SN: 0065017, *TAP: SIZE: C LOC: 110 FEET FROM P LINE AT ABUNDANCE, *MB: CODE: OOOO LOC: ON BRUXELLES, 110' FROM P.L. ABUNDANCE, 7' OUTSIDE ****/ | 2019-05-28 | EXCAVATED IN SIDEWALK 3 X 3 CUT AND MADE REPAIR ON 5/8 INCH HANDWHEEL
201900776701 | 2019-05-18 | LEAD | 1768 | N DUPRE |  | WMTLK | LOCATIONID#140829-491902 METER#A254712 LEAK INSIDE METERBOX /** 1) MN: A254712 SN: 0071665, *TAP: SIZE: A LOC: 179 FEET FROM P LINE AT AUBRY, *MB: CODE: CDLN LOC: ON N DUPRE 179' FROM PL OF AUBRY ****/ | 2019-05-28 | EXCAVATED IN MUDE PLOT MADE REPAIR ON CURB COCK BACKFILLED AND CLEANED THE AREA
201900776801 | 2019-05-18 | LEAD | 1763 | PAUL MORPHY |  | WMTLK | LOCATIONID#151534-491977 METER#A357321 LEAK INSIDE METERBOX /** 1) MN: A217599 SN: 0058749, *TAP: SIZE: B LOC: 161 FEET FROM P LINE AT AUBRY, *MB: CODE: AD LOC: 161FT FROM PL AUBRY METER ON PAUL MORPHY ****/ | 2019-05-24 | EXCAVATED IN MUD PLOT AD MADE REPAIR ON 3/4 INCH INLET SERVICE BEHIND METER BOX BACKFILLED AREA
201900777201 | 2019-05-18 | LEAD | 1612 | N GALVEZ |  | WMTLK | LOCATIONID#131197-570127 METER#A422656 LEAK INSIDE METERBOX /** 1) MN: A247018 SN: 0033884, *TAP: SIZE: A LOC: 102 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: BF LOC: ON NO. GALVEZ,101' FROM L.P.L. LAPEYROUSE ****/ | 2019-05-23 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH METER BOX BOTTOM ALSO MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA JOB COMPLETE
201900777501 | 2019-05-18 | LEAD | 1713 | ST CLAUDE AV |  | WMTLK | LOCATIONID#123524-485946 METER#A395501 LEAK INSIDE METERBOX /** 1) MN: A338902 SN: 0060235, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT ANNETTE, *MB: CODE: AD6 LOC: ON ST CLAUDE AVE 118' FROM LSPL ANNETTE ****/ | 2019-05-30 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACE METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900777601 | 2019-05-18 | LEAD | 1756 | N RAMPART |  | WMTLK | LOCATIONID#118922-485893 METER#A357218 LEAK INSIDE METERBOX /** 1) MN: A233825 SN: 0042430, *TAP: SIZE: A LOC: 50 FEET FROM P LINE AT ST ANTHONY, *MB: CODE: ADK5 LOC: ON N RAMPART 50' FROM URPL ST ANTHONY ST ****/ | 2019-05-30 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED 5/8 INCH METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900777701 | 2019-05-18 | LEAD | 1907 | N RAMPART |  | WMTLK | LOCATIONID#154052-703589 METER#A139376 LEAK INSIDE METERBOX /** 1) MN: A139376 SN: 0061578, *TAP: SIZE: B LOC: 48 FEET FROM P LINE AT PAUGER, *MB: CODE: CELM LOC: ON RAMPART 50' FROM PL PAUGER 8' OUTSIDE PL 2' INS ****/ | 2019-05-30 | REPLACE HANDWHEEL AND WASHERS TO STOP LEAK
201900777801 | 2019-05-18 | LEAD | 1808 | N RAMPART |  | WMTLK | LOCATIONID#106020-485770 METER#A281258 LEAK INSIDE METERBOX /** 1) MN: A281258 SN: 0049970, *TAP: SIZE: A LOC: 94 FEET FROM P LINE AT ST ANTHONY, *MB: CODE: AEK LOC: ON N RAMPART 94 FT FROM PL OF ST ANTHONY ****/ | 2019-05-24 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900778101 | 2019-05-18 | LEAD | 2057 | N PRIEUR |  | WOLK | LOCATION ID-125025 MTR-A417169 UNDERGROUND LEAK BETWEEN MTR AND STOP & WASTE/CONS REG ON MTR /** 1) MN: A263022 SN: 0054686, *TAP: SIZE: A LOC: 97 FEET FROM P LINE AT TOURO, *MB: CODE: ADKO LOC: OPP GATE 98' P.L. TOURO ****/ | 2019-05-24 | EXAMINE JOB AT ABOVE LOCATION FOUND NO CONSTANT REG ON METER
201900778901 | 2019-05-19 | LEAD | 1424 | N ROMAN | ESPLANADE AV | WOLK | WM-LEAK IN SIDEWALK CHANGED FROM 1428 N ROMAN *******CUSTOMER OUT OF WATER******* D RANDOLPH @ 8:56AM OUTLET SERVICE, HOLE IS OPEN /** 1) MN: B030187 SN: 0057296, *TAP: SIZE: B LOC: 147 FEET FROM P LINE AT KERLEREC, *MB: CODE: CEK LOC: ON N ROMAN 147FT FROM URPL OF KERLEREC ****/ | 2019-05-19 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 3/4 INCH OUTLET SERVICE MADE REPAIR ON OUTLET BACKFILLED JOB WITH RIVERSAND
201900779601 | 2019-05-20 | LEAD | 1729 | AGRICULTURE |  | WMTLK | LOCATIONID#145395-492429 METER#A413015 METERBOX OVERFLOWING /** 1) MN: A268684 SN: 0076870, *TAP: SIZE: B LOC: 261 FEET FROM P LINE AT REPUBLIC, *MB: CODE: CDL LOC: METER ON AGRICULTURE 263.8 FT FROM PL REPUBLIC ****/ | 2019-05-30 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900784101 | 2019-05-20 | LEAD | 3037 | BANKS |  | WOLK | MI-- LEAK INSIDE METER BOX CHECK OUTLET SERVICE FOR A LEAK IN THE MUD PLOT @ PROPERTY LINE. METER SITS ON SIDE OF THE HOUSE /** 1) MN: A272584 SN: 0011562, *TAP: SIZE: A LOC: 44 FEET FROM P LINE AT BANKS, *MB: CODE: BFHL LOC: ON SALCEDO 44FT FOMR BANKS ****/ | 2019-05-30 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON ABANDON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900784301 | 2019-05-20 | LEAD | 1736 | TRICOU | N DERBIGNY | WMTBG | MI-RAISE TO GRADE METER#A410748 /** 1) MN: A330716 SN: 0125991, *TAP: SIZE: A LOC: 279 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BDM4 LOC: RES ON TRICOU 279FT FROM PL DERBIGNY N 7' OUTSIDE ****/ | 2019-06-04 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH METER BOX CASING BRING IT UP TO GRADE BACKFILLED + DRESSED UP AREA
201900785301 | 2019-05-20 | LEAD | 1011 | N ROCHEBLAVE | ST PHILIP | WILK | WM-LEAK BETWEEN SIDEWALK & STREET INLET SERVICE LEAK IN SIDEWALK /** 1) MN: A133746 SN: 0016977, *TAP: SIZE: A LOC: 116 FEET FROM P LINE AT ST PHILIP, *MB: CODE: BFL LOC: 116' P.L. ST PHILIP ****/ | 2019-05-30 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900788101 | 2019-05-21 | LEAD | 1630 | ST ROCH AV | N CLAIBORNE AV | WOLK | ACCT# 140106-482440 MTR# A362660 INSPECTOR FOUND CONSTANT REGISTRATION ON METER /** 1) MN: 000000 SN: 0070863, *TAP: SIZE: A LOC: 251 FEET FROM P LINE AT CLAIBORNE AV N, *MB: CODE: BDN2 LOC: 251' P.L. N CLAIBORNE AV ****/ | 2019-05-30 | EXAMINED JOB + FOUND JOB ALREADY REPAIRED
201900788401 | 2019-05-21 | LEAD | 1734 | CONGRESS |  | WILK | ML: METER LEAK ACCT#305494-723667 MTR# A416275 INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A312678 SN: 0084453, *TAP: SIZE: A LOC: 249 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BDK LOC: ON CONGRESS, 249' FROM P.L. NO. DERBIGNY ****/ | 2019-05-31 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR ON OUTLET SERVICE LINE BACKFILL AND CLEANED THE AREA. JOB COMPLETE
201900789001 | 2019-05-21 | LEAD | 2526 | CONGRESS | LAW | WILK | WM: LEAK ON SIDEWALK INLET SERVICE LEAK INSIDE METER BOX. METER CASING SITS IN THE MUD PLOT /** 1) MN: A136424 SN: 0104924, *TAP: SIZE: A LOC: 95 FEET FROM P LINE AT LAW, *MB: CODE: BDK1 LOC: ON CONGRESS, 95' FROMP.L. LAW, 7' OUTSIDE P.L. ****/ | 2019-05-31 | EXCAVATED 3 X 3 MUD PLOT RAISED METER BOX UP GRADE AND REDUCED 1 INCH LINE TO 3/4 LINE BACKFILLED AND CLEANED THE AREA
201900789501 | 2019-05-21 | LEAD | 4722 | SHALIMAR DR | PRENTISS AV | WMTLK | WATER METER LEAK. LEAK IS VISIBLE. ECHOLOGICS REPORTED AND MARKED LEAK ON 5/20/2019. /** 1) MN: B027798 SN: 0124772, *TAP: SIZE: B LOC: 154 FEET FROM P LINE AT DREUX AVE, *MB: CODE: AD LOC: RES ON SHALIMAR 154FT PL DREUX AV 8' OUTSIDE 3' ****/ | 2019-05-22 | EXCAVATED IN MUDPLOT OVER BOTH METER BOXES FOUND LEAD LINE LEAKING ON 3/4 TEE ON INLET SERVICE MADE REPAIR ON INLET SERVICE. NEED BACK HOE TO CUT OUT IN STREET TO REPLACE LEAD LINE, BACKFILL MUDPLOT WITH SAND
201900792201 | 2019-05-22 | LEAD | 1721 | MONTEGUT | N ROMAN | WILK | INLET SERVICE LEAK /** 1) MN: SN: 0103079, *TAP: SIZE: B LOC: 168 FEET FROM P LINE AT N DERBIGNY, *MB: CODE: BGT LOC: ON MONTEGUT, 168' FROM P.L. NO. DERBIGNY, 7' OUT- ****/ | 2019-05-21 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA
201900792901 | 2019-05-22 | LEAD | 1008 | FRANKLIN AV | N RAMPART | WILK | ML-METER LEAK MTR # A401766 ACCT # 109007-536342 INLET SERVICE LEAK BAD BLEEDER VALVE INSIDE METER BOX FOUND MTR OFF LEFT MTR OFF /** 1) MN: A248704 SN: 0045138, *TAP: SIZE: B LOC: 78 FEET FROM P LINE AT RAMPART N, *MB: CODE: CELM LOC: ON LAFAYETTE AVE 243' FROM IRPL ST CLAUDE AVE ****/ | 2019-05-31 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE
201900793801 | 2019-05-22 | LEAD | 1862 | INDUSTRY |  | WILK | INSP L UDUEBOR STATES BLEEDER VALVE IS LEAKING BADLY. PLEASE REPAIR METER A433496 LOC 307660 INLET SERVICE LEAK IN THE MUD PLOT BAD BLEEDER VALVE /** 1) MN: A235095 SN: 0107754, *TAP: SIZE: B LOC: 163 FEET FROM P LINE AT NEW ORLEANS, *MB: CODE: DK2 LOC: ON INDUSTRY, 163' FROM P.L. NEW ORLEANS, 7' OUT- ****/ | 2019-05-31 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900794001 | 2019-05-22 | LEAD | 1139 | KERLEREC |  | WILK | INSP L UDUEBOR STATES INLET SERVICE LEAKING BECAUSE OF BAD CURB COCK. PLEASE REPAIR AND SET 5/8 METER. LOC 307668 INLET SERVICE LEAK INSIDE METER BOX, REPLACE 5/8 METER AFTER REPAIRS ARE MADE ALSO REMOVE LEAD /** 1) MN: A317193 SN: 0002391, *TAP: SIZE: B LOC: 67 FEET FROM P LINE AT ST CLAUDE, *MB: CODE: BEK1 LOC: ON KERLEREC 69' FROM PL OF ST CLAUDE AVE 4' OUTSID ****/ | 2019-05-23 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVIC E MADE REPAIR ON INLET SET A 5/8 INCH WATER METER AT ABOVE LOCATION BACKFILLED JOB WITH RIVERSAND COLDMILL
201900794101 | 2019-05-22 | LEAD | 1139 | KERLEREC |  | WILK | INSP L UDUEBOR STATES INLET SERVICE LEAKING BECAUSE OF BAD CURB COCK. PLEASE REPAIR AND SET 5/8 METER. LOC 307669 **********1ST AM********** INLET SERVICE LEAK BAD CURB COCK, ALL METER BOX CASING SITS IN CONCRETE IN SIDEWALK, ALSO SET 5/8 METER AFTER REPAIRS ARE MADE /** 1) MN: A317193 SN: 0002391, *TAP: SIZE: B LOC: 67 FEET FROM P LINE AT ST CLAUDE, *MB: CODE: BEK1 LOC: ON KERLEREC 69' FROM PL OF ST CLAUDE AVE 4' OUTSID ****/ | 2019-05-23 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET SET A 5/8 INCH WATER METER AT ABOVE LOCATION BACKFILLED JOB WITH RIVERSAND COLDMILL
201900795901 | 2019-05-22 | LEAD | 1803 | LAHARPE |  | WMRE | INSP L UDUEBOR STATES SERVICE IS BURIED. PLEASE RAISE TO GRADE AND SET 5/8 METER. LOC 307512 LOCATE, RAISE TO GRADE & SET 5/8 METER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-05-31 | EXCAVATED 4 X 4 MUD PLOT RAISE METER BOX UP TO GRADE ALSO SET A 5/8 INCH WATER METER AT ABOVE LOCATION BACKFILL JOB WITH RIVERSAND
201900798101 | 2019-05-22 | LEAD | 2340 | DELERY | N ROCHEBLAVE | WOLK | WATER OUTLET SERVICE LEAK. LEAK IS VISIBLE AND DRAINING INTO THE GUTTER.. LEAK IS AT THE CORNER OF DELERY AND N ROCHEBLAVE. /** 1) MN: A292615 SN: 0136112, *TAP: SIZE: C LOC: 13 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: CDN1 LOC: RES ON DELERY 13FT P/L N ROCHEBLAVE 6' OUTSIDE ****/ | 2019-05-31 | EXCAVATED 3 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE LINE BACKFILL AND CLEANEDTHE AREA
201900799001 | 2019-05-22 | LEAD | 634 | LESSEPS |  | WMTLK | ML: METER LEAK ACCT#223756-562205 MTR#E008533 EXAMINE INLET/OUTLET SERVICE FOR A LEAK IN MUDPLOT INSIDE MANHOLE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-06-05 | EXAMINED JOB AT ABOVE LOCATION FOUND LEAK ON 2 INCH OUTLET SERVICE LEAK INSIDE MANHOLE MADE REPAIR ON 2 INCH OUTLET SERVICE. JOB COMPLETE
201900799301 | 2019-05-22 | LEAD | 1977 | LAW |  | WILK | ML--METER LEAK LOC#163883 METER# A379096 INLET SERVICE LEAK IN MUDPLOT ALSO CHANGED 5/8 HANDWHEEL /** 1) MN: A296885 SN: 0099904, *TAP: SIZE: A LOC: 74 FEET FROM P LINE AT NEW ORLEANS, *MB: CODE: CDN1 LOC: ON LAW, 74' FROM P.L. NEW ORLEANS, 8' OUTSIDE P.L. ****/ | 2019-06-03 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900800201 | 2019-05-23 | LEAD | 112 | ROYAL | CANAL | WOLK | OUTLET SERVICE LEAK /** 1) MN: SN: 0005647, *TAP: SIZE: A LOC: 91 FEET FROM P LINE AT CANAL, *MB: CODE: BEN LOC: ON ROYAL ** 2) MN: B023187 SN: 0005647, *TAP: SIZE: B LOC: 91 FEET FROM P LINE AT CANAL, *MB: CODE: OOO LOC: MTR ON ROYAL 91FT FRM PL CANAL ****/ | 2019-05-22 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION REPLACE 1 INCH CHOKE WATER METER OLD METER INFO: C027662 FACT: 59814253 MAKE: SENSUS READ: 12563
201900807401 | 2019-05-24 | LEAD | 4607 | BABYLON | DREUX AV | WILK | WATER INLET SERVICE LEAK. LEAK IS UNDERNEATH ROADWAY IN FRONT OF FIRE HYDRANT. ECHOLOGICS REPORTED AND MARKED LEAK ON 5/22/2019. /** 1) MN: A277749 SN: 0115043, *TAP: SIZE: A LOC: 231 FEET FROM P LINE AT DREUX AVE, *MB: CODE: BDL LOC: ON BABYLON, 231' FROM P.L. DREUX AVE., 7' OUTSIDE ****/ | 2019-06-27 | EXAMINED JOB AND FOUND LEAK IN STREET. EXCAVATED IN ASPHALT TO EXPOSE LEAK. FOUND BUSTED LEAD LINE. STOPPPED LEAK WITH 3/4 TOP COCK AND PACK JOINT 5/8 RESTORED SERVICE TO CUSTOMER. LEAD NEEDS TO BE REOMVED ON OUTLET AND INLET
201900809001 | 2019-05-24 | LEAD | 5309 | DAUPHINE |  | WMTLK | LOCATIONID#173872-708862 METER#A237298 LEAK INSIDE METERBOX /** 1) MN: 000000 SN: 0056823, *TAP: SIZE: A LOC: 121 FEET FROM P LINE AT EGANIA, *MB: CODE: BEL1 LOC: ON DAUPHINE 120FT LRPL EGANIA 2' INSIDE CURB ****/ | 2019-06-05 | EXCAVATED 2 X 4 BRICK SIDEWALK FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIR ON OUTLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL JOB COMPLETE
201900809201 | 2019-05-24 | LEAD | 5641 | CHARTRES |  | WMTLK | LOCATIONID#111742-425943 METER#A413904 LEAK INSIDE METERBOX /** 1) MN: A260696 SN: 0059502, *TAP: SIZE: A LOC: 24 FEET FROM P LINE AT LAMANCHE, *MB: CODE: AFL LOC: ON CHARTRES 24FT FROM LAMANCHE ****/ | 2019-06-10 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900809303 | 2019-06-19 | LEAD | 5446 | DAUPHINE |  | WMTLK | EXAMINED JOB AT ABOVE LOCATION AND FOUND RED CHRSYLER SEABRING ZNN643 IS THE PLATE NUMBER CUSTOMER STATE THE CAR HAS BEEN THERE FOR MONTH JOB REFER BACK TO ZONE 07/29/19 5446-48 DAUPHINE EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER IN A LOW LYING AREA (KSW) /** 1) MN: A302865 SN: 0041517, *TAP: SIZE: A LOC: 175 FEET FROM P LINE AT FLOOD, *MB: CODE: CDL LOC: ON DAUPHINE 177FT FROM URPL FLOOD ****/ | 2019-08-14 | MADE REPAIR INLET AND OUTLET SERVICE IN MUD PLOT BACKFILLED AND CLEAN UP AREA 5/8 INCH LEAD + PLASTIC
201900809401 | 2019-05-24 | LEAD/PLASTIC | 1548 | AVIATORS |  | WMTLK | LOCATIONID#182614-488081 METER#C022112 METERBOX OVERFLOWING /** 1) MN: C026543 SN: 0133151, *TAP: SIZE: C LOC: 167 FEET FROM P LINE AT PARIS AVE, *MB: CODE: C LOC: 167FT PL PARIS AV 8' OUTSIDE 2' INSIDE CURB ****/ | 2019-06-10 | EXCAVATED A 3 X 3 MUD PLOT IN TREE ROOTS AND MADE REPAIRS ON THE INLET SERVICE PLASTIC ON THE OUTLET SERVICE LEAD ON THE INLET SERVICE BACKFILL AND CLEAN UP
201900809601 | 2019-05-24 | LEAD | 4500 | ST CLAUDE AV |  | WOLK | LOCATION ID-130204 MTR-A360638 UNDERGROUND LEAK BETWEEN MTR AND STOP & WASTE/CONS REG ON MTR /** 1) MN: A252498 SN: 0059723, *TAP: SIZE: A LOC: 71 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: BDLZ LOC: ON KENTUCKY 71FT FROM PL ST CLAUDE ****/ | 2019-06-19 | REPLACE BOTH OUTLET AND INLET WASHERS AT ABOVE LOCATION. JOB COMPLETE
201900809701 | 2019-05-24 | LEAD | 935 | ST ANN |  | WMTLK | LOCATION ID-119283 MTR-A404008 UNDERGROUND LEAK BY MTR /** 1) MN: A187966 SN: 0029822, *TAP: SIZE: A LOC: 35 FEET FROM P LINE AT BURGUNDY, *MB: CODE: AEK1 LOC: 18FT LPL CURB ****/ | 2019-06-05 | EXCAVATED IN PREVIOUS CUT + MADE REPAIR ON 3/4 INLET SERVICE LINE BACKFILLED + DRESSED UP AREA JOB COMPLETE
201900810201 | 2019-05-24 | LEAD | 1301 | FRANKLIN AV |  | WILK | ML-METER LEAK ACCT#124357-479766 METER#A360805 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A331469 SN: 0045137, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT ALMONASTER AVE, *MB: CODE: BDH1 LOC: SIDE ST ON URQUHART 49' P.L. ALMONASTER AVE ****/ | 2019-06-05 | EXCAVATED 2 X 4 LIMESTONES DRIVEWAY FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900811901 | 2019-05-24 | LEAD | 1135 | N MIRO | GOV NICHOLLS | WILK | ML: METER LEAK MTR# B042742 ACCT# 104200-524149 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: B027518 SN: 0022193, *TAP: SIZE: A LOC: 28 FEET FROM P LINE AT GOVERN NICHOLLS, *MB: CODE: CHL LOC: ON N MIRO 26FT FROM USPL OF GOVERN NICHOLLS ****/ | 2019-06-04 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 3/4 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND JOB COMPLETE
201900812901 | 2019-05-24 | LEAD | 2007 | ARTS | N JOHNSON | WMTLK | ML- METER LEAK METER# A373698 ACCT# 113525-577838 EXAMINE INLET/OUTLET SERVICE FOR A LEAK, UNABLE TO PUMP METER BOX DOWN /** 1) MN: A209336 SN: 0048598, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CGLM LOC: 49FT FROM LSPL JOHNSON ON ARTS ****/ | 2019-06-03 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900817301 | 2019-05-26 | LEAD | 2623 | SAGE | FRANKLIN AV | WILK | WATER LEAK ON INLET FLOODING AREA /** 1) MN: A229026 SN: 0087706, *TAP: SIZE: A LOC: 167 FEET FROM P LINE AT FRANKLIN AVE, *MB: CODE: BDL2 LOC: ON SAGE 167 FT FROM PL FRANKLIN AV 68350070197 ****/ | 2019-05-27 | EXAMINE WATER LEAK AT ABOVE LOCATION FOND 5/8 CURB COCK LEAKING.REPLACED 5/8 CURB COCK ALSO REPLACED 5/8 METER BOX COMPLETE. JOB COMPLETE
201900817401 | 2019-05-27 | LEAD | 2816 | PALMYRA | WHITE | WOLK | ML- METER LEAK ACCT#127233-705779 MTR# A138196 INSPECTOR FOUND CONS. OR METER. /** 1) MN: A138196 SN: 0052630, *TAP: SIZE: A LOC: 129 FEET FROM P LINE AT WHITE S, *MB: CODE: CD2 LOC: ****/ | 2019-06-14 | EXCAVATED IN MUD PLOT BEHIND METER BOX AND FOUND NO LEAK REPLACED HAND WHEEL INSIDE METER BOX FOUND NO CONSTANT BACKFILLED AREA
201900818101 | 2019-05-27 | LEAD | 316 | S BROAD | PALMYRA | WILK | WATER INLET SERVICE /** 1) MN: A121130 SN: 0035123, *TAP: SIZE: B LOC: 143 FEET FROM P LINE AT PALMYRA, *MB: CODE: CDM2 LOC: 143 FT FROM URP LINE AT PALMYRA ST. ****/ | 2019-05-26 | EXCAVATED 4 X 3 EXISTING DRIVEWAY CUT REPLACE METER COCK + CHOKE METER BACKFILLED AND CLEANED THE AREA OLD METER INFO: A429519 FACT: 16355108 MAKE: HERSEY READ: 0
201900818801 | 2019-05-27 | LEAD | 853 | TAFT PL | ORLEANS AV | WMTLK | ML- METER LEAK ACCT# 140719-514213 MTR# A314175 EXAMINE INLET AND OUTLET SERVICE FOR LEAK IN TREE ROOTS, METER UNDER WATER /** 1) MN: A314175 SN: 0071195, *TAP: SIZE: B LOC: 200 FEET FROM P LINE AT DUMAINE, *MB: CODE: BD LOC: ON TAFT 199' FROM USPL OF DUMAINE ****/ | 2019-06-13 | REPLACE WASHERS + SET NEW METER DUE TO METER HAVING A HOLE AT THE BOTTOM
201900819501 | 2019-05-27 | LEAD | 2117 | ST ROCH AV | N GALVEZ | WILK | WM-LEAK ON THE SIDEWALK INLET SERVICE LEAK IN ASPHALT STREET /** 1) MN: A271215 SN: 0056448, *TAP: SIZE: B LOC: 8 FEET FROM P LINE AT N GALVEZ, *MB: CODE: AL1 LOC: ON ST ROCH AVE. 9' FROM DPL OF NO. GALVEZ 8' OUTSI ****/ | 2019-06-17 | EXCAVATED 9 X 20 STREET CUT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED TEH AREA
201900819801 | 2019-05-28 | LEAD | 2102 | ST ANTHONY | N GALVEZ | WILK | WATER INLET LEAK /** 1) MN: 000000 SN: 0054877, *TAP: SIZE: A LOC: 67 FEET FROM P LINE AT ST ANTHONY, *MB: CODE: ADH LOC: METER ON GRANT 66.4 FT FROM PL ST ANTHONY AVE ****/ | 2019-05-26 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA ALSO REPLACED BROKEN 5/8 INCH METER BOX BOTTOM
201900821101 | 2019-05-28 | LEAD | 1605 | MANDEVILLE | N ROCHEBLAVE | WILK | ML- METER LEAK METER #A294245 ACCT#127403-724193 INLET SERVICE LEAK IN BOX CAUSING METER BOX TO OVERFLOW /** 1) MN: A234017 SN: 0052725, *TAP: SIZE: A LOC: 42 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: BDN LOC: ON MANDEVILLE,41.5' FROM L.S.P.L. NO. CLAIBORNE ****/ | 2019-06-11 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET RAISE METER BOX UP TO GRADE REPLACE CHOKED 5/8 INCH WATER METER BACKFILLED JOB WITH RIVERSAND COLDMILL **************OLD METER INFO************* METER:A294245 FAC:50331014 MAKE:SENSUS READ:8165
201900821801 | 2019-05-28 | LEAD | 1028 | ST FERDINAND |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 114373-426700 METER NUMBER - 396658 EXAMINE INLET SERVICE FOR A LEAK /** 1) MN: A253416 SN: 0019630, *TAP: SIZE: A LOC: 169 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: CFL LOC: 169FT FROM URPL ST CLAUDE AVE ****/ | 2019-06-11 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL LEFT ONE SAFETY CONE ON JOB FOR SAFETY. JOB COMPLETE
201900821901 | 2019-05-28 | LEAD | 4774 | EASTVIEW DR |  | WILK | WM-- LEAK INSIDE METER BOX ONCE REPAIRED 05/21/19 INLET ON ABANDON SERVICE IN FRONT VACANT LOT /** 1) MN: A293881 SN: 0128616, *TAP: SIZE: A LOC: 5 FEET FROM P LINE AT HAMMOND, *MB: CODE: BDK LOC: ON EASTVIEW DR 5' FROM PL HAMMOND 7' OUTSIDE PL ****/ | 2019-06-05 | EXCAVATED DOWN ON INLET SERVICE. FOUND LEAD AND INLET WAS LEAKING. MADE REAPIRS BY REPLACING SERVICE FROM LEAK TO METER BOX. BACKFILLED =. ABANDON LOT NO METER.
201900826401 | 2019-05-29 | LEAD | 920 | TAFT PL | DUMAINE | WILK | ML-METER LEAK ACCT#141336-704160 MTR#A296963 INLET SERVICE LEAK IN BOX IN MUDPLOT /** 1) MN: A254803 SN: 0072634, *TAP: SIZE: B LOC: 177 FEET FROM P LINE AT DUMAINE, *MB: CODE: BD LOC: ON TAFT PL 177' FROM PL DUMAINE ****/ | 2019-06-07 | EXCAVATED BY HAND IN MUD PLOT TO FIND INLET LEAKING MADE REPAIR ON 3/4 INCH INLET SERVICE BACKFILLED AND CLEANED THE AREA
201900828102 | 2019-06-08 | LEAD | 3613 | N MIRO |  | WILK | MADE 4 X 4 SIDEWALK CUT AND BEHIND METER BOX ON 3/4 INCH INLET SERVICE AND FOUND STILL NO WATER ON INLET AFTER CUTTING SHUT OFF VALVES ON REFER BACKFILLED TO ZONE TO RUN NEW FROM WATER MAIN /** 1) MN: A143830 SN: 0084578, *TAP: SIZE: A LOC: 136 FEET FROM P LINE AT CONGRESS, *MB: CODE: CE LOC: ON NO. MIRO,136' FROM P.L. CONGRESS,8' OUTSIDE ****/ | 2019-06-15 | EXCAVATED IN THE 5 X 8 CUT IN THE STREET OVER 4 INCH WATER AND FOUND 3/4 INCH TAP ON THE MAIN REPLACE 3/4 INCH TAILPIECE AND 20 FT 3/4 INCH WATER TUBING 5/8 INCH WATER BOX COMPLETE AND PUT ON THE OUTLET SERVICE 6 FT OF 3/4 INCH WATER TUBING PROPERTY SIDE BACKFILLED
201900828401 | 2019-05-29 | LEAD | 1472 | N ROMAN |  | WILK | ML- METER LEAK METER #A437559 ACCT #128431-487734 EXAMINE INLET SERVICE FOR LEAK /** 1) MN: A147943 SN: 0057405, *TAP: SIZE: A LOC: 82 FEET FROM P LINE AT COLUMBUS, *MB: CODE: BDK LOC: ON N ROMAN ST 85.5' FROM URPL COLUMBUS ****/ | 2019-06-24 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900833701 | 2019-05-30 | LEAD | 820 | BARTHOLOMEW | DAUPHINE | WILK | WATER INLET SERVICE LEAK /** 1) MN: A125867 SN: 0060148, *TAP: SIZE: __ LOC: 152 FEET FROM P LINE AT DAUPHINE, *MB: CODE: BDM2 LOC: ON BARTHOLOMEW,153.6' FROM P.L. DAUPHINE ****/ | 2019-05-29 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH HANDWHEEL BACKFILLED + DRESSED UP AREA. JOB COMPLETE
201900835901 | 2019-05-30 | LEAD | 2566 | N ROCHEBLAVE |  | WMTLK | LOCATION ID-140042 MTR-A420600 UNDERGROUND LEAK BETWEEN MTR AND STOP & WASTE/CONS REG ON MTR /** 1) MN: SN: 0142850, *TAP: SIZE: A LOC: 44 FEET FROM P LINE AT MUSIC, *MB: CODE: CDL1 LOC: ON N ROCHEBLAVE ST 43.6' FROM URPL MUSIC ST ****/ | 2019-06-11 | EXAMINED AND REMOVE CEMENT FROM INSIDE OF METER BOX FOUND NO CONS REG ON 5/8 INCH METER AT ABOVE LOCATION
201900836401 | 2019-05-30 | LEAD | 1217 | DESIRE |  | WMTLK | LOCATIONID#121460-429615 METER#A420354 LEAK INSIDE METERBOX /** 1) MN: A278168 SN: 0061825, *TAP: SIZE: A LOC: 155 FEET FROM P LINE AT MARAIS, *MB: CODE: __ LOC: 155' P.L. MARAIS ****/ | 2019-06-19 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND CODLMILL LEFT ONE SAFETY CONE ON JOB SITE
201900836501 | 2019-05-30 | LEAD | 1207 | FRANCE |  | WMTLK | LOCATIONID#136281-432110 METER#A423561 LEAK INSIDE METERBOX /** 1) MN: A144536 SN: 0053550, *TAP: SIZE: A LOC: 68 FEET FROM P LINE AT MARAIS, *MB: CODE: AEK4 LOC: ON FRANCE ST 68' FROM PL MARAIS ****/ | 2019-06-12 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900836601 | 2019-05-30 | LEAD | 1240 | LESSEPS |  | WILK | LOCATIONID#137114-430752 METER#A427334 BLEEDER LEAK /** 1) MN: A287518 SN: 0067710, *TAP: SIZE: A LOC: 79 FEET FROM P LINE AT LESSEPS, *MB: CODE: BDL3 LOC: ON URQUHART, 79' FROM P.L. LESSEPS ****/ | 2019-06-17 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900836701 | 2019-05-30 | LEAD | 1317 | LESSEPS |  | WMTLK | LOCATIONID#146254-430890 METER#A432464 LEAK INSIDE METERBOX /** 1) MN: A330636 SN: 0078140, *TAP: SIZE: B LOC: 140 FEET FROM P LINE AT URQUHART, *MB: CODE: CEL1 LOC: ON LESSEPS, 139' FROM P.L. URQUHART ****/ | 2019-06-17 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900837501 | 2019-05-30 | LEAD | 809 | BOURBON | ST ANN | WILK | MI- CUT SERVICE ENETERGY GAS 3700 TULANE AVE NEW ORLEANS LA 70119 # 504-593-3439 ** CUST WITHOUT WATER*** *******DAMAGE CLAIM******* (J GILLIAM @ 10:32AM) CUT INLET SERVICE IN STREET INTERFERING WITH ENTERGY WORK, CUSTOMER OUT OF WATER **FOREMAN DANIEL MURRAY (985)516-52584 /** 1) MN: A302069 SN: 0006261, *TAP: SIZE: C LOC: 66 FEET FROM P LINE AT ST ANN LSPL, *MB: CODE: AFKM LOC: 66' FROM LSPL ST ANN ****/ | 2019-05-30 | ARRIVED AT ABOVE LOCATION FOUND INLET SERVICE DAMAGE BY ENTERGY CONSTRUCTION MADE REPAIR AT MAIN TO GIVE CUSTOMER WATER BACK FORCE ACCOUNT TO ENTERGY. JOB COMPLETE
201900838601 | 2019-05-30 | LEAD | 1355 | ST BERNARD AV | URQUHART | WOLK | ACCT# 109175-525615 MTR# B042880 INSPECTOR FOUND CONS. REG ON METER. /** 1) MN: B024194 SN: 0043077, *TAP: SIZE: B LOC: 72 FEET FROM P LINE AT URQUHART, *MB: CODE: AEW2 LOC: 72FT FROM LSPL URQUHART ON ST BERNARD AVE ****/ | 2019-06-11 | EXAMINED JOB AT ABOVE LOCATION FOUND NO CON REG ON 3/4 INCH METER
201900838701 | 2019-05-30 | LEAD | 1530 | INDEPENDENCE | N CLAIBORNE AV | WILK | ACCT# 162006-430482 MTR# A389802 INSPECTOR FOUND LEAK INSIDE METER AND AROUND CURBCOCK /** 1) MN: A313945 SN: 0100816, *TAP: SIZE: A LOC: 153 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: ADO2 LOC: 153'FROM P L NO CLAIBORNE 7' OUTSIDE PL ****/ | 2019-06-17 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900840301 | 2019-05-30 | LEAD | 2235 | CHARTRES | MARIGNY | WILK | ML; METER LEAK ACCT #112428-73189 MTR#A263773 INLET SERVICE LEAK BAD CURBCOCK IN CONCRETE SIDEWALK /** 1) MN: A263773 SN: 0032949, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT MARIGNY, *MB: CODE: BFKN LOC: 48' P.L. MARIGNY ****/ | 2019-06-12 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL JOB COMPLETE
201900841001 | 2019-05-30 | LEAD | 2208 | EADS |  | WOLK | LOCATION: 149714 MTR# A 419475 INSP UDUEBOR STATES OUTLET SERVICE LEAKING BEHIND WHEEL. PLEASE REPAIR. OUTLET SERVICE LEAK BROKEN HANDWHEEL WITH CONSTANT REGISTRATION /** 1) MN: A224532 SN: 0082360, *TAP: SIZE: B LOC: 80 FEET FROM P LINE AT MIRO N, *MB: CODE: CDLN LOC: 80FT FROM PL MIRO ****/ | 2019-06-12 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION NO MORE CONS REG ON METER. JOB COMPLETE
201900841101 | 2019-05-30 | LEAD | 1418 | MAZANT |  | WILK | LOCATION: 135738 MTR# A 433898 INSP UDUEBOR FOUND INLET SERVICE LEAKING, BAD BLEEDER VALVE. PLEASE REPAIR INLET SERVICE LEAK INSIDE CONCRETE SIDEWALK /** 1) MN: A314913 SN: 0069827, *TAP: SIZE: A LOC: 177 FEET FROM P LINE AT VILLERE N, *MB: CODE: CDL1 LOC: 177'FROM N VILLERE ****/ | 2019-06-19 | EXAMINE JOB AT ABOVE FOUND NO ELAK ON INLET OR OUTLET SERVICE
201900842401 | 2019-05-31 | LEAD | 116 | BARONNE |  | WOLK | MI-METER BOX LEAKING CHECK FOR LEAK @ PROPERTY LINE IN SIDEWALK, CON REG /** 1) MN: B030884 SN: 0009788, *TAP: SIZE: Y LOC: 117 FEET FROM P LINE AT CANAL, *MB: CODE: AIN LOC: 4TH METER 117FT FROM URPL CANAL ****/ | 2019-06-12 | EXAMINE JOB AT ABOVE LOCATION FOUND CONS REG ON 3/4 INCH METER CUSTOMER HAS A ICE MAKER MACHINE INSIDE HE SHUT OFF ICE MAKER AND CONS REG STOP THERE NO LEAK ON OUTLET ICE MAKER KEEP RUNNING CAUSING CON REG ON METER
201900843101 | 2019-05-31 | LEAD | 2257 | MARAIS |  | WILK | ML-METER LEAK ACCT#128006-481434 MTR#A418578 INLET SERVICE LEAK IN DRIVEWAY, METER UNDER WATER IN LOW LINE AREA /** 1) MN: A290662 SN: 0054708, *TAP: SIZE: A LOC: 123 FEET FROM P LINE AT MARIGNY, *MB: CODE: AD2 LOC: ON MARAIS,120.4' FROM L.S.P.L. MARIGNY ****/ | 2019-06-18 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900845001 | 2019-05-31 | LEAD | 847 | TAFT PL | ORLEANS AV | WOLK | ML-METER LEAKING AGAIN METER#A312379 ACCT#143807-716090 OUTLET LEAK (IN MUDPLOT), HOUSE UNDER CONSTRUCTION /** 1) MN: A312379 SN: 0075130, *TAP: SIZE: B LOC: 332 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: BE LOC: ON TAFT PL., 332' FROM P.L. ORLEANS AVE. ****/ | 2019-06-07 | MADE REPAIR ON OUTLET SERVICE BACKFILLED AND CLEANED THE AREA
201900845401 | 2019-05-31 | LEAD | 717 | N RENDON | ORLEANS AV | WILK | MI: LEAK IN THE SIDEWALK INLET LEAK IN SIDEWALK (ON ORLEANS STREET SIDE) , FLOODING THE SIDEWALK BUT GETTING OFF IN THE DCB /** 1) MN: B030386 SN: 0054713, *TAP: SIZE: B LOC: 58 FEET FROM P LINE AT RENDON N, *MB: CODE: BDHN LOC: ON ORLEANS AVE.,59.3' FROM U.S.P.L. NO. RENDON ****/ | 2019-06-14 | MADE 4 X 4 SIDEWALK CUT AND MADE REPAIR ON 3/4 INCH INLET SERVICE AND REPLACEDCURB COCK BACKFILLED AREA
201900845501 | 2019-05-31 | LEAD | 1625 | MARIGNY |  | WOLK | LOCATION: 307755 INSP UDUEBOR SET METER# A 433878. CUSTOMER NEED OUTLET TIE IN. CUSTOMER WAITING ON WATER RENEW OUTLET SERVICE (HOUSE UNDER RENOVATION) /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-06-12 | EXCAVATED 2 X 8 MUD PLOT IN SIDEWALK RENEW 5/8 INCH OUTLET SERVICE FROM METER BOX TO PROPERTY BACKFILLED JOB WITH RIVERSAND TIE INTO 3/4 INCH PLASTIC LINE
201900847101 | 2019-06-01 | LEAD | 2104 | MUSIC | N GALVEZ | WILK | WM-LEAK IN STREET INLET LEAK IN 7X7 ASPHALT STREET CUT C /** 1) MN: A295458 SN: 0075933, *TAP: SIZE: B LOC: 37 FEET FROM P LINE AT GALVEZ N, *MB: CODE: ADK3 LOC: ON MUSIC ST 36.5' FROM PL N GALVEZ ST ****/ | 2019-06-15 | EXCAVATED IN THE 4 X 8 CUT IN THE STREET OVER 3/4 INCH INLET SERVICE FOUND 3/4 INCH TAILPIECE AND REPLACED 4 FT OF 3/4 INCH WATER TUBING BACKFILL JOB COMPLETE
201900851501 | 2019-06-03 | LEAD | 130 | S WHITE | CANAL | WILK | INLET SERVICE LEAK. LEAK IS BETWEEN SIDEWALK AND CURB. LEAK IS VISIBLE. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 5/30/2019. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-06-13 | EXCAVTED 5 X 4 STREET CUT MADE REPAIR ON ABANDON INLET SERVICE LINE BACKFILLED JOB COMPLETE
201900854701 | 2019-06-03 | LEAD | 129 | S DUPRE | CLEVELAND AV | WILK | INLET SERVICE LEAK. LEAK IS SATURATING GRASS AND DRAINING DOWN ROADWAY. ECHOLOGICS REPORTED AND MARKED LEAK. /** 1) MN: A290321 SN: 0015264, *TAP: SIZE: A LOC: 87 FEET FROM P LINE AT CLEVELAND AVE, *MB: CODE: AFM6 LOC: INSIDE 91' P.L. CLEVELAND AVE ****/ | 2019-06-11 | EXCAVATED 9 X 6 MUD PLOT TO LOCATE INLET SERVICE LEAK MADE REPAIR ON SERVICE LINE BACKFILLED AND CLEANED THE AREA
201900855501 | 2019-06-03 | LEAD | 1817 | ST PHILIP |  | WILK | ML - METER LEAK ACCOUNT NUMBER - 304620-719478 METER NUMBER - A415932 INLET SERVICE LEAK BAD BLEEDER VALVE LEAKING INSIDE METER BOX /** 1) MN: SN: 0051030, *TAP: SIZE: A LOC: 128 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: AFKL LOC: INSIDE BY S & W 0128' P.L. N DERBIGNY ****/ | 2019-06-18 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED WITH RIVERSAND AND COLDMILL LEFT ONE SAFETY CONE JOB SITE
201900857001 | 2019-06-03 | LEAD | 2305-07 | FRENCHMEN |  | WILK | MI- LEAK IN THE STREET *****FLOODING THE AREA******* INLET SERVICE LEAK IN ASPHALT STREET GETTING OFF IN DCB LEFT ONE (1) CONE FOR SAFETY /** AT 2305: 1) MN: A267582 SN: 0069136, *TAP: SIZE: B LOC: 52 FEET FROM P LINE AT TONTI, *MB: CODE: BDLM LOC: ON FRENCHMEN ST 52' FROM N TONTI ** AT 2307: 2) MN: A329083 SN: 0069136, *TAP: SIZE: B LOC: 53 FEET FROM P LINE AT ROCHEBLAVE, *MB: CODE: BDL1 LOC: ON FRENCHMEN 54'FROM DPL OF NO.ROCHEBLAVE 8' OUTSI ****/ | 2019-06-18 | EXCAVATED 4 X 4 STREET CUT MADE REPAIR ON INLET SERVICE LINE REPLACE CHOKED METER WITH NEW METER BACKFILLED AND CLEANED TEH AREA OLD METER INFO: A407764 FACT: 14113526 MAKE: HERSEY READ: 4871
201900857003 | 2019-06-19 | LEAD | 2305-07 | FRENCHMEN |  | WILK | INLET SERVICE LEAK /** AT 2305: 1) MN: A267582 SN: 0069136, *TAP: SIZE: B LOC: 52 FEET FROM P LINE AT TONTI, *MB: CODE: BDLM LOC: ON FRENCHMEN ST 52' FROM N TONTI ** AT 2307: 2) MN: A329083 SN: 0069136, *TAP: SIZE: B LOC: 53 FEET FROM P LINE AT ROCHEBLAVE, *MB: CODE: BDL1 LOC: ON FRENCHMEN 54'FROM DPL OF NO.ROCHEBLAVE 8' OUTSI ****/ | 2019-06-18 | REPLACED CHOKE METER WITH NEW METER
201900857201 | 2019-06-03 | LEAD | 520 | ROYAL | ST LOUIS | WILK | WM - LEAK IN THE STREET CHANGED FROM 500 BLK ROYAL/ST LOUIS INLET SERVICE LEAK IN ASPHALT STREET 06/05/19 CUSTOMER STATES LEAK GETTING WORSE (NLD) /** 1) MN: A330398 SN: 0000000, *TAP: SIZE: H LOC: 154 FEET FROM P LINE AT ST LOUIS, *MB: CODE: CD LOC: ON ROYAL 154FT FROM ST LOUIS ****/ | 2019-06-12 | EXCAVATED 9 X 6 STREET CUT MADE REPAIR ON 2 INCH ABANDON SERVICE LINE BACKFILLED AND CLEANED THE AREA
201900858801 | 2019-06-04 | LEAD | 2017 | MARAIS | TOURO | WOLK | INSP L UDUEBOR STATES SERVICE HAS AN OUTLET SERVICE LEAK. CUSTOMER IS WAITING ON WATER. PLEASE REPAIR METER A433917 LOC 307775 **********CUSTOMER OUT OF WATER********** M DAIGLE 10:38 OUTLET SERVICE LEAKING BEHIND HANDWHEEL ***TENANT IS HOME*** /** 1) MN: A132250 SN: 0051213, *TAP: SIZE: A LOC: 73 FEET FROM P LINE AT TOURO, *MB: CODE: AFKN LOC: BY GATE AT 2017 STEPS 2FT FROM LPL CURB ** 2) MN: A195773 SN: 0051213, *TAP: SIZE: B LOC: 2 FEET FROM P LINE AT TOURO, *MB: CODE: OOOO LOC: ON MARAIS 3FT FROM DIV P/L TOUTO 2FT OUTSIDE ****/ | 2019-06-04 | EXCAVATED 4 X 4 BRICK SIDEWALK LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIR ON OUTLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900860901 | 2019-06-04 | LEAD | 2887 | ANNETTE | FLORIDA AV | WMTLK | WATER METER LEAK. LEAK IS VISIBLE. LEAK IS NEXT TO POWER POLE. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 5/31/2019. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-06-26 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900861601 | 2019-06-04 | LEAD | 1829 | ARTS | N PRIEUR | WMTLK | WATER METER LEAK. LEAK BETWEEN ROADWAY AND SIDEWALK. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 5/31/2019. /** 1) MN: A281939 SN: 0055826, *TAP: SIZE: A LOC: 101 FEET FROM P LINE AT PRIEUR N, *MB: CODE: ADN1 LOC: ON ARTS,100' FROM L.R.P.L. NO. PRIEUR ****/ | 2019-06-20 | EXCAVATED IN GUTTER BOTTOM AND REPLACED 5/8 INCH CURB COCK WITH NEW ONE BACKFILLED AREA
201900861701 | 2019-06-04 | LEAD | 1571 | N ROCHEBLAVE | LAPEYROUSE | WILK | MI- METER BOX LEAK **VACANT LOT** EXAMINE INLET SERVICE LEAK /** 1) MN: A306586 SN: 0043936, *TAP: SIZE: A LOC: 97 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: CFLM LOC: ON N ROCHEBLAVE 95FT FROM USPL LAPEYROUSE ****/ | 2019-06-19 | PUMPED WATER FROM FLOODED AREA MADE 3 X 2 MUD PLOT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201900862601 | 2019-06-04 | LEAD | 226 | N RENDON | BIENVILLE | WILK | WM- LEAK IN STREET INLET SERVICE LEAK IN ASPHALT STREET IN FRONT OF ABOVE ADDRESS /** 1) MN: A330132 SN: 0016809, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT IBERVILLE, *MB: CODE: CFLM LOC: ON N RENDON 154FT FROM PL IBERVILLE 4' OUTSIDE PL ****/ | 2019-06-16 | EXCAVATED 7 X 5 STREET CUT MADE REPAIR ON INLET SERVICE LINE IN STREET BACKFILLED AND CLEANED THE AREA
201900864701 | 2019-06-05 | LEAD | 2232 | PAINTERS | N TONTI | WMTLK | WATER METER LEAK. LEAK IS BETWEEN THE ROADWAY AND SIDEWALK. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/03/2019. /** 1) MN: A313280 SN: 0064824, *TAP: SIZE: A LOC: 81 FEET FROM P LINE AT TONTI N, *MB: CODE: CMN LOC: ON PAINTERS, 84' FROM P.L. NO. TONTI ****/ | 2019-06-24 | EXCAVATED IN GUTTER BOTTOM AND MADE REPAIR ON 3/4 INCH INLET SERVICE BACKFILLED AREA NO METER INSIDE BOX
201900864901 | 2019-06-05 | LEAD | 1408 | LEDA CT | ESPLANADE AV | WOLK | MI: LEAD WHIP CHANGE ACCT#137746-490897 MTR#A407273 CHANGE LEAD WHIP HOLE OPEN. FOUND 1 BARREL ON SITE /** 1) MN: A336018 SN: 0068467, *TAP: SIZE: B LOC: 121 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: BDL LOC: ON LEDA, 120.8' FROM P.L. ESPLANADE AVE. ****/ | 2019-07-08 | EXCAVATED IN CONMCRETE SIDEWALK + REPLACED 5/8 INCH LEAD OUTLET FROM METER BOX TO PROPERTY BACKFILLED + DRESSED UP AREA
201900865001 | 2019-06-05 | LEAD | 2407 | N VILLERE | ST ROCH AV | WMTLK | WATER METER LEAK. LEAK BETWEEN ROADWAY AND SIDEWALK. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/3/2019. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-06-24 | REMOVED BRICK AND STACKED AGAINST FENCE EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA NO METER INSDE BOX
201900866302 | 2019-06-18 | LEAD/PLASTIC | 839 | BELLEVILLE |  | WMRE | INSP L MITCHELL STATES SERVICE IS BURIED. PLEASE RAISE TO GRADE AND SET 5/8 METER. LOC 307774 LOCATE, RAISE TO GRADE, SET 5/8 METER, ALSO RENEW OUTLET SERVICE ***NEW CONSTRUCTION*** /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-06-20 | EXCAVATED IN MUD PLOT TO LOCATE METER. LOCATED AND RASIED METER BOX TO GRADE. INSTALLED A NEW METER BOX COMPLETE AND METER. HOLE WAS BACKFILLE, PLACTIC WHIP ON THE OUTLET RASIED WITH STICK AND MARKED WITH BLUE PANI FOR VISIBILITY.
201900867801 | 2019-06-05 | LEAD | 2019 | GALLIER | N JOHNSON | WILK | WM- LEAK BETWEEN SIDEWALK AND STREET INLET SERVICE LEAK IN MUDPLOT NEXT TO VACANT LOT /** 1) MN: A289939 SN: 0084256, *TAP: SIZE: A LOC: 125 FEET FROM P LINE AT JOHNSON N, *MB: CODE: AD LOC: FRONT ****/ | 2019-06-19 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900868201 | 2019-06-05 | LEAD | 3113 | BANKS | S LOPEZ | WILK | ML-METER LEAK METER#A364758 ACCT#114176-532224 INLET SERVICE LEAK IN SIDEWALK /** 1) MN: A273574 SN: 0015852, *TAP: SIZE: A LOC: 85 FEET FROM P LINE AT LOPEZ S, *MB: CODE: CFML LOC: ON BANKS 86' FROM LRPL S LOPEZ ****/ | 2019-06-24 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900868501 | 2019-06-05 | LEAD | 1519 | ST ANN | VILLERE | WILK | WM - LEAK ON THE INLET SERVICE LEAK IN SIDEWALK /** 1) MN: A323193 SN: 0033619, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT VILLERE N, *MB: CODE: BFK2 LOC: ****/ | 2019-08-07 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION. JOB COMPLETE
201900870101 | 2019-06-06 | LEAD | 324 | N ROMAN |  | WMTLK | LOCATIONID#138804-708480 METER#A404679 METERBOX OVERFLOWING /** 1) MN: A212996 SN: 0069448, *TAP: SIZE: B LOC: 197 FEET FROM P LINE AT BIENVILLE, *MB: CODE: AD LOC: ON NO. ROMAN, 103' FROM U.P.L. CONTI ****/ | 2019-06-24 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900870401 | 2019-06-06 | LEAD/PLASTIC | 3706 | VINCENNES PL | MC KENNA | WOLK | LOCATION ID-153730 MTR-B023246 UNDERGROUND LEAK BETWEEN MTR AND STOP & WASTE/CONS REG ON MTR /** 1) MN: B023246 SN: 0089739, *TAP: SIZE: B LOC: 49 FEET FROM P LINE AT VINCENNES PL, *MB: CODE: AH2 LOC: ON MCKENNA 49FT FROM PL VINCENNES 5FT OUT PL ****/ DOTTIE READY 6-11-19 EXP 7-1-19 | 2019-06-12 | EXAMINED ,EXCAVTED BY HAND AND RENEWED OUTLET FROM METER BOX TO PROPERTY LINE BY REMOVING LEAD LINE AND REPLACED WITH PLASTIC TUBING .BACKFILLED CLEANED UP AND WASHED DOWN WORK AREA TO COMPLETE JOB ALSO RAISED METER TO PROPER GRADE."LEAD INLET" (SOC 2 FT. X 4 FT .S/W) *********OLD METER INFO*********** METER:B023246 FAC:34753381 MAKE:ROCKWELL READ:25407
201900870701 | 2019-06-06 | LEAD | 1418 | SPAIN | N VILLERE | WMTLK | WATER METER LEAK. LEAK UNDERNEATH SIDEWALK. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/4/2019. /** 1) MN: A314833 SN: 0054903, *TAP: SIZE: A LOC: 155 FEET FROM P LINE AT VILLERE N, *MB: CODE: CEL LOC: ON SPAIN,153.5' FROM P.L. NO. VILLERE ****/ | 2019-06-24 | MADE 2 X 2 SIDEWALK CUT AND REPLACE 5/8 INCH CURB COCK BACKFILL AREA
201900871001 | 2019-06-06 | LEAD | 2219 | SPAIN | N MIRO | WMTLK | WATER METER LEAK. LEAK IS BETWEEN THE ROADWAY AND THE SIDEWALK. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/4/2019. /** 1) MN: A271355 SN: 0102632, *TAP: SIZE: A LOC: 143 FEET FROM P LINE AT MIRO N, *MB: CODE: CDLM LOC: ON SPAIN, 143' FROM P.L. NO. MIRO, 8' OUTSIDE P.L. ****/ | 2019-06-28 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201900871301 | 2019-06-06 | LEAD | 2324 | N DERBIGNY | SPAIN | WMTLK | WATER METER LEAK. LEAK UNDERNEATH SIDEWALK. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/4/2019. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-06-20 | EXCAVATE 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND CODLMILL
201900872701 | 2019-06-06 | LEAD | 1338 | KERLEREC |  | WILK | MI LEAK BY THE CURB INLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A268329 SN: 0005610, *TAP: SIZE: A LOC: 125 FEET FROM P LINE AT VILLERE N, *MB: CODE: BFNK LOC: ****/ | 2019-06-21 | EXCAVATED 6 X 3 MUD PLOT AT EDGE OF SIDEWALK MADE REPAIR ON INLET SERVICE LINEAT MAIN BACKFILLED AND CLEANEDTHE AREA
201900874101 | 2019-06-06 | LEAD | 1984 | N DORGENOIS |  | WILK | ML-METER LEAK ACCT#160337-495576 MTR#A329041 INLET SERVICE LEAK ON SIDEWALK /** 1) MN: A117752 SN: 0125777, *TAP: SIZE: A LOC: 185 FEET FROM P LINE AT NEW ORLEANS, *MB: CODE: AD LOC: ON N DORGENOIS 184.5' FROM PL NEW ORLEANS 8' OUTSI ****/ | 2019-06-20 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL LEFT ONE SAFETY CONE ON JOB SITE
201900875201 | 2019-06-07 | LEAD | 701 | DECATUR |  | WOLK | OUTLET SERVICE LEAK /** 1) MN: A226738 SN: 0000000, *TAP: SIZE: B LOC: 18 FEET FROM P LINE AT ST PETER, *MB: CODE: __ LOC: ON DECATUR, 18' FROM C.P.L. ST. PETER, 15' OUTSIDE ****/ | 2019-06-06 | EXCAVATED AND MADE REPAIR ON 3/4 INCH OUTLETSERVICE LEAK BACKFILLED AND CLEANED UP AREA
201900875301 | 2019-06-07 | LEAD | 1233 | KERLEREC |  | WILK | ML METER LEAK METER# A359971 ACCT# 102398-486164 INLET SERVICE LEAK IN BRICK SIDEWALK /** 1) MN: A123002 SN: 0003585, *TAP: SIZE: B LOC: 225 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: BFK5 LOC: ON KERLEREC 225FT FROM LSPL OF ST CLAUDE AVE ****/ | 2019-06-20 | EXCAVATED 3 X 2 BRICK SIDEWALK CUT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED TEH AREA LEFT BRICK STACK AGAINT THE HOUSE
201900875501 | 2019-06-07 | LEAD | 1225 | KERLEREC | ST CLAUDE AV | WILK | **********PICK UP********** INLET SERVICE LEAK BAD BLEEDER VALVE /** 1) MN: A250233 SN: 0055738, *TAP: SIZE: A LOC: 79 FEET FROM P LINE AT TOULOUSE, *MB: CODE: AFM4 LOC: ON KERLEREC,194' FROM L.S.P.L. ST. CLAUDE AVE. ****/ | 2019-06-20 | EXCAVATED 3 X 2 SIDEWALK CUT MADE REPAIR ON INLET SERVICE ;INE BACKFILLED AND CLEANEDTHE AREA
201900881901 | 2019-06-09 | LEAD | 2901 | BRUXELLES | AGRICULTURE | WMLK | MI LEAK BTW SIDEWALK/STREET LEAK ON THE MAIN IN CONCRETE DRIVEWAY /** 1) MN: A308794 SN: 0078048, *TAP: SIZE: C LOC: 2 FEET FROM P LINE AT AGRICULTURE, *MB: CODE: ADK2 LOC: 25FT FROM PL AGRICULTURE ****/ | 2019-06-16 | EXCAVATED 4 X 3 DRIVEWAY CUT ALSO 4 X 3 MUD PLOT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA NO METER AT THIS LOCATION WHERE LEAK WAS FOUND
201900882001 | 2019-06-09 | LEAD/PLASTIC | 7955 | EDGELAKE CT |  | WMLK | MI LEAK IN THE STREET OVERFLOWING CHANGED FROM 7965 EDGELAKE CT EXAMINE WATER MAIN FOR LEAK IN STREET /** 1) MN: A233328 SN: 0137331, *TAP: SIZE: B LOC: 14 FEET FROM P LINE AT HYDT #4, *MB: CODE: CEL4 LOC: ON EDGEDLAKE CT 14' FROM PL HYDT #4 R/S 7' OUTSIDE ****/ | 2019-06-30 | MADE A 10X8 CUT IN ASPHALT STREET. EXCAVATED DOWN ON 6 INCH WATER MAIN AT TAP. FOUND LEAD AND PLASTIC ALSO CORP COCK WAS COMING FRM OUT OF MAIN. MADE REPAIRS BY USING A 6 INCH FULL CIRCLE TAP CLAMP TO COVER OVER HOLE IN MAIN ALSO REPLACED COCK TAILPIECE AND 7FT OF SERVICE BACKFILLED. SERVICE WAS FRO ABANDON LOT ACROSS THE STREET FROM LOCATION ABOVE NO METER.
201900882601 | 2019-06-10 | LEAD/PLASTIC | 427 | S PIERCE | BANKS | WILK | INLET SERVICE LEAK. LEAK UNDERNEATH ROADWAY. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/5/2019. /** 1) MN: A320908 SN: 0026845, *TAP: SIZE: A LOC: 115 FEET FROM P LINE AT BAUDIN, *MB: CODE: __ LOC: 115' P.L. BAUDIN ****/ DOTTIE READY 6-13-19 EXP 7-3-19 | 2019-06-22 | MADE CUT OVER WATER MAIN.REPAIRED INLET SERVICE BACKFILLED CUT.(SOC 6FT. X 6 FT .ASPHALT F/D)
201900882701 | 2019-06-10 | LEAD | 1336 | ST FERDINAND | N VILLERE | WMTLK | WATER METER LEAK. LEAK UNDERNEATH SIDEWALK - VISIBLE. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/5/2019. /** 1) MN: C023272 SN: 0123894, *TAP: SIZE: C LOC: 54 FEET FROM P LINE AT VILLERE N, *MB: CODE: CDN3 LOC: FRONT BY POST 54FT PL N VILLERE 7' OUTSIDE 1' IN- ****/ | 2019-06-27 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 1 INCH INLET SERVICE MADE REAPIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900882801 | 2019-06-10 | LEAD | 1405 | MARIGNY | N DERBIGNY | WMLK | WATER MAIN LEAK. LEAK IS UNDERNEATH ROADWAY - VISIBLE. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/5/2019. /** 1) MN: SN: 0058188, *TAP: SIZE: A LOC: 46 FEET FROM P LINE AT VILLERE N, *MB: CODE: BD5 LOC: FRONT ON MARIGNY 44FT FROM LSPL VILLERE ****/ | 2019-06-15 | EXCAVATED 6 X 6 STREET CUT MADE REPAIR ON INLET SERVICE LINE AT MAIN BACKFILLED AND CLEANED THE AREA ALSO LEFT ONE BARREL ON TOP OF CUT DUE WETNESS OF THE MATERIAL
201900883001 | 2019-06-10 | LEAD | 1415 | ELYSIAN FIELDS AV | N VILLERE | WILK | MI- LEAK IN THE STREET INLET SERVICE LEAK INSIDE BOX IN TREE ROOTS /** 1) MN: A309401 SN: 0037872, *TAP: SIZE: A LOC: 1045 FEET FROM P LINE AT VILLERE N, *MB: CODE: BD1 LOC: ON ELYSIAN FIELDS AVE.,103' FROM L.S.P.L. ****/ | 2019-06-15 | EXCAVATED 3 X 2 MUD PLOT THROUGH TREE ROOTS MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANEDTHE AREA
201900883602 | 2019-06-24 | LEAD/PLASTIC | 120 | S PIERCE | CANAL | WILK | EXCAVATED 12 X 12 STREET CUT REPAIR 2 INCH INLET SERVICE LINE ANOTHER LEAK EXIST BUT WAS UNABLE TO PINPOINT LEAK REFER BACK ZONE 3 TO MAKE REPAIR REFER TO ECHOLOGICS TO PINPOINT LEAK BACKFILLED AND CLEANED THE AREA ALSO LEFT BARREL WITH FLAGS AROUND AREA FOR SAFETY /** 1) MN: 000000 SN: 0072873, *TAP: SIZE: B LOC: 146 FEET FROM P LINE AT CANAL, *MB: CODE: CD LOC: 3RD METER-147FT FROM PL OF CANAL ** 2) MN: C023564 SN: 0072873, *TAP: SIZE: C LOC: 39 FEET FROM P LINE AT CANAL, *MB: CODE: CD LOC: ON S PIERCE 39FT FROM DIV P/L CANAL 12FT OUTSIDE THERE IS 1 MORE NOT LISTED. ****/ DOTTIE READY 6-13-19 EXP 7-3-19 | 2019-06-30 | MADE REPAIRS ON INLET SERVICE IN STREET .BACKFILLED WITH SAND AND LIME STONES.(SOC 12 FT. X 12 FT. CONCRETE BASE)
201900886801 | 2019-06-10 | LEAD | 6216 | N ROBERTSON |  | WMTLK | LOCATION ID-191138 MTR-A400845 METER LEAK/AREA FLOODED EXAMINE INLET/OUTLET SERVICE FOR LEAK UNABLE TO PUMP DOWM /** 1) MN: A317614 SN: 0141565, *TAP: SIZE: B LOC: 138 FEET FROM P LINE AT ST MAURICE, *MB: CODE: ADKO LOC: RES ON ROBERTSON 137FT FROM PL ST MAURICE ****/ | 2019-06-21 | EXCAVATED 4 X 3 MUD PLOT AFTER REMOVING WATER OUT THE AREA MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201900887501 | 2019-06-10 | LEAD | 4910 | ROYAL |  | WILK | ML METER LEAK MTR# B042768 ACCT# 150077-422457 MR WASHINGTON STATED HE HAS A SEVERE WATER LEAK AROUND THE METER INLET SERVICE LEAK IN METER BOX BAD CURBCOCK /** 1) MN: B023691 SN: 0101339, *TAP: SIZE: C LOC: 74 FEET FROM P LINE AT DESLONDE, *MB: CODE: CD LOC: 73FT FROM PL DESLONDE ****/ | 2019-06-25 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON ON 3/4 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSNAD
201900887801 | 2019-06-10 | LEAD | 2508 | N MIRO | ARTS | WMTLK | ML-METER LEAK METER#A429616 ACCT#131469-483946 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A113569 SN: 0062161, *TAP: SIZE: A LOC: 35 FEET FROM P LINE AT ARTS, *MB: CODE: BDK3 LOC: ON NO. MIRO,35' FROM P.L. ARTS ****/ | 2019-06-21 | EXCAVATED IN MUD PLOT AND MADE REPAIR ON 3/4 INCH OUTLET SERVICE BEHIND METER BOX BACKFILLED AREA JOB COMPLETE
201900888701 | 2019-06-11 | LEAD | 1314 | ANNETTE | MARAIS | WMLK | WATER MAIN LEAK. LEAK IN ROADWAY. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/7/2019. /** 1) MN: A322719 SN: 0057624, *TAP: SIZE: A LOC: 126 FEET FROM P LINE AT MARAIS, *MB: CODE: BF4 LOC: INSIDE 126' P.L. MARAIS ****/ | 2019-06-15 | EXCAVATED 6 X 5 STREET CUT MADE REPAIR AT MAIN TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900888901 | 2019-06-11 | LEAD | 1834 | O"REILLY | OLD PRIEUR | WMLK | WATER MAIN LEAK. LEAK IS UNDERNEATH ROADWAY. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/7/2019. /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-06-15 | EXCAVATED 7 X 10 STREET CUT MADE REPAIR ON 2 INCH CONTROLLING LINE BACKFILLED AND CLEANEDTHE AREA. JOB COMPLETE
201900890801 | 2019-06-11 | LEAD | 1124 | INDEPENDENCE | MARAIS | WILK | WM - LEAK BETWEEN SIDEWALK AND CURB INLET SERVICE LEAK INSIDE METER BOX METER UNDER WATER, CARS PARKING ON METER /** 1) MN: A258082 SN: 0054293, *TAP: SIZE: A LOC: 48 FEET FROM P LINE AT MARAIS, *MB: CODE: BFLM LOC: METER ON INDEPENDENCE 48 FT FROM PL MARAIS ****/ | 2019-06-24 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA ALSO EXCAVATED IN GUTTER BOTTOM + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE + REPLACED CHOKED 5/8 INCH METER AFTER SECOND REPAIR FOUND LEAK ON INLET REPLACED 3/4 INCH INLET FROM CURB TO METER BOX ***************OLD METER INFO************** METER:A415886 FAC:15481332 MAKE:HERSEY READ:237
201900890901 | 2019-06-11 | LEAD | 2730 | CLEVELAND AV |  | WILK | ML- METER LEAK MTR# A225681 ACCT# 150083-530973 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A194301 SN: 0046809, *TAP: SIZE: B LOC: 246 FEET FROM P LINE AT BROAD S, *MB: CODE: CF LOC: 240' P.L. S BROAD ****/ | 2019-06-24 | EXCAVATED 2 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WOTH RIVERSAND
201900891001 | 2019-06-11 | LEAD | 2443 | DESIRE | N DORGENOIS | WILK | ML- METER LEAK METER# A417971 ACCT# 158706-433875 INLET SERVICE LEAKING BEHIND CURB COCK INTO METER BOX /** 1) MN: A217661 SN: 0096345, *TAP: SIZE: A LOC: 274 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BDK5 LOC: FRONT 307'5'' FR. PL ROCHEBLAVE 9FT OUT PL 2FT IN ****/ | 2019-06-24 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA. JOB COMPLETE
201900895301 | 2019-06-12 | LEAD | 1329 | POLAND AV | N VILLERE | WOLK | MI- CONS ON METER PER INSPECTOR METER # B-040320 ACCT # 150100-727111 /** 1) MN: B027373 SN: 0125860, *TAP: SIZE: B LOC: 285 FEET FROM P LINE AT URQUHART, *MB: CODE: CEL1 LOC: 285'P L URQUHART ****/ | 2019-06-27 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900897201 | 2019-06-12 | LEAD | 2028 | ST CLAUDE AV |  | WILK | INSP L UDUEBOR STATES SERVICE HAS A BAD BLEEDER VALVE LEAK AND HE IS UNABLE TO REMOVE METER. PLEASE REPAIR AND REMOVE METER A434920 LOC 116305 INLET SERVICE LEAK IN METER BOX, NO METER IN BOX ***INSPC UDUEBOR REMOVED METER*** /** 1) MN: A297170 SN: 0073140, *TAP: SIZE: A LOC: 94 FEET FROM P LINE AT FRENCHMEN, *MB: CODE: BDKL LOC: ON ST CLAUDE 94FT FROM FRENCHMEN ****/ | 2019-06-21 | MADE 2 X 2 SIDE WALK CUT THAT WAS NEWLY PAVED AND REPLACED 5/8 INCH CURB COCK WITH NEW ONE METER WAS ALREADY REMOVED FROM LOCATION BACKFILLED AREA
201900897301 | 2019-06-12 | LEAD | 1801-03 | TOURO | N ROMAN | WILK | WM - LEAK IN THE STREET CHANGED RFOM 2014 N ROMAN INLET SERVICE LEAK IN STREET ON N ROMAN /** AT 1801: 1) MN: A132784 SN: 0067556, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT TOURO, *MB: CODE: BDHO LOC: ON N ROMAN 64' FROM PL OF TOURO ****/ | 2019-06-22 | EXCAVATED 4 X 8 ASPHALT STREET CUT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED AND CODLMILL
201900901001 | 2019-06-12 | LEAD | 2812 | N DORGENOIS | EADS | WMTLK | ML: METER LEAK METER# A390618 ACCT# 166148-476219 EXAMINE INLET/OUTLET SERVICE FOR LEAK IN MUDPLOT METER BOX UNDER WATER /** 1) MN: A147911 SN: 0106460, *TAP: SIZE: A LOC: 79 FEET FROM P LINE AT EADS, *MB: CODE: BDLM LOC: ON NO. DORGENOIS, 79' FROM P.L. EADS, 7.5' OUTSIDE ****/ | 2019-07-16 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND JOB COMPLETE
201900901501 | 2019-06-12 | LEAD | 819 | URSULINES AV | BOURBON | WILK | WM- LEAK BETWEEN SIDEWALK AND STREET LEAK BETWEEN CURVE AND STREET /** 1) MN: A311667 SN: 0017822, *TAP: SIZE: B LOC: 149 FEET FROM P LINE AT BOURBON, *MB: CODE: BE5 LOC: ON URSULINES 133 FT FROM PL BOURBON ****/ | 2019-08-13 | EXCAVATED IN CONCRETE SIDEWALK + MADE REPAIR ON 1 INCH INLET SERVICE LINE BACKFILLED + DRESED UP AREA
201900901901 | 2019-06-12 | LEAD | 1731 | ALVAR | N DERBIGNY | WMTBG | MI- RASIE METER TO GRADE ACCT# 154100-432556 METER# A432872 (PER CSM REMAINDER NOTES METER BURIED UNABLE TO READ 5/28/2019) ADJUST METER BOX TO PROPER GRADE /** 1) MN: A257576 SN: 0090294, *TAP: SIZE: A LOC: 256 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BDM1 LOC: ON ALVAR 234FT FROM P.L. N.DERBIGNY 9' OUTSIDE PL ****/ | 2019-07-02 | EXCAVATED IN MUD PLOT + RAISED 5/8 METER BOX TO GRADE BACKIFLLED + DRESSED UP AREA JOB COMPLETE
201900902301 | 2019-06-12 | LEAD | 2513 | REPUBLIC | N DORGENOIS | WILK | ML-METER LEAK METER#A434923 ACCT#307416-425829 INLET SERVICE LEAK IN GUTTER BOTTOM /** 1) MN: A278372 SN: 0074372, *TAP: SIZE: A LOC: 79 FEET FROM P LINE AT DORGENOIS NO., *MB: CODE: BD5 LOC: ON REPUBLIC, 79' FROM P.L. NO. DORGENOIS ****/ | 2019-06-19 | EXCAVATEDIN LIMESTONE GUTTER BOTTOM AND REPLACED 5/8 INCH CURB COCK WITH NEW ONE BACKFILLED AREA JOB COMPLETE
201900903101 | 2019-06-13 | LEAD | 5101 | N VILLERE | FORSTALL | WILK | INLET WATER SERVICE LEAK /** 1) MN: A257556 SN: 0106309, *TAP: SIZE: A LOC: 11 FEET FROM P LINE AT VILLERE N, *MB: CODE: DH2 LOC: ON FORSTALL 11FT FROM VILLERE 6FT OUTSIDE ****/ | 2019-06-12 | EXCAVATED 8 X 13 STREET CUT MADE REPAIR ON ABANDON INLET SERVICE IN FRONT OF VACANT LOT ALSO WHILE EXCAVATED FOUND SEWER PROBLEM UNABLE TO MAKE REPAIR DUE TO SEWER MAIN BEING UP USED BARRELS WITH FLAGS AROUND AREA TO MAKE AND ALSO DUMP 6 YDS OF RIVERSAND INFRONT OF CUT
201900903501 | 2019-06-13 | LEAD | 3801 | TOULOUSE |  | WOLK | ACCT# 213485-515526 MTR# C030505 CONSTANT FOUND ON METER, NO VISIBLE STW. /** 1) MN: C023714 SN: 0173842, *TAP: SIZE: C LOC: 96 FEET FROM P LINE AT TOULOUSE, *MB: CODE: CD LOC: ON SCOTT 96FT FROM TOULOUSE ** 2) MN: A326908 SN: 0000000, *TAP: SIZE: H LOC: 57 FEET FROM P LINE AT TOULOUSE, *MB: CODE: CD LOC: ON CORTEZ 57FT FROM TOULOUSE 7FT OUTSIDE ****/ | 2019-06-25 | EXCAVATEDIN MUD PLOT AND FOUND NO LEAK ON OUTLET FOR METER LOCATED ON S SCOTT REPLACED METER BOX CASING AND FOUND NO CONSTANT ON METER NO TAG ON METER
201900906101 | 2019-06-13 | LEAD | 2700 | ESPLANADE AV |  | WILK | ML-METER LEAK ACCT#101309-520769 METER#A417102 BLEEDER VALVE LEAKING @ CURB /** 1) MN: A240473 SN: 0027247, *TAP: SIZE: B LOC: 6 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: BDH7 LOC: ON CRETE,6' FROM U.P.L. ESPLANADE AVE. ****/ | 2019-06-27 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900908701 | 2019-06-13 | LEAD | 1958 | N PRIEUR | ST ANTHONY | WILK | MI-LEAK BETWEEN THE SIDEWALK AND THE STREET INLET SERVICE LEAK IN ASPHALT STREET FLOODING STREET /** 1) MN: B025317 SN: 0113345, *TAP: SIZE: B LOC: 139 FEET FROM P LINE AT ST ANTHONY, *MB: CODE: ADK7 LOC: ON N. PRIEUR, 139' FROM P.L. ST. ANTHONY, 9' OUT- ****/ | 2019-06-22 | EXCAVATED 4 X 10 ASPHALT STREET CUT FOUND LEAK ON 1 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900909601 | 2019-06-13 | LEAD | 5217 | ROYAL | EGANIA | WILK | *****************PICKUP***************** INLET SERVICE LEAK INSIDE METER BOX IN CONCRETE DRIVEWAY BAD CURBCOCK /** 1) MN: A318546 SN: 0059349, *TAP: SIZE: A LOC: 140 FEET FROM P LINE AT EGANIA, *MB: CODE: CFL1 LOC: ON ROYAL 121FT FROM USPL EGANIA ****/ | 2019-07-15 | EXCAVATED 2 X 4 CONCRETE DRIVEWAY FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201900909901 | 2019-06-13 | LEAD | 5428 | N ROMAN |  | WMTLK | ML- METER LEAK MTR# A395482 ACCT#151744-424081 EXAMINE INLET/OUTLET SERVICE FOR LEAK /** 1) MN: A351516 SN: 0138839, *TAP: SIZE: A LOC: 200 FEET FROM P LINE AT ANDRY, *MB: CODE: CD LOC: RES ON ROMAN 196FT FROM PL ANDRY 7FT OUT PL 2FT IN ****/ | 2019-07-15 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900911001 | 2019-06-14 | LEAD | 864 | ROOSEVELT PL | DUMAINE | WMBK | ML-METER LEAK ACCT#113553-514671 METER#A357228 **************J.GILLIAM @ 9:13AM**************** LOWER METER BOX BROKEN, BOX KEEP EXPANDING, FOUND OFF LEFT, CUSTOMER WAITING ON WATER /** 1) MN: A292655 SN: 0029128, *TAP: SIZE: A LOC: 4 FEET FROM P LINE AT ROOSEVELT PL, *MB: CODE: BFZ LOC: ON DUMAINE NEAR CARROLLTON INSIDE OF WALK ****/ | 2019-06-14 | EXCAVATED 4 X 4 MUD PLOT FOUND 5/8 INCH BOTTOM BROKEN REPLACED 5/8 INCH BOTTOM AND BACKFILLED JOB WITH RIVERSAND ALSO RAISE METER BOX UP TO GRADE
201900911201 | 2019-06-14 | LEAD | 2434 | GOV NICHOLLS | N ROCHEBLAVE | WILK | INLET SERVICE LEAK. LEAK IN ROADWAY. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/12/2019. /** 1) MN: A321696 SN: 0046624, *TAP: SIZE: A LOC: 36 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: CFL LOC: IN GARDEN 36' P.L. N ROCHEBLAVE ****/ | 2019-06-22 | EXCAVATED 12 X 12 STREET CUT MADE REPAIR ON INLET SERVICE AT WATER MAIN TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201900911601 | 2019-06-14 | LEAD | 6100 | N RAMPART |  | WILK | LOCATION: 170607 MTR# A 433805 INSP UDUEBOR STATES BLEEDER VALVE IS LEAKING. PLEASE REPAIR. INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A133612 SN: 0113190, *TAP: SIZE: A LOC: 6 FEET FROM P LINE AT RAMPART N, *MB: CODE: ADH5 LOC: ON TUPELO 6FT FROM PL RAMPART 7' OUTSIDE PL ****/ | 2019-08-01 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900912801 | 2019-06-14 | LEAD | 5920 | CONSTANCE | ELEONORE | WILK | MI: LEAK IN THE STREET EXAMINE INLET SERVICE FOR LEAK UNDERGROUND IN ASPHALT STREET /** 1) MN: B028615 SN: 0012548, *TAP: SIZE: B LOC: 156 FEET FROM P LINE AT ELEONORE ST, *MB: CODE: BEM LOC: ON CONSTANCE,156' FROM U.R.P.L. ELEONORE ****/ DOTTIE READY 6-19-19 EXP 7-9-19 | 2019-06-23 | REPLACED METER WASHERS TO STOP LEAK
201900913901 | 2019-06-14 | LEAD | 4644 | BACCICH | LOMBARD | WILK | ML-METER LEAK ACCT 156770-479143 METER# A313076 INLET SERVICE LEAK IN MUD PLOT /** 1) MN: A283489 SN: 0093952, *TAP: SIZE: A LOC: 316 FEET FROM P LINE AT LOMBARD, *MB: CODE: ADKM LOC: ON BACCICH, 316.5' FROM P.L. LOMBARD, 7' OUTSIDE ****/ | 2019-06-18 | EXCAVATED IN A 4X4 MUDPLOT BY HAND FOUND TEE LEAKING ON LEAD LINE ON INLET. REPAIR LEAD LINE WITH STOP COCK AN NEW TEE RUN 6FT OF 3/4 WATER TUBING TO METER BOX RAISE METER BOX TO GRADE BACKFILL AND DRESS.
201900915401 | 2019-06-14 | LEAD | 924 | DESLONDE | N RAMPART | WILK | PP- POOR PRESSURE ACCT# 189735-715004 MTR# A425585 INLET SERVICE LEAK IN DRIVEWAY FLOODING THE DRIVEWAY CAUSING POOR PRESSURE NO OUTSIDE FAUCET B 1ST AM /** 1) MN: A324925 SN: 0147277, *TAP: SIZE: C LOC: 164 FEET FROM P LINE AT BURGUNDY, *MB: CODE: ADK6 LOC: ON DESLONDE, 164' FROM P.L. BURGUNDY, 7' OUTSIDE ** 2) MN: A144339 SN: 0147277, *TAP: SIZE: C LOC: 164 FEET FROM P LINE AT BURGUNDY, *MB: CODE: ADK6 LOC: ON DESLONDE, 165' FROM P.L. BURGUNDY, 7' OUTSIDE THERE ARE 2 MORE NOT LISTED. ****/ | 2019-06-17 | EXAMINED JOB AT ABOVE LOCATION FOUND LEAK ON 3/4 INCH OUTLET BROKEN HANDWHEEL REPLACE HANDWHEEL JOB COMPLETE
201900916101 | 2019-06-15 | LEAD | 2735 | GEN PERSHING | CLARA | WMLK | MI- LEAK IN THE STREET LEAK ON WATER MAIN IN THE STREET, GETTING OFF IN THE DCB /** 1) MN: A239739 SN: 0012324, *TAP: SIZE: B LOC: 66 FEET FROM P LINE AT CLARA, *MB: CODE: CFLM LOC: ON GEN PERSHING 67FT FROM CLARA ****/ | 2019-06-23 | MADE CUT IN STREET FOUND INLET SERVICE LEAKING. REPAIR SERVICE STOP THE LEAK BACKFILLED CUT WITH SAND AND LIMESTONE.(SOC 5FT. X 5 FT. CONCRETE BASE)
201900916501 | 2019-06-15 | LEAD | 2331-33 | N VILLERE | SPAIN | WILK | MI: LEAK IN THE STREET INLET SERVICE LEAK IN THE STREET WITH A LIL WATER BUBBLING UP IN THE STREET /** AT 2331: 1) MN: A260261 SN: 0017519, *TAP: SIZE: B LOC: 13 FEET FROM P LINE AT SPAIN, *MB: CODE: BEK LOC: ON N VILLERE 63 FT FROM PL SPAIN ****/ | 2019-06-22 | EXCAVATED 4 X 10 ASPHALT STREET CUT FOUND LEAK 3/4 INCH INLET SERVICE TO MADE REPAIR
201900918101 | 2019-06-17 | LEAD | 812 | ROOSEVELT PL |  | WMTLK | LOCATION ID-113580 MTR-A115251 MTR LEAK/MTR BOX OVER FLOWING /** 1) MN: A303118 SN: 0029249, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: BDL LOC: 102FT FROM LRPL ORLEANS ****/ | 2019-06-25 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH BOTTOM AND CURB COCK BACKFILLED AREA
201900918401 | 2019-06-17 | LEAD | 3053 | ORLEANS AV |  | WMTLK | LOCATION ID-218112 MTR-A319093 LEAK AROUND MTR/AREA FLOODED /** 1) MN: A319093 SN: 0054578, *TAP: SIZE: A LOC: 69 FEET FROM P LINE AT LOPEZ N, *MB: CODE: CDKM LOC: ON ORLEANS AVE.,69.5' FROM L.R.P.L. NO. LOPEZ ****/ | 2019-06-27 | REPLACED 5/8 INCH HANDWHEEEL + GUTS IN METER BOX ALSO REPLACED BROKEN 5/8 INCH METER BOX CASING
201900919101 | 2019-06-17 | LEAD | 1525 | DESIRE |  | WILK | ML METER LEAK ACCOUNT # 184347-429947 METER #A402944 INLET SERVICE LEAKING UNDERGROUND ON NEWLY RENOVATED SERVICE /** 1) MN: A282733 SN: 0078414, *TAP: SIZE: __ LOC: 198 FEET FROM P LINE AT NO. ROBERTSON, *MB: CODE: BEN2 LOC: ON DESIRE, 199' FROM P.L. NO. ROBERTSON, 3' OUT- ****/ | 2019-06-22 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 3/4 INCH INLET SERVICE COOPER LINE MADE REPAIR ON INLET RAISEMETER BOX UP TO GRADE BACKFILLED JOB WITH RIVERSAND AND CODLMILL
201900920201 | 2019-06-17 | LEAD | 2532 | D"ABADIE |  | WILK | WM - LEAK ON THE SIDEWALK INLET SERVICE LEAK IN METER BOX /** 1) MN: A318918 SN: 0076466, *TAP: SIZE: B LOC: 42 FEET FROM P LINE AT ROUSSELIN DR, *MB: CODE: ADLN LOC: 42FT FROM PL ROUSSELIN ON D ABADIE ****/ | 2019-07-01 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900922002 | 2019-06-27 | LEAD/PLASTIC | 2511 | S CARROLLTON AV | NELSON | WILK | WILK WATER LEAK - INLET SERVICE (TRUCK 594 EXCAVATED IN STREET OVER 4"WATER MAIN TO REPAIR LEAK.(DOTTIE C-6/19/19;R-6/24/19;EXP.7/14/19) /** 1) MN: E006348 SN: 0072521, *TAP: SIZE: G LOC: 18 FEET FROM P LINE AT CARROLLTON AVE S, *MB: CODE: ADHP LOC: IN MH ON NELSON 11FT FROM LPL S CARROLLTON ****/ | 2019-06-28 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 1"ABANDON CORP.COCK LEAKING.REPLACED 1"CORP COCK AND 4FT. OF 1"TUBING.ALSO REPLACED 10FT. OF 10" PVC PIPE FOR MDL.(SOC 7FT. X 10FT. CONCRETE BASE)
201900922102 | 2019-07-02 | LEAD | 2901 | BRUXELLES | AGRICULTURE | WILK | INLET SERVICE IN MUD PLOT GETTING OFF IN DCB LEAK ON AGRUICULTURE EXCAVATED IN MUD PLOT UNABLE TO LOCATION LEAK REFER TO ECHOLOGICS /** 1) MN: A308794 SN: 0078048, *TAP: SIZE: C LOC: 2 FEET FROM P LINE AT AGRICULTURE, *MB: CODE: ADK2 LOC: 25FT FROM PL AGRICULTURE ****/ | 2019-07-03 | EXCAVATED OVER A 4 INCH WATER TO FIND A 1 INCH CORP COCK LEAKING MADE THE WATER CLOSURE AND REPLACED WITH A 1 INCH COCK TO MAKE THE REPAIR SERVICE WAS FOR A FLUSH TANK
201900923301 | 2019-06-18 | LEAD | 322 | N DORGENOIS | CONTI | WILK | WATER INLET SERVICE LEAK /** 1) MN: C013018 SN: 0113697, *TAP: SIZE: C LOC: 186 FEET FROM P LINE AT BIENVILLE, *MB: CODE: CDM LOC: ON NO. DORGENOIS, 186' FROM P.L. BIENVILLE, 8' ****/ | 2019-06-16 | EXCAVATED 4 X 8 CONCRETE BASE STREET CUT FOUND LEAK 1 INCH ABANDON INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL. JOB COMPLETE
201900923601 | 2019-06-18 | LEAD | 3238 | BIENVILLE | N RENDON | WILK | WATER INLET SERVICE LEAK /** 1) MN: A291497 SN: 0047805, *TAP: SIZE: A LOC: 32 FEET FROM P LINE AT BIENVILLE, *MB: CODE: CDH LOC: ON NO. RENDON,32.8' FROM U.R.P.L. BIENVILLE ****/ | 2019-06-16 | EXCAVATED 7 X 6 STREET CUT MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND COLDMILL
201900926201 | 2019-06-18 | LEAD | 1720 | INDEPENDENCE |  | WMTLK | ML- METER LEAK AAT# 150390-489426 MTR# A264886 EXAMINE INLET & OUTLET SERVICE FOR A LEAK BETWEEN GUTTER BOTTOM & SIDEWALK. METER IN LOW LYING AREA UNDER WATER /** 1) MN: A264886 SN: 0092931, *TAP: SIZE: A LOC: 162 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: ADK LOC: 160'PL N DERBIGNY ON INDEPENDENCE ****/ | 2019-06-26 | MADE 8 X 8 CUT IN BLACK TOP STREET AND RENEWED 3/4 INCH INLET SERVICE FROM MAIN TO METER BOX ALSO RELOCATED METER FROM GUTTER BOTTOM TO SIDEWALK MADE 4 X 4 SIDEWAKJ CUT CUSTOMER HAS GALVENIZED PIPE THAT FULL OF CORRSION AND HAS PRESSURE PROBLEM BACKFILLED AREA
201900927401 | 2019-06-18 | LEAD | 1934 | PIETY |  | WILK | ML- METER LEAK ACCT# 161913-432498 METER # A397649 BAD CURB COCK INSIDE METER BOX IN CONCRETE DRIVEWAY /** 1) MN: A236758 SN: 0100645, *TAP: SIZE: A LOC: 238 FEET FROM P LINE AT PRIEUR N, *MB: CODE: AE5 LOC: 238FT FROM P.L. N. PRIEUR 9' OUTSIDE ****/ | 2019-07-11 | MADE 4 X 4 CUT IN DOUBLE LAYER DRIVEWAY AND REPLACED 3/4 INCH CURB COCK WITH NEW ONE BACKFILLED AREA
201900928801 | 2019-06-19 | LEAD | 4721 | N VILLERE | JOURDAN AV | WILK | WATER INLET SERVICE LEAK /** 1) MN: C021285 SN: 0135362, *TAP: SIZE: C LOC: 4 FEET FROM P LINE AT JOUDAN, *MB: CODE: BDK3 LOC: ON NO. VILLERE ST. 4' FROM DIV. P.L. OF JOURDAN AV ** 2) MN: SN: 0135362, *TAP: SIZE: C LOC: 119 FEET FROM P LINE AT JOURDAN AVE, *MB: CODE: BDL LOC: RES 122FT FROM P.L. JOURDAN ON VILLERE THERE IS 1 MORE NOT LISTED. ****/ | 2019-06-18 | MADE 6 X 6 CUT IN BLACK TOP STREET AND MADE REPAIR ON 3/4 INCH INLET SERVICE FOR ABANDON LOT BACKFILLED AREA
201900929401 | 2019-06-19 | LEAD | 930 | TOURO |  | WILK | LOCATIONID#122509-485990 METER#A329349 BLEEDER LEAK /** 1) MN: A228526 SN: 0041152, *TAP: SIZE: A LOC: 68 FEET FROM P LINE AT RAMPART N, *MB: CODE: BEK4 LOC: ON TOURO,68' FROM U.R.P.L. NO. RAMPART ****/ | 2019-07-05 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA
201900929501 | 2019-06-19 | LEAD | 1758 | N RAMPART |  | WMTLK | LOCATIONID#109825-485800 METER#A324886 LEAK INSIDE METERBOX /** 1) MN: A324886 SN: 0024776, *TAP: SIZE: A LOC: 38 FEET FROM P LINE AT RAMPART N, *MB: CODE: AFHN LOC: SIDE ON ST ANTHONY 38' P.L. N RAMPART ****/ | 2019-07-02 | MADE 2 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX WITH NEW ONE BACKFILLED AREA
201900929601 | 2019-06-19 | LEAD | 1417 | KERLEREC |  | WMTLK | LOCATIONID#114196-725842 METER#A419042 LEAK INSIDE METERBOX /** 1) MN: A221084 SN: 0043428, *TAP: SIZE: C LOC: 113 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: AFLM LOC: ON KERLEREC 113' FROM LRPL N ROBERTSON ****/ | 2019-07-03 | EXCAVATED IN CONCRETE SIDEWALK + BOTTOM OF STEPS RELOCATED METER BOX FROM STEP AREA TO SIDEWALK BACKFILLED + DRESED UP AREA
201900929701 | 2019-06-19 | LEAD | 1425 | ST CLAUDE AV |  | WMTLK | LOCATIONID#115431-486311 METER#A312156 LEAK INSIDE METERBOX /** 1) MN: A312156 SN: 0044778, *TAP: SIZE: A LOC: 83 FEET FROM P LINE AT KERLEREC, *MB: CODE: CEM3 LOC: ST CLAUDE AVE 83FT FROM PL OF KERLEREC ****/ | 2019-07-01 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900929801 | 2019-06-19 | LEAD | 710 | MAZANT |  | WOLK | LOCATION# 131983 CUSTOMER# 483214 METER# A257666 INSPECTOR DID AN OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION AT METER AROUND CURB-COCK......PLEASE REPAIR /** 1) MN: A257666 SN: 0051049, *TAP: SIZE: A LOC: 74 FEET FROM P LINE AT ROYAL, *MB: CODE: CELN LOC: ON MAZANT 77FT FROM USPL ROYAL ****/ | 2019-06-28 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK WITH NEW ONE BACKFILLED AREA. JOB COMPLETE
201900930001 | 2019-06-19 | LEAD | 1511 | MARAIS |  | WMTLK | LOCATIONID#117209-486325 METER#A400835 LEAK INSIDE METERBOX /** 1) MN: A296992 SN: 0053334, *TAP: SIZE: A LOC: 80 FEET FROM P LINE AT COLUMBUS, *MB: CODE: CFLM LOC: 80' P.L. COLUMBUS ****/ | 2019-07-01 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900930201 | 2019-06-19 | LEAD | 1513 | N VILLERE |  | WMTLK | LOCATIONID#118982-723576 METER#A411408 LEAK INSIDE METERBOX /** 1) MN: A324981 SN: 0043284, *TAP: SIZE: A LOC: 99 FEET FROM P LINE AT COLUMBUS, *MB: CODE: AFON LOC: ON NO. VILLERE,99' FROM P.L. COLUMBUS ****/ | 2019-07-01 | REPLACED 5/8 INCH METER + WASHERS AT ABOVE LOCATION **************OLD METER INFO************ METER:A411408 FAC:14117170 MAKE:HERSEY READ:0
201900930301 | 2019-06-19 | LEAD | 1518 | N TONTI |  | WMTLK | LOCATIONID#145467-488879 METER#A421907 LEAK INSIDE METERBOX /** 1) MN: A155000 SN: 0076919, *TAP: SIZE: A LOC: 167 FEET FROM P LINE AT COLUMBUS, *MB: CODE: BD LOC: ON N TONTI ST 166' FROM PL COLUMBUS ST ****/ | 2019-07-01 | EXCAVATED IN MUD PLOT + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900930901 | 2019-06-19 | LEAD | 3009 | LAFITTE | N GAYOSO | WMTLK | ML- METER LEAK ACCT# 146152-724374 MTR# A428515 /** 1) MN: A245282 SN: 0078146, *TAP: SIZE: B LOC: 58 FEET FROM P LINE AT GAYOSO N, *MB: CODE: CDLN LOC: 58FT. FRM P.L. N GAYOSO ****/ | 2019-07-01 | EXCAVATED TO FIND A 3/4 INCH OUTLET SERVICE LEAKING REPAIRED WHERE THE LEAK WAS FOUND THE WATER WAS GETTING AWAY UNDER GROUND
201900931001 | 2019-06-19 | LEAD | 2816 | NEW ORLEANS |  | WILK | LOCATION# 218820 CUSTOMER# 495848 METER# A424722 INSPECTOR DID AN OUTSIDE INSPECTION FOUND LEAK INSIDE METER-BOX AT CURB-COCK.........PLEASE REPAIR /** 1) MN: A322364 SN: 0102766, *TAP: SIZE: B LOC: 153 FEET FROM P LINE AT INDUSTRY, *MB: CODE: ADLN LOC: 153FT FROM PL INDUSTRY 8' OUTSIDE PL ****/ | 2019-07-05 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO MAKE THE REPAIR
201900933201 | 2019-06-19 | LEAD | 3201 | LAFITTE | N LOPEZ | WMTLK | WATER METER LEAK. LEAK IN THE REAR OF THE HOUSE ON 3201 LAFITTE - ACTUALLY ON N LOPEZ IN THE GRASS. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/17/2019. /** 1) MN: A312341 SN: 0068220, *TAP: SIZE: A LOC: 40 FEET FROM P LINE AT LAFITTE AVE, *MB: CODE: BD4L LOC: ON N LOPEZ ST 48' FROM PL LAFITTE AVE ****/ | 2019-07-01 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO MAKE THE REPAIR
201900933901 | 2019-06-19 | LEAD | 2261 | MARAIS | MANDEVILLE | WMTLK | WM - LEAK IN THE STREET EXAMINE INLET/OUTLET SERVICE FOR A LEAK, UNABLE TO PUMP DOWN /** 1) MN: A295604 SN: 0025218, *TAP: SIZE: A LOC: 133 FEET FROM P LINE AT MANDEVILLE, *MB: CODE: BD LOC: METER ON MARAIS 132.5 FT FROM PL MANDEVILLE ****/ | 2019-07-11 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900934401 | 2019-06-19 | LEAD/PLASTIC | 412 | CALHOUN | ANNUNCIATION | WILK | WM- LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET FLOODING CURB /** 1) MN: A337528 SN: 0054109, *TAP: SIZE: A LOC: 67 FEET FROM P LINE AT ANNUNCIATION, *MB: CODE: AEKO LOC: INSIDE SIDEWALK RIVER PL ON CALHOUN 69 FT FROM PL ****/ DOTTIE READY 7-5-19 EXP 7-25-19 | 2019-07-03 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND TAIL PEICE LEAKING AT 12" WATER MAIN.REPLACED 3/4 TAIL PEICE AND 8FT. OF 3/4 TUBING.(SOC 8FT. X 8 FT .ASPHALT F/D)
201900934901 | 2019-06-20 | LEAD | 1773 | N BROAD |  | WMTBG | ACCOUNT# 130288-491749 METER# A295783 METER AND METER CASING IS BELOW GRADE /** 1) MN: A295783 SN: 0059836, *TAP: SIZE: A LOC: 80 FEET FROM P LINE AT O REILLY, *MB: CODE: CD LOC: ON NO. BROAD,81.5' FROM P.L. O'REILLY ****/ | 2019-07-01 | ARRIVED AT ABOVE LOCATION TO FIND A 5/8 INCH METER BELOW GRADE EXCAVATED AND RAISED METER TO GRADE
201900935301 | 2019-06-20 | LEAD | 2018 | N TONTI | ANNETTE | WMTLK | ACCT# 167553-495221 METER# A371075 INSPECTOR FOUND LEAK AT OR AROUND METER BOX /** 1) MN: A303028 SN: 0108920, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT ANNETTE, *MB: CODE: BEK LOC: ON N TONTI 134FT FROM P.L. OF ANNETTE 8FT OUTSIDE ****/ | 2019-07-08 | EXAMINED AND PUMPED METER BOX DOWN AND REPLACED 5/8 INCH WASHERS ON INLET AND OUTLET TO STOP LEAK METER LOCATED IN DRIVEWAY
201900938501 | 2019-06-20 | LEAD | 2112 | CHARTRES |  | WILK | MI LEAK IN THE STREET INLET SERVICE LEAK @ THE MAIN IN THE STREET ***NOT A DUPLICATE PER K GRIFFIN*** /** 1) MN: A236060 SN: 0056472, *TAP: SIZE: C LOC: 93 FEET FROM P LINE AT FRENCHMEN, *MB: CODE: __ LOC: ON CHARTRES 93FT FROM PL FRENCHMEN 5' OUTSIDE PL 4 ****/ | 2019-08-17 | EXCAVATED 4 X 8 CONCRETE BASE STREET CUT FOUND LEAK ON 1 INCH SERVICE AT WATER MAIN MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL. JOB COMPLETE
201900938601 | 2019-06-20 | LEAD | 923 | ST ROCH AV | N RAMPART | WMTLK | ML: METER LEAK ACCT#121828-732190 MTR#A258607 EXAMINE INLET & OUTLET SERVICE FOR A LEAK WITH CONSTANT REGISTRATION /** 1) MN: A258607 SN: 0052388, *TAP: SIZE: A LOC: 117 FEET FROM P LINE AT RAMPART N, *MB: CODE: CFM LOC: ON ST. ROCH AVE.,117' FROM L.R.P.L. NO. RAMPART ****/ | 2019-07-05 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO MAKE THE REPAIR
201900940101 | 2019-06-20 | LEAD | 1531 | FRANCE |  | WILK | LOCATION: 162917 MTR# A 436574 INSP UDUEBOR STATES BLEEDER VALVE IS LEAKING BAD. LEFT OFF, CUSTOMER WAS NOT HOME. PLEASE REPAIR ASAP INLET SERVICE LEAK IN MUD PLOT /** 1) MN: A240287 SN: 0102254, *TAP: SIZE: A LOC: 231 FEET FROM P LINE AT ROBERTSON N, *MB: CODE: CEL1 LOC: 229'FROM P L NO ROBERTSON ON FRANCE 7FT OUTSD PL ****/ | 2019-07-08 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND COLDMILL CUSTOMER HAS LEAK ON INLET AT WATERMIAN POOR PRESSURE ON INLET LEFT ONR SAFETY CONE ON JOB SITE IN SIDEWALK
201900941101 | 2019-06-20 | LEAD | 1213 | LESSEPS | MARAIS | WMTBG | MI-RAISE TO GRADE METER#A427389 /** 1) MN: A129725 SN: 0078900, *TAP: SIZE: B LOC: 118 FEET FROM P LINE AT MARAIS, *MB: CODE: ADL1 LOC: 118'FROM P L MARAIS ON LESSEPS ****/ | 2019-07-11 | EXCAVATED IN GUTTER BOTTOM AND RAISED METER TO GRADE BACKFILLED AREA JOB COMPLETE
201900942501 | 2019-06-21 | LEAD | 813 | N ROMAN | ST ANN | WMTLK | WATER METER LEAK. LEAK ON THE SHOULDER OF ROADWAY. LEAK IS VISIBLE. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/18/2019. /** 1) MN: A345889 SN: 0048346, *TAP: SIZE: B LOC: 114 FEET FROM P LINE AT ST ANN, *MB: CODE: BDT LOC: METRS CROSSD XXXX BET DUMAINE/ST ANN 117' P/L ****/ | 2019-06-27 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA (NO METER) JOB COMPLETE
201900943701 | 2019-06-21 | LEAD | 2122 | N BROAD |  | WILK | ML- METER LEAK METER #A409106 ACCT #152944-490381 INLET SERVICE LEAK IN METER BOX. METER IN HEART OF TREE ROOTS /** 1) MN: A324704 SN: 0065953, *TAP: SIZE: C LOC: 173 FEET FROM P LINE AT DUELS, *MB: CODE: BDK LOC: ON NO. BROAD, 173' FROM P.L. DUELS,10' OUTSIDE PL ****/ | 2019-07-03 | EXAMINED AREA AT ABOVE LOCATION + FOUND NO LEAK OR PROBLEM
201900944301 | 2019-06-21 | LEAD | 2027 | N TONTI | ST ANTHONY | WMTBG | WATER METER BELOW GRADE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-06-13 | EXCAVATED 2 X 4 MUD PLOT IN GUTTER BOTTOM RAISE METER BOX UP TO GRADE AT ABOVE LOCATION
201900944401 | 2019-06-21 | LEAD | 2883 | ANNETTE | FLORIDA AV | WILK | WATER INLET SERVICE LEAK /** 1) MN: A301745 SN: 0099134, *TAP: SIZE: A LOC: 171 FEET FROM P LINE AT INDUSTRY, *MB: CODE: CDL LOC: ON ANNETTE 171' FROM PL INDUSTRY 8' OUTSIDE PL ****/ | 2019-06-19 | EXCAVATED 6 X 4 GUTTER BOTTOM RAISED METER BOX TO GRADE AND MADE REPAIR ON INLET SERVICE LINE BACKFILLED AND CLEANED THE AREA
201900944501 | 2019-06-21 | LEAD | 1952 | FLORIDA AV | ANNETTE | WILK | INLET SERVICE LEAK /** 1) MN: SN: 0115990, *TAP: SIZE: B LOC: 69 FEET FROM P LINE AT FLORIDA AVE, *MB: CODE: BDL LOC: ON ANNETTE 65' P/L FLORIDA AV 10' OUTSIDE 2' IN- ** 2) MN: A344993 SN: 0115990, *TAP: SIZE: B LOC: 69 FEET FROM P LINE AT FLORIDA AVE, *MB: CODE: BDL LOC: ON ANNETTE 66' P/L FLORIDA AV 8' OUTSIDE 2' INSIDE THERE ARE 6 MORE NOT LISTED. ****/ | 2019-06-19 | EXCAVATED 3 X 2 GUTTER BOTTOM REPLACE METER COCK TO STOP LEAK BACKFILL AND CLEANED THE AREA
201900944601 | 2019-06-21 | LEAD | 1909 | DUELS | ALLEN | WILK | INLET SERVICE LEAK /** 1) MN: A304063 SN: 0077643, *TAP: SIZE: A LOC: 81 FEET FROM P LINE AT ALLEN, *MB: CODE: BDL LOC: ON DUELS 80' FROM PL OF ALLEN ****/ | 2019-06-19 | EXCAVATED 2 X 2 MUD PLOT REPLACE METER COCK TO STOP LEAK ****NO METER AT THIS LOCATION***
201900945601 | 2019-06-21 | LEAD | 905 | ROYAL | DUMAINE | WILK | WM- LEAK BETWEEN THE STREET AND SIDEWALK INLET SERVICE LEAK IN THE STREET UNDERGROUND /** 1) MN: B024139 SN: 0029221, *TAP: SIZE: B LOC: 68 FEET FROM P LINE AT DUMAINE, *MB: CODE: BF LOC: ON ROYAL 68FT FROM DUMAINE ****/ | 2019-08-16 | EXCAVATED IN ASPHALT STREET + REPLACED 3/4 INCH BEND ADAPTER COMPACTED BACKFILL + DRESSEDUP AREA
201900946001 | 2019-06-21 | LEAD | 1317 | TUPELO | URQUHART | WMTLK | ML- METER LEAK METER #A194890 ACCT # 165111-422538 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER UNDER WATER /** 1) MN: A194890 SN: 0105139, *TAP: SIZE: A LOC: 105 FEET FROM P LINE AT URQUHART, *MB: CODE: BDL LOC: ON TUPELO, 105' FROMP.L. URQUHART, 6.5' OUTSIDE ****/ | 2019-07-15 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900946701 | 2019-06-21 | LEAD/PLASTIC | 2411 | BROADWAY | MOBILE | WILK | ML- METER LEAK ACCT# 142777-541121 METER# A377357 INLET SERVICE LEAK AT CURB FLOODING CURB GETTING OFF INTO DRAIN CATCH BASIN /** 1) MN: A315361 SN: 0074092, *TAP: SIZE: A LOC: 93 FEET FROM P LINE AT MOBILE, *MB: CODE: CDN1 LOC: METER ON BROADWAY 77.5 FT FROM PL MOBILE ****/ DOTTIE READY 6-27-19 EXP 7-17-19 | 2019-06-28 | ARRIVED ON THE JOB AND FOUND INLET SERVICE WAS LEAKING THE CREW DUG UP THE JOB AND MADE.REPAIR ON 5/3 INLET SERVICE.
201900948801 | 2019-06-22 | LEAD | 6214 | N ROBERTSON | TRICOU | WILK | WATER INLET SERVICE LEAK /** 1) MN: A316117 SN: 0141565, *TAP: SIZE: B LOC: 132 FEET FROM P LINE AT ST MAURICE, *MB: CODE: ADKO LOC: 2 APTS ON N ROBERTSON 132' PL ST MAURICE XX ****/ | 2019-06-21 | EXCAVATED 4 X 3 MUDPLOT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED TEH AREA
201900948901 | 2019-06-22 | LEAD | 1920 | ANNETTE | N PRIEUR | WOLK | WATER OUTLET SERVICE LEAK /** 1) MN: A321169 SN: 0047274, *TAP: SIZE: A LOC: 143 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CDL1 LOC: ON ANNETTE 144FT FROM PL OF N JOHNSON ****/ | 2019-06-21 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900949001 | 2019-06-22 | LEAD | 2727 | N ROBERTSON | ST FERDINAND DR | WMTBG | WATER METER BELOW GRADE /** 1) MN: A330914 SN: 0057468, *TAP: SIZE: A LOC: 40 FEET FROM P LINE AT ST FERDINAND, *MB: CODE: BDL1 LOC: METER ON N ROBERTSON 37.5 FT FROM PL ST FERDINAND ****/ | 2019-06-21 | REPLACE UPPER METER BOX CASING AT ABOVE LOCATION JOB COMPLETE
201900949201 | 2019-06-22 | LEAD | 2939 | ESPLANADE AV | LEPAGE | WILK | WATER INLET SERVICE LEAK /** 1) MN: B029749 SN: 0046415, *TAP: SIZE: B LOC: 10 FEET FROM P LINE AT GAYOSO N LRPL, *MB: CODE: ADH2 LOC: 10' FROM LRPL GAYOSA ****/ | 2019-06-22 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 3/4 INCH INLET SERVICE MADE REPAIR ON NLET BACKFILLED WITH RIVERSAND
201900949601 | 2019-06-23 | LEAD | 4816 | ANNUNCIATION | BORDEAUX | WLPR | WLPR WATER 'LOW PRESSURE /** 1) MN: A290564 SN: 0047760, *TAP: SIZE: A LOC: 121 FEET FROM P LINE AT BORDEAUX, *MB: CODE: CDM1 LOC: OPP WINDOW AT 16 CURB NEXT TO WALK 122' P.L. ****/ | 2019-06-22 | MADE CUT OVER 6"WATER MAIN AND FOUND 5/8 LEAD LINE LEAKING AT THE SWEAT JOINT,MADE REPAIR AND BACKFILLED TO GRADE.(SOC 8FT. X 8 FT. ASPHALT F/D)
201900949901 | 2019-06-23 | LEAD | 815 | PAULINE | DAUPHINE | WILK | WM-LEAK IN BETWEEN STREET AND SIDEWALK CHANGED FROM 816 PAULINE INLET SERVICE LEAK IN BRICK SIDEWALK /** 1) MN: A319849 SN: 0082315, *TAP: SIZE: A LOC: 114 FEET FROM P LINE AT DAUPHINE, *MB: CODE: BFKL LOC: 113FT FROM SPL DAUPHINE ON PAULINE ****/ | 2019-07-05 | EXCAVATED IN 3 X 3 BRICK SIDEWALK FOUND 3/4 INCH LEAD LINE LEAKING + REPAIR IT OLD METER INFO: A319849 FACT: 53300793 MAKE: SENSUS READ: 5714
201900952401 | 2019-06-24 | LEAD | 900 | TAFT PL | DUMAINE | WVLK | WATER VALVE LEAK. LEAK IN ROADWAY - NOT VISIBLE. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/20/2019. /** 1) MN: A330374 SN: 0072079, *TAP: SIZE: A LOC: 72 FEET FROM P LINE AT TAFT, *MB: CODE: CD LOC: ON DUMAINE 72FT FROM TAFT 3FT OUTSIDE ****/ | 2019-07-01 | REPLACED PACKING + GLANDS ON 6 INCH VALVE IN MANHOLE AT ABOVE LOCATION
201900955801 | 2019-06-24 | LEAD/PLASTIC | 2423 | AMELIA | FRERET | WMRE | INSP S BIBBINS STATES HE IS UNABLE TO SET METER, CASING IS SITTING DIRECTLY ON OUTLET. PLEASE REPAIR AND SET 5/8 METER. LOC 307130 LOCATE, MARK & SET 5/8 METER ***HOUSE UNDER RENOVATIONS*** /** 1) MN: A126386 SN: 0051062, *TAP: SIZE: A LOC: 159 FEET FROM P LINE AT HOWARD AVE, *MB: CODE: CDN1 LOC: 159FT FROM SPL HOWARD ON AMELIA ****/ DOTTIE READY 6-27-19 EXP 7-17-19 | 2019-07-01 | ARRIVED ON THE JOB SITE ,MADE ALL REPAIRS ALSO USED METER BOX COMPLETE AND RESET 5/8 WATER METER AND MARK AND LOCATE.
201900957301 | 2019-06-24 | LEAD | 3112 | DUMAINE | N LOPEZ | WILK | MI-LEAK AT CURB INLET SERVICE LEAK IN THE STREET /** 1) MN: A310501 SN: 0030157, *TAP: SIZE: B LOC: 108 FEET FROM P LINE AT LOPEZ N, *MB: CODE: CD LOC: ON DUMAINE 108FT FROM SLPL. OF N LOPEZ ****/ | 2019-07-08 | EXCAVATED IN ASPHALT STREET + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE COMPACTED BACKFILL + DRESSED UP AREA
201900957702 | 2019-07-07 | LEAD | 1122 | MANDEVILLE |  | WILK | UNABLE TO SET METER NO WATER COMING FROM MAIN PLEASE REPAIR AND SET 5/8 INCH METER EXAMINED JOB AT ABOVE LOCATION TO MAKE REPAIR AND WAS UNABLE TO DUE JOB BECAUSE CAR ON SITE NO ONE IN BLOCK KNOW WHO THE OWNER GREY SUBURN NORTH CORLINA PLATE JOB REFER BACK TO ZONE 4 FOR REAPIR 07/8/19 CAR NOW REMOVED PER SR#12880233 (AJR) /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-07-16 | EXCAVATED IN CONCRETE STREET + SIDEWALK +MADE REPAIR ON 3/4 INCH INLET SERVICE LINERESTORING WATER BACK TO ABOVE LOCATION COMPACTEED BACKFILL + DRESSED UP AREA ALSO SET 5/8 INCH METER
201900958701 | 2019-06-24 | LEAD | 1727 | PIETY |  | WOLK | CUSTOMER IS HOME WAITING ON WATER NEED OUTLET SIDE REPAIRED A-436299 OUTLET SERVICE LEAK INSIDE METERBOX BROKEN HANDWHEEL FOUND METER OFF LEFT METER OFF HOUSE VACANT /** 1) MN: A148748 SN: 0102990, *TAP: SIZE: A LOC: 161 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BE5 LOC: ON PIETY, 161' FROM P.L. NO. DERBIGNY, 7' OUTSIDE ****/ | 2019-07-24 | EXCAVATED 3 X 2 SIDEWALK CUT MADE REPAIR ON OUTLET SERVICE LINE ALSO REPLACED HANDWHEEL BACKFILLED AND CLEANED THE AREA
201900959501 | 2019-06-25 | LEAD | 732 | ST PETER |  | WOLK | LOCATION# 108848 CUSTOMER# 732228 METER# A407578 INSPECTOR DID AN OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION ON METER, CAN'T DETERMINE WHERE LEAK IS COMING FROM UNABLE TO PERFORM NO S&W VALVE......PLEASE REPAIR /** 1) MN: A266699 SN: 0010101, *TAP: SIZE: A LOC: 71 FEET FROM P LINE AT BOURBON, *MB: CODE: BENL LOC: 71FT FROM LRPL BOURBON ****/ | 2019-08-16 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900959601 | 2019-06-25 | LEAD | 2221 | MARAIS | MARIGNY | WMTLK | ML- METER LEAK MTR.# A-424416 ACCT #117143-481267 /** 1) MN: A118858 SN: 0024105, *TAP: SIZE: A LOC: 112 FEET FROM P LINE AT MARAIS, *MB: CODE: BF7 LOC: 112' P.L. MARIGNY ****/ | 2019-07-11 | REPLACED 5/8 INCH WASHERS IN METER BOX
201900959701 | 2019-06-25 | LEAD | 5403 | N ROCHEBLAVE |  | WMTLK | LOCATIONID#168203-421580 METER#A381745 LEAK INSIDE METERBOX /** 1) MN: A321385 SN: 0130105, *TAP: SIZE: A LOC: 25 FEET FROM P LINE AT ANDRY, *MB: CODE: CDL LOC: RES ON ROCHEBLAVE 25FT PL ANDRY 7' OUTSIDE 3' ****/ | 2019-07-19 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201900962301 | 2019-06-25 | LEAD | 2838 | HIAWATHA | PEOPLES AV | WOLK | ML- METER LEAK METER # A 412396 ACCT# 139227 - 735483 **********C ROSS 12:30********** **********CUSTOMER OUT OF WATER********** OUTLET SERVICE LEAK IN METER BOX ON HANDWHEEL IN THE MUD PLOT. FOUND METER OFF LEFT METER OFF /** 1) MN: A232968 SN: 0085845, *TAP: SIZE: A LOC: 214 FEET FROM P LINE AT PEOPLES AVE, *MB: CODE: ADL3 LOC: ON HIAWATHA 213FT FROM PEOPLES ****/ | 2019-06-25 | HANDDUG IN MUDPLOT FOUND LEAK ON 3/4 HANDWHEEL OUTLET. RENEWED METERBOX COCK AND HANDWHEEL. LEAD ON INLET. METER BOX COMPLETE. BACKFILLED. AND DRESSED WITH RIVERSAND.
201900962601 | 2019-06-25 | LEAD | 1824 | LOUISA |  | WMTLK | BAD BLEEDER VALVE LEAK. PLEASE REPAIR LOC 302411 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-07-09 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVCIE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201900964001 | 2019-06-25 | LEAD/PLASTIC | 2500 | 1ST | FRERET | WILK | WILK WATER LEAK-INLET SERVICE (LEAK IS ON FRERET ST. MARKED IN WHITE PAINT.) /** 1) MN: A248456 SN: 0022610, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT FIRST, *MB: CODE: ADHK LOC: SIDE FENCE ON FRERET 74.5 FT FROM PL 1ST, 9.5 FT ****/ | 2019-06-29 | CUT OVER WATER MAIN AND MADE REPAIR ON SERVICWE.BACKFILLED CUT WITH SAND AND LIMESTONES.(SOC 6FT. X 6 FT .CONCRETE BASE STREET)
201900964301 | 2019-06-25 | LEAD/PLASTIC | 2300 BLK | 1ST | LASALLE | WILK | WILK WATER LEAK-INLET SERVICE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-06-30 | MADE CUT OVER WATER MAIN.REPAIR INLET SERVICE BACKFILED WITH SAND AND LIMESTONES.(SOC6FT. X 6 FT .CONCRETE )
201900966501 | 2019-06-25 | LEAD | 2215 | AGRICULTURE | MARIGNY | WILK | REPAIR LEAK IN STREET /** 1) MN: SN: 0096110, *TAP: SIZE: C LOC: 167 FEET FROM P LINE AT ELYSIAN FIELDS AVE, *MB: CODE: BDKL LOC: ON AGRICULTURE 167FT FROM ELY FIELDS 8FT OUTSIDE ****/ | 2019-06-25 | FOUND LEAK ON ABANDONED SERVICE INLET SERVICE. LEAD PLACED 3/4 STOPCOCK ON LEAD SERVICE.
201900966601 | 2019-06-25 | LEAD | 2303 | ALVAR | N TONTI | WMLK | WM-LEAK ON THE SIDEWALK WATER MAIN LEAKING IN ASPHALT STREET IN FRONT OF 2300 ALVAR /** 1) MN: A302045 SN: 0094603, *TAP: SIZE: A LOC: 37 FEET FROM P LINE AT TONTI N, *MB: CODE: ADN LOC: 36FT FROM PL N. TONTI 7' OUTSIDE PL 2' INSIDE CURB ****/ | 2019-07-05 | EXCAVATED IN 6 X 6 STREET CUT + MADE REPAIR ON WATERMAIN + 3/4 INCH LEAD LINE BACKFILLED + CLEAN AREA
201900967701 | 2019-06-26 | LEAD | 1401 | ST BERNARD AV |  | WILK | LOCATION: 123667 METER REMOVED 6/25/19 INSP UDUEBOR STATES INLET SERVICE NEED REPAIRS, BAD CURB COCK. PLEASE MAKE REPAIRS ONLY INLET SERVICE LEAK IN BOX IN SIDEWALK /** 1) MN: 000000 SN: 0043606, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT VILLERE N, *MB: CODE: AEK2 LOC: ON ST. BERNARD AVE.,54' FROM L.S.P.L. NO. VILLERE ****/ | 2019-07-11 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA NO METER
201900969301 | 2019-06-26 | LEAD | 439 | ROYAL | CONTI | WILK | PP-POOR PRESSURE METER#C008430 ACCT#155099-527389 *****************1ST AM****************** NLET SERVICE LEAK IN BOX CAUSING POOR PRESSURE , FOUND 15PSI @ FAUCET /** 1) MN: C008430 SN: 0004805, *TAP: SIZE: C LOC: 270 FEET FROM P LINE AT ST LOUIS, *MB: CODE: AEN3 LOC: ON ROYAL 27' FROM PL ST LOUIS 6.5' OUTSIDE PL 1.5' ****/ | 2019-07-02 | EXCAVATED TO FIND A 1 INCH CURB COCK LEAKING REMOVED AND REPALCED WITH A 1 INCH CURB COCK TO MAKE THE REPAIR
201900970801 | 2019-06-26 | LEAD | 3034 | FORTIN |  | WILK | ML---- METER LEAK METER# A240841 ACCT# 175300-567060 INLET SERVICE LEAK IN MUDPLOT IN BOX /** 1) MN: A240841 SN: 0054867, *TAP: SIZE: A LOC: 237 FEET FROM P LINE AT LOPEZ N, *MB: CODE: CDLM LOC: ON FORTIN 237FT FROM PL LOPEZ ****/ | 2019-07-10 | EXCAVATED IN GUTTER BOTTOM IN HEAVY RAIN AND REPLACED 5/8 INCH CURB COCK BACKFILLED AREA IN RAIN LEFT 3 INCH CONES ON SITE AREA WAS FLOODED DUE TO RAIN
201900971301 | 2019-06-26 | LEAD | 1342 | ESPLANADE AV |  | WILK | INSP L UDUEBOR STATES SERVICE HAS A BAD BLEEDER VALVE LEAK. PLEASE REPAIR LOC 107067 INLET SERVICE LEAK IN BOX IN SIDEWALK /** 1) MN: A322987 SN: 0008730, *TAP: SIZE: A LOC: 84 FEET FROM P LINE AT ESPLANADE AVE, *MB: CODE: BFHM LOC: CENTER OF WALK SIDE ST NEAR GATE MIDDLE OF SDWL ****/ | 2019-07-03 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH COCK BACKFILLED + DRESSED UP AREA
201900972401 | 2019-06-26 | LEAD | 4743 | SANDALWOOD | HAMMOND | WOLK | ML-METER LEAK METER#B029734 OUTLET SERVICE LEAK WITH CONSTANT REGISTRATION /** 1) MN: B024254 SN: 0128195, *TAP: SIZE: B LOC: 139 FEET FROM P LINE AT HAMMOND, *MB: CODE: ADM4 LOC: ON SANDALWOOD 139FT FROM HAMMOND 8FT OUTSIDE ****/ | 2019-06-28 | EXCAVATED DOWN ON OUTLET SERVICE. FOUND LEAD AND HANDWHEEL WAS LEAKING, MADE REPAIRS BY REPLACING WASHERS. HANDWHEEL. BACKFILLED.
201900974601 | 2019-06-27 | LEAD | 1803 | LAHARPE |  | WILK | ML- METER LEAK ACCT# 307512-730343 MTR# A439434 INLET SERVICE LEAK IN MUDPLOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-07-19 | EXCAVATED TO FIND A LEAK ON A 5/8 INCH LEAD INLET SERVICE REPAIRED WHER THE LEAK WAS FOUND MADE A 3 X3 MUD CUT BACKFILLED AND DRESS UP CUT
201900975401 | 2019-06-27 | LEAD | 2012 | ANNETTE | N JOHNSON | WILK | INLET SERVICE LEAK /** 1) MN: B022745 SN: 0064814, *TAP: SIZE: B LOC: 115 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CDK LOC: ON ANNETTE,115.4' FROM P.L. NO. JOHNSON,3' FROM ****/ | 2019-06-26 | EXCAVATED IN LIMESTONE GUTTER BOTTOM + REPLACE 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201900977301 | 2019-06-27 | LEAD | 1201 | MAZANT | MARAIS | WMTLK | ***********************PICKUP*********************** EXAMINE INLET AND OUTLET SERVICE FOR LEAK INSIDE MANHOLE ON MARAIS, GETTING OFF IN DCB 07/23/18 CUST STATED LEAK HAS GOTTEN WORSE (KSW) /** 1) MN: D005509 SN: 0063436, *TAP: SIZE: __ LOC: 90 FEET FROM P LINE AT MARAIS, *MB: CODE: OOO LOC: 90' P.L. MARAIS ****/ | 2019-07-31 | MADE REPAIR ON 1 INCH INLET SERVICE INSIDE OF MANHOLE
201900977701 | 2019-06-27 | LEAD | 2507 | ANDRY | N DORGENOIS | WMTLK | ML- METER LEAK ACCT# 178759-732335 METER# A424069 EXAMINE INLET AND OUTLET SERVICE FOR LEAK , SIDEWALK FLOODED /** 1) MN: 000000 SN: 0133743, *TAP: SIZE: A LOC: 55 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: AD24 LOC: RES ON ANDRY 55FT PL N DORGENOIS 6' OUTSIDE ****/ | 2019-07-17 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION IN MOSQUITOES BED JOBH WELL DONE
201900981101 | 2019-06-28 | LEAD | 3119 | ROYAL |  | WMTLK | LOCATIONID#125305-427412 METER#A387761 METERBOX OVERFLOWING /** 1) MN: A192062 SN: 0059508, *TAP: SIZE: A LOC: 130 FEET FROM P LINE AT CLOUET, *MB: CODE: ADN LOC: ON ROYAL,128.3' FROM L.S.P.L. CLOUET ****/ | 2019-07-18 | EXCAVATED TO FIND A LEAK ON A 3/4 INCH LEAD LINE REPAIRED WHERE THE LEAK WAS FOUND MADE A 3X3 CON SIDE WALK. BACKFILLED AND DRESS UP CUT. JOB COMPLETE
201900981301 | 2019-06-28 | LEAD | 618 | LOUISA DR |  | WMTLK | LOCATIONID#125490-427419 METER#A116994 LEAK INSIDE METERBOX /** 1) MN: A116994 SN: 0052467, *TAP: SIZE: A LOC: 137 FEET FROM P LINE AT CHARTRES, *MB: CODE: CEM LOC: 136FT FROM USPL CHARTRES ****/ | 2019-07-11 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIRS ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL JOB COMPLETE
201900981801 | 2019-06-28 | LEAD | 927 | CLOUET |  | WMTLK | LOCATIONID#123180-427379 METER#A293287 METERBOX OVERFLOWING /** 1) MN: A293287 SN: 0049094, *TAP: SIZE: A LOC: 99 FEET FROM P LINE AT RAMPART N, *MB: CODE: AE27 LOC: 100FT FROM LRPL RAMPART ON CLOUET ****/ | 2019-07-11 | EXCAVATED 2 X 4 CONCRETE DRIVEWAY FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201900981901 | 2019-06-28 | LEAD | 918 | PIETY |  | WMTLK | LOCATIONID#114252-427235 METER#A395035 LEAK INSIDE METERBOX /** 1) MN: 000000 SN: 0016895, *TAP: SIZE: A LOC: 142 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CELM LOC: 142FT FROM USPL BURGUNDY ON PIETY ****/ | 2019-07-18 | REPLACE BROKEN 5/8 INCH HANDWHEEL AT ABOVE LOCATION
201900982001 | 2019-06-28 | LEAD | 1007 | PIETY |  | WMTLK | LOCATIONID#137562-428017 METER#A211772 LEAK INSIDE METERBOX /** 1) MN: A211772 SN: 0068436, *TAP: SIZE: B LOC: 36 FEET FROM P LINE AT RAMPART S, *MB: CODE: BEK5 LOC: 36FT FROM PL RAMPART ON S RAMPART ****/ | 2019-07-18 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND CODLMILL
201900982101 | 2019-06-28 | LEAD | 1025 | PIETY |  | WMTLK | LOCATIONID#131581-703846 METER#A381368 LEAK INSIDE METERBOX /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-07-18 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSNAD AND COLDMILL
201900982201 | 2019-06-28 | LEAD | 1045 | CLOUET |  | WMTLK | LOCATIONID#121962-427351 METER#A121962 LEAK INSIDE METERBOX /** 1) MN: A131106 SN: 0039912, *TAP: SIZE: A LOC: 52 FEET FROM P LINE AT ST CLAUDE AVE, *MB: CODE: CFL7 LOC: ON CLOUET,52' FROM L.R.P.L. ST. CLAUDE AVE. ****/ | 2019-07-16 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201900982401 | 2019-06-28 | LEAD | 3918 | ROYAL |  | WMTLK | LOCATIONID#146800-428430 METER#A124443 LEAK INSIDE METERBOX /** 1) MN: A124443 SN: 0119718, *TAP: SIZE: A LOC: 157 FEET FROM P LINE AT ALVAR, *MB: CODE: CELM LOC: ON ROYAL 157FT FROM PL ALVAR ****/ | 2019-07-11 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK WITH NEW ONE BACKFILLED AREA. JOB COMPLETE
201900982601 | 2019-06-28 | LEAD | 821 | ALVAR |  | WMTLK | LOCATIONID#128144-707657 METER#A403037 LEAK INSIDE METERBOX /** 1) MN: A311280 SN: 0054937, *TAP: SIZE: A LOC: 147 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CDLM LOC: ON ALVAR 146FT FROM LRPL BURGUNDY ****/ | 2019-07-11 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK WITH NEW ONE BACKFILLED AREA
201900984001 | 2019-06-28 | LEAD | 800 | VALENCE |  | WILK | ML METER LEAK ACCOUNT #109302-557251 METER A273202 WILK SERVICVE LEAK BEHIND CURB COCK FLOODING GRASSY AREA & GUTTER BOTTOM /** 1) MN: A273202 SN: 0010587, *TAP: SIZE: B LOC: 80 FEET FROM P LINE AT VALENCE, *MB: CODE: ADHO LOC: FIRST METER SIDE ST ON CONSTANCE ST 79' P.L. ****/ DOTTIE READY 8-23-19 EXP 9-12-19 | 2019-08-25 | ARRIVED ON THE JOB AND FOUND BAD CURB COCK THE CREW DUG UP THE JOB CHANGE CURB COCK OUT WITH NEW CURB COCK OUT WITH NEW CURB COCK AND STOP THE LEAK.(4FT. X 4 FT .MUD-PLOT)
201900985201 | 2019-06-28 | LEAD | 2318 | TENNESSEE | N TONTI | WILK | WM: LEAK ON SIDE WALK INLET ON ABANDON SERVICE ON FRONT VACANT LOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-07-22 | EXCAVATED IN MUD PLOT + MADE REPAIR ON ABANDONED 3/4 INCH INLET SERVICE LINE BACKFILLED + DRSESED UP AREA
201900988701 | 2019-06-28 | LEAD | 3154 | TOULOUSE |  | WMTLK | ML--METER LEAK ACCOUNT#135932-520302 METER#A355567 EXAMINE INLET/OUTLET SERVICE FOR LEAK METER BOX UNDER WATER /** 1) MN: A276732 SN: 0066555, *TAP: SIZE: B LOC: 132 FEET FROM P LINE AT LOPEZ N, *MB: CODE: ADKM LOC: AT 3154 - 132' P.L. N LOPEZ ****/ | 2019-07-18 | EXCAVATED IN MUD PLOT + REPLACED BROKEN 5/8 INCH METER BOX BOTTOM THAT WAS CASING LEAK ALSO RASIED IT TO GRADE BACKFILLED + DRESSEED UP AREA
201900990301 | 2019-06-29 | LEAD | 4102 | DAUPHINE |  | WLPR | PP-POOR PRESSURE MTR#A271394 EXAMINE INLET SERVICE FOR POOR PRESSURE /** 1) MN: A271394 SN: 0054381, *TAP: SIZE: A LOC: 26 FEET FROM P LINE AT MAZANT, *MB: CODE: ADE LOC: ON DAUPHINE 27FT FROM LRPL MAZANT ****/ | 2019-07-11 | EXAMINED JOB AND REMOVED METER AND FOUND GOOD PRESSURE ON INLET REPLACED 5/8 INCH WASHERS AND SET METER BACK IN BOX JOB COMPLETE
201900993801 | 2019-07-01 | LEAD | 2332 | PAUGER | N DERBIGNY | WILK | LOCATION#130807-493838. METER#A383164. THE METER HAS A LEAK AT THE CURB COCK SIDE OF THE METER, /** 1) MN: A273199 SN: 0068147, *TAP: SIZE: A LOC: 84 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: AEL1 LOC: ON BOURBON ST 82.5' FROM RPL N DERBIGNY ****/ | 2019-07-15 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX
201900994301 | 2019-07-01 | LEAD | 1921 | PAINTERS |  | WMRE | LOCATION: 301559 INSP UDUEBOR STATES METER BOX IS BURIED. PLEASE LOCATE, RAISE AND CHANGE METER# A426346 LOCATE, RAISE TO GRADE & CHANGE METER /** 1) MN: A333889 SN: 0054967, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT PRIEUR N, *MB: CODE: AFL LOC: ON PAINTER 134FT FROM PRIEUR N ****/ | 2019-07-15 | EXCAVATED ACROSS PROPERTY AT ABOVE LOCATION + LOCATED METER BOX RAISED 5/8 INCH METER TO GRADE + REPLACED 5/8 INCH METER BACKFILLED + DRESSED UP AREA *************OLD METER INFO********** METER:A426346 FAC:16311358 MAKE:HERSEY READ:125
201900994901 | 2019-07-01 | LEAD | 2153 | N ROCHEBLAVE |  | WMTLK | LOCATION: 186621 INSP UDUEBOR STATES METER BOX UNDER WATER, AREA FLOODED. PLEASE REPAIR LEAK AND CHANGE METER# A432757 EXAMINE INLET & OUTLET SERVICE FOR A LEAK METER BOX IN LOW LYING AREA /** 1) MN: A288339 SN: 0141740, *TAP: SIZE: B LOC: 147 FEET FROM P LINE AT TOURO, *MB: CODE: ADK LOC: 147FT FROM PL TOURO 8' OUTSIDE PL ON N ROCHEBLAVE ****/ | 2019-07-15 | EXCAVATED IN MUD PLOT + REPLACE 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA ALSO REPLACED 5/8 INCH METER OLD METER INFO: A432757 FACT: 181377 MAKE: HERSEY READ: 485
201900995301 | 2019-07-01 | LEAD | 3305 | MARAIS |  | WMRE | LOCATION: 304277 INSP UDUEBOR STATES METER SERVICE IS BURIED. HOUSE UNDER RENOVATIONS & VACANT. PLEASE LOCATE, RAISE AND SET A 5/8 METER. (METER SIZE PER HOUSE CONN) LOCATE, RAISE TO GRADE & SET METER, ALSO OUTLET TIE IN /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-07-02 | EXCAVATED TO FIND A 5/8 INCH BOTTOM DID SO AND RAISE TO GRADE ALSO SET A 5/8 INCH METER
201900995501 | 2019-07-01 | LEAD/PLASTIC | 5747 | PAULINE DR |  | WILK | ML- METER LEAK METER# A 415424 ACCT#176220-458428. INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A303799 SN: 0120343, *TAP: SIZE: B LOC: 50 FEET FROM P LINE AT PRENTISS AVE, *MB: CODE: CDM1 LOC: MTR ON PAULINE 50FT FRM PL PRENTISS 7FT OUTSD PL ****/ | 2019-07-02 | EXAMINED JOB FOUND LEAK ON LEAD OUTLET. RENEWED OUTLET WITH 6FT PLASTI NEW HANDWHEEL 3/4 AND 3/4 C AND I. HANDUG ON OUTLET AND INLET. FOUND LEAD ON OUTLET AS WELL. BACKFILLED AND DRESSED WITH SND AND COAL MILL.
201900999401 | 2019-07-02 | LEAD | 1730 | BIENVILLE |  | WILK | LOCATION ID-221362 MTR-A429252 CURB COCK BROKEN /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-07-15 | EXCAVATED IN MUD PLOT AND REPLACED 5/8 INCH CURB COCK WITH ONE BACKFILLED AREA
201901000401 | 2019-07-02 | LEAD | 1515 | TUPELO | N ROBERTSON | WMTLK | WATER METER LEAK. LEAK IS BETWEEN SIDEWALK AND CURB, VISIBLE. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 6/27/2019. /** 1) MN: A317789 SN: 0095305, *TAP: SIZE: A LOC: 98 FEET FROM P LINE AT NO. ROBERTSON, *MB: CODE: BDLM LOC: ON TUPELO, 98' FROM P.L. NO. ROBERTSON, 8' OUTSIDE ****/ | 2019-07-17 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND ALSO REPLACED CHOKE 5/8 INCH METER AT ABOVE LOCATION ************OLD METER INFO********** OLD METER:A433653 FAC:18138692 MAKE:HERSEY READ:3
201901000701 | 2019-07-02 | LEAD | 2413 | LAMANCHE | N ROCHEBLAVE | WILK | MI- LEAK IN SIDEWALK FLOODING STREET INLET SERVICE LEAK ON ABANDON SERVICE IN THE MUD PLOT /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-07-17 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON ABANDON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201901001601 | 2019-07-02 | LEAD | 4217 | N CLAIBORNE AV |  | WMTLK | ML METER LEAK ACCOUNT #172381-433092 METER#A218258 EXAMINE INLET & OUTLET SERVICE FOR A LEAK CARS ROLLING OVER METER BOX /** 1) MN: A198750 SN: 0115653, *TAP: SIZE: A LOC: 156 FEET FROM P LINE AT FRANCE, *MB: CODE: CDL2 LOC: ON N CLAIBORNE AV 125' P/L/ FRANCE 7' OUTSIDE ****/ | 2019-08-12 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201901002501 | 2019-07-02 | LEAD | 3719 | N RAMPART |  | WMTLK | LOCATIONID#112208-428156 METER#A278575 LEAK INSIDE METERBOX /** 1) MN: A324712 SN: 0134036, *TAP: SIZE: A LOC: 53 FEET FROM P LINE AT PAULINE, *MB: CODE: CELM LOC: ON NO. RAMPART,52' FROM U.S.P.L. PAULINE ****/ | 2019-07-18 | EXCAVATED IN CONCRETE SIDEWALK +REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSEED UP AREA
201901002601 | 2019-07-02 | LEAD | 4124 | N RAMPART |  | WILK | LOCATIONID#129746-723311 METER#A394578 BLEEDER LEAK /** 1) MN: SN: 0058545, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT FRANCE RD, *MB: CODE: AE LOC: 60FT PL FRANCE RD 6' OUTSIDE 2' INSIDE CURB ****/ | 2019-07-18 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201901004101 | 2019-07-02 | LEAD | 2415 | MUSIC |  | WILK | LOCATION: 308000 INSP UDUEBOR STATES INLET SERVICE NEED REPAIRS, NO CURB COCK IN BOX. PLEASE REPAIR AND SET A 5/8 METER. CUSTOMER WILL BE MOVING IN SOON. INLET SERVICE LEAK NO CURB COCK IN METER BOX /** 1) MN: A226517 SN: 0108236, *TAP: SIZE: A LOC: 100 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BDM1 LOC: 100FT FROM PL ROCHEBLAVE MTR ON MUSIC 8FT OUTSIDE ****/ | 2019-07-15 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE ALSO SET 5/8 INCH METER BACKFILLED + DRESSED UP AREA
201901004701 | 2019-07-02 | LEAD | 4527 | MARAIS | KENTUCKY | WOLK | ML-METER LEAK ACCT#210183-431521 METER#A433754 CHECK FOR LEAK @ PROPERTY LINE CONSTANT REG ON METER /** 1) MN: A275477 SN: 0170956, *TAP: SIZE: B LOC: 17 FEET FROM P LINE AT KENTUCKY, *MB: CODE: BMDL LOC: ON MARAIS 19FT. FROM DIV. PL KENTUKY 9FT OUTSIDE ****/ | 2019-07-19 | EXSCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO MAKE THE REPAIR MADE A 3 X3 MADE CUT BACKFILLED AND DRESS UP CUT
201901004901 | 2019-07-02 | LEAD | 1628 | GORDON | N CLAIBORNE AV | WILK | ML: METER LEAK ACCT#160551-713278 MTR#A417832 INLET SERVICE LEAK INSIDE METER BOX BAD CURB COCK IN CONCRETE DRIVEWAY /** 1) MN: A112803 SN: 0133913, *TAP: SIZE: A LOC: 263 FEET FROM P LINE AT CLAIBORNE AVE S, *MB: CODE: BDKL LOC: RES ON GORDON 263' FROM PL CLAIBORNE AVE 7' OUTSID ****/ | 2019-07-11 | EXCAVAVTED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201901005301 | 2019-07-02 | LEAD | 720 | EGANIA | DAUPHINE | WILK | ML-METER LEAK METER#A430260 ACCT#128029-424832 INLET SERVICE LEAK INSIDE METER BOX BAD CURB COCK /** 1) MN: A216546 SN: 0054729, *TAP: SIZE: A LOC: 123 FEET FROM P LINE AT DAUPHINE, *MB: CODE: BEK2 LOC: ON EGANIA,122FT FROM URPL DAUPHINE ****/ | 2019-07-11 | EXCAVATED IN CONCRETE SIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201901005801 | 2019-07-03 | LEAD | 2015 | ANDRY |  | WOLK | ML METERLEAK MTR#A377613 LOC/CUST#212454-726161 CONS REG ON METER. /** 1) MN: A154835 SN: 0130144, *TAP: SIZE: B LOC: 8 FEET FROM P LINE AT N JOHNSON, *MB: CODE: CD LOC: ON ANDRY 7FT FROM DPL OF N JOHNSON 7FT OUTSIDE PL ****/ | 2019-07-17 | EXAMINE JOB AT ABOVE LOCATION FOUND NO CONSTANT REG ON METER
201901009701 | 2019-07-03 | LEAD | 4721 | N VILLERE | JOURDAN AV | WMBK | MI-METER BOX CASING BROKEN REPLACE BROKEN METER BOX CASING /** 1) MN: C021285 SN: 0135362, *TAP: SIZE: C LOC: 4 FEET FROM P LINE AT JOUDAN, *MB: CODE: BDK3 LOC: ON NO. VILLERE ST. 4' FROM DIV. P.L. OF JOURDAN AV ** 2) MN: SN: 0135362, *TAP: SIZE: C LOC: 119 FEET FROM P LINE AT JOURDAN AVE, *MB: CODE: BDL LOC: RES 122FT FROM P.L. JOURDAN ON VILLERE THERE IS 1 MORE NOT LISTED. ****/ | 2019-08-13 | REPLACED UPPER METER BOX CASING AT ABOVE LOCATION JOB COMPLETE
201901011501 | 2019-07-04 | LEAD | 700 | DELERY |  | WILK | WM-LEAK BETWEEN STREET AND THE SIDEWALK INLET SERVICE LEAK CAUSING METER BOX TO OVERFLOW IN GRASS AREA, LEAK IS ON ROYAL /** 1) MN: A208924 SN: 0058903, *TAP: SIZE: A LOC: 51 FEET FROM P LINE AT DELERY, *MB: CODE: CDH6 LOC: ON ROYAL,51.5' FROM U.S.P.L. DELERY ****/ | 2019-07-24 | EXCAVATED 3 X 2 MUD PLOT REPALCED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA JOB COMPLETE
201901012301 | 2019-07-05 | LEAD | 2100 | BURGUNDY | FRENCHMEN | WOLK | ACCT# 107764-426650 METER# A150971 INSPECTOR FOUND CONSTANT REGISTRATION ON METER /** 1) MN: A150971 SN: 0012426, *TAP: SIZE: B LOC: 49 FEET FROM P LINE AT BURGUNDY, *MB: CODE: BEKO LOC: ON FRENCHMEN 49' RPL BURGUNDY ****/ | 2019-07-23 | REMOVED BRICKS EXCAVATED IN MUD PLOT AND REPLACED BAD CURB COCK FOUND CONSTRANT ON METER DUE TO OPEN PIPE ON EMPTY LOT LEFT METER OFF INSIDEMETER BOX TO STOP CONSTRANT
201901012801 | 2019-07-05 | LEAD | 616 | ANDRY | CHARTRES | WMTLK | WATER METER LEAK. LEAK BETWEEN SIDEWALK AND ROADWAY. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 7/2/2019. /** 1) MN: A315397 SN: 0117171, *TAP: SIZE: A LOC: 149 FEET FROM P LINE AT CHARTRES, *MB: CODE: BDL2 LOC: 149FT PL CHARTRES 8' OUTSIDE ****/ | 2019-07-22 | EXCAVATED IN MUD PLOT WITH HEAVY RAIN AND REPLACED CURB COCK BACKFILLED AREA WITH HEAVY DOWN POURS. JOB COMPLETE
201901014301 | 2019-07-05 | LEAD/PLASTIC | 137 | 30TH | PONTCHARTRAIN BL | WILK | MI-LEAK IN THE STREET INLET SERVICE LEAK IN AN ASPHALT STREET /** 1) MN: B019564 SN: 0127853, *TAP: SIZE: B LOC: 307 FEET FROM P LINE AT PONTCHARTRAIN BLVD, *MB: CODE: ADK3 LOC: 308FT P/L PONTCHARTRAIN BL 8' OUTSIDE ****/ | 2019-07-22 | MADE A 4 X 5 ASPHALT STREET EXCAVATED AND MADE REPAIRS ON A 6 X 3/4' WATER MAIN. LEAD ON THE INLET PLASTIC ON THE OUTLET (JOB REFERRED)
201901015001 | 2019-07-05 | LEAD | 3019 | BANKS | S SALCEDO | WMTLK | ML- METER LEAK ACCT# 107653-531132 MTR# A275262 EXAMINE INLET & OUTLET SERVICE FOR A LEAK INSIDE METER BOX IN MUD PLOT /** 1) MN: A336785 SN: 0018168, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT SALCEDO S, *MB: CODE: ADK4 LOC: ON BANKS 133FT FROM PL OF SALCEDO S ****/ | 2019-07-23 | EXAMINED JOB AND PUMPED METER DOWN AND FOUND WASHERS LEAKING ON INLET REPLACED WASHERS ON INLET AND OUTLET
201901019401 | 2019-07-07 | LEAD | 2217 | FELICIANA | N MIRO | WILK | WATER INLET SERVICE LEAK /** 1) MN: A253630 SN: 0102914, *TAP: SIZE: A LOC: 150 FEET FROM P LINE AT MIRO N, *MB: CODE: AEL1 LOC: ON FELICIANA, 150' FROM P.L. NO. MIRO, 5' OUTSIDE ****/ | 2019-07-05 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO MAKE THE REPAIR
201901020801 | 2019-07-08 | LEAD | 717 | CONTI |  | WOLK | ML METERLEAK MTR#E004607 LOC/CUST#191618-600153 CONS REG ON METER. /** 1) MN: E004607 SN: 0004505, *TAP: SIZE: E LOC: 155 FEET FROM P LINE AT ROYAL, *MB: CODE: ADR LOC: ON CONTI 159' FRM ROYAL IN MH IN STREET ** 2) MN: D004638 SN: 0004505, *TAP: SIZE: D LOC: 145 FEET FROM P LINE AT ROYAL, *MB: CODE: BE6 LOC: ON CONTI 145FT FR PL ROYAL ****/ | 2019-07-22 | EXAMINE JOB AT ABOVE LOCATION FOUND NO CONSTANT REG ON 1 INCH METER IN MANHOLE METER BELONGS TO (HOTEL LEMARAIS)
201901021301 | 2019-07-08 | LEAD | 5200 | DAUPHINE |  | WMTBG | ACCOUNT# 134982-432275 METER# A400853 METER BURIED UNDER ROCK AND DIRT, NEED TO LOCATE AND RAISE TO GRADE PROPERTY OCCUPIED /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-07-24 | EXCAVATED 8 X 4 MUD PLOT TO LOCATE METER RAISED METER BOX UP TO GRADE BACKFILLED AND CLEANED THE AREA
201901021401 | 2019-07-08 | LEAD | 3914 | MARAIS |  | WILK | MI- LEAK IN SIDEWALK AREA FLOODING INLET SERVICE LEAK IN LOWLINE AREA, METER UNDER WATER /** 1) MN: A296538 SN: 0114138, *TAP: SIZE: A LOC: 93 FEET FROM P LINE AT ALVAR, *MB: CODE: BDL1 LOC: ON MARAIS, 92.5' FROM P.L. ALVAR ****/ | 2019-07-23 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INLET SERVICE MADE REPAIR ON INLET AND RAISE METER BOX UP TO GRADE LEFT ONE SAFTY CONE IN HOLE
201901023301 | 2019-07-08 | LEAD | 720 | LAMANCHE | ROYAL | WMBK | MI-MISSING METER COVER MISSING METER BOX CASING AND COVER IN MUDPLOT /** 1) MN: A250982 SN: 0102183, *TAP: SIZE: A LOC: 180 FEET FROM P LINE AT ROYAL, *MB: CODE: BD LOC: ON LAMANCHE, 182' FROM P.L. ROYAL, 9' OUTSIDE P.L. ****/ | 2019-07-24 | EXCAVATED 2 X 2 MUD PLOT AROUND METER BOX SET ONE METER BOX CASING ON METER BOTTOM BACKFILLED AND CLEANED THE AREA
201901025101 | 2019-07-08 | LEAD | 2550 | JASMINE |  | WILK | METER LEAK INLET SERVICE LEAK INSIDE METER BOX BAD CURBCOCK /** 1) MN: A314265 SN: 0086224, *TAP: SIZE: A LOC: 411 FEET FROM P LINE AT IRIS, *MB: CODE: ADK2 LOC: 411' P.L. IRIS ****/ | 2019-07-11 | MADE A 2X2 CUT IN DRIVEWAY. EXCAVATED DOWN ON INLET SERVICE. FOUND LEAD AND CURB COCK WAS LEAKING .A MADE REPAIRS BY REPLACING COCK WASHERS. BACKFILLED.
201901025701 | 2019-07-08 | LEAD | 3815 | D"HEMECOURT | S CORTEZ | WMTLK | MI- LEAK BETWEEN THE SIDEWALK IN THE STREET *******FLOODING AREA*********** EXAMINE INLET/OUTLET SERVICE FOR LEAK IN METER BOX GETTING OFF INTO DRAIN CATCH BASIN UNABLE TO PUMP OUT /** 1) MN: A257702 SN: 0071178, *TAP: SIZE: A LOC: 157 FEET FROM P LINE AT CORTEZ SO, *MB: CODE: ADK LOC: ON D'HEMECOURT, 157' FROM S.P.L. SO. CORTEZ ****/ DOTTIE READY 7-12-19 EXP 8-1-19 | 2019-07-20 | EXCAVTED IN GUTTER BOTTOM OVER INLET SERVICE CHANGED 5/8 METER BOX COCK AND REPAIR LEAK ON 3/4 LEAD. JOB COMPLETE
201901026201 | 2019-07-08 | LEAD | 5303 | BURGUNDY | EGANIA | WOLK | MI- PLEAS SET A 5"8 METER PER SUPVS (TREPANIER) ACCT#206704-447444 HANDWHEEL MISSING UNABLE TO SET METER SET 5/8 METER /** 1) MN: A259085 SN: 0101270, *TAP: SIZE: B LOC: 28 FEET FROM P LINE AT BURGUNDY, *MB: CODE: __ LOC: ON EGANIA 27FT FROM PL BURGUNDY ****/ | 2019-07-09 | REPLACE 5/8 INCH HANDWHEEL AND SET A 5/8 WATER METER AT ABOVE LOCATION
201901031601 | 2019-07-10 | LEAD | 625 | BURGUNDY |  | WMTLK | ML METERLEAK MTR#B028812 LOC/CUST#104255-528243 POSS CONS REG ON METER /** 1) MN: B028812 SN: 0020411, *TAP: SIZE: B LOC: 118 FEET FROM P LINE AT ST PETER URPL, *MB: CODE: BEK1 LOC: 118' FROM URPL ST. PETER ****/ | 2019-07-22 | EXAMINE JOB AT ABOVE LOCATION FOUND NO CONS REG ON 3/4 INCH METER
201901031901 | 2019-07-10 | LEAD | 1306 | TREME |  | WOLK | LOCATION# 103240 CUSTOMER# 526031 METER# B033320 INSPECTOR DID AN OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION ON METER, CAN'T DETERMINE WHERE LEAK IS COMING FROM...........PLEASE REPAIR /** 1) MN: B022422 SN: 0033888, *TAP: SIZE: B LOC: 73 FEET FROM P LINE AT BARRACKS LRPL, *MB: CODE: AEKM LOC: ****/ | 2019-07-22 | EXAMINE JOB AT ABOVE LOCATION FOUND NO CONSTANT REGISTRATION ON 3/4 INCH METER
201901033401 | 2019-07-10 | LEAD | 4520 | N ROBERTSON | JAPONICA | WILK | WATER INLET SERVICE LEAK /** 1) MN: A294505 SN: 0077175, *TAP: SIZE: A LOC: 213 FEET FROM P LINE AT KENTUCKY, *MB: CODE: ADL1 LOC: ON NO. ROBERTSON, 176' FROM P.L. KENTUCKY ****/ | 2019-07-09 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR IN INLET BACKFILLED JOB WITH RIVERSAND
201901033601 | 2019-07-10 | LEAD | 1414 | JAPONICA | N VILLERE | WILK | WATER INLET SERVICE LEAK /** 1) MN: A327243 SN: 0102272, *TAP: SIZE: A LOC: 121 FEET FROM P LINE AT VILLERE N, *MB: CODE: ADL2 LOC: 121'FROM P L VILLERE N 8' OUTSIDE PL ****/ | 2019-07-09 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201901033701 | 2019-07-10 | LEAD | 1406 | REYNES | N VILLERE | WILK | INLET SERVICE LEAK. LEAK UNDERNEATH SIDEWALK. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 7/8/2019. /** 1) MN: A334098 SN: 0104314, *TAP: SIZE: A LOC: 387 FEET FROM P LINE AT URQUHART, *MB: CODE: CFL LOC: RES 387FT FROM P.L. URQUHART 2.5' OUTSIDE PL ****/ | 2019-08-01 | EXAMINE JOB AT ABOVE LOCATION FOUND NO LEAK
201901035601 | 2019-07-10 | LEAD | 1773 | N BROAD |  | WOLK | WM-LEAK IN SIDEWALK OUTLET SERVICE LEAK CAUSING LARGE DEPRESSION HOLE EXPOSED LEFT FIVE (5) SAFETY CONES **1ST AM** /** 1) MN: A295783 SN: 0059836, *TAP: SIZE: A LOC: 80 FEET FROM P LINE AT O REILLY, *MB: CODE: CD LOC: ON NO. BROAD,81.5' FROM P.L. O'REILLY ****/ | 2019-07-18 | EXCAVATED IN MUD PLOT + MADE REPAIR ON 3/4 INCH OUTLET SERVICE LINE RAISED 5/8 INCH METER BXO BOTTOM TO GRADE FOUND NO OTHER PROBLEMIN CUT BACKFILLED + DRESSED UP AREA
201901037001 | 2019-07-11 | LEAD | 4962 | ST CLAUDE AV | TENNESSEE | WMTLK | WATER METER LEAK. LEAK UNDERNEATH SIDEWALK. LEAK LOCATED NEAR ST CLAUDE SERVICE ROAD. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 7/9/2019. /** 1) MN: 000000 SN: 0119967, *TAP: SIZE: B LOC: 157 FEET FROM P LINE AT TENNESSEE, *MB: CODE: AF LOC: ON ST CLAUDE 157FT FROM PL TENNESSEE 2' OUTSIDE ****/ | 2019-07-26 | EXCVATED 2 X 3 SIDEWALK FOUND LEAK ON 5/8 INCH INLETSERVICE MADE REPAIRS ON INLET BACKFILLED WITH COLDMILL JOB COMPLETE
201901041001 | 2019-07-13 | LEAD | 2319 | SPAIN | N TONTI | WILK | INLET SERVICE LEAK /** 1) MN: A293286 SN: 0056454, *TAP: SIZE: A LOC: 144 FEET FROM P LINE AT TONTI N, *MB: CODE: BDK2 LOC: ON SPAIN ST 143' FROM LSPL N TONTI ST ****/ | 2019-07-11 | EXCAVATED IN CONCRETE SIDEWALK + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE ALSO RAISED 5/8 INCH METER BOX BOTTOM TO GRADE BACKFILLED + DRESSED UP AREA FOUND METER OFF CUT OFF ON SHORTLY + FOUND LEAK ON PROPERTY CUT OFF REFER BACK TO PROPERTY OWNER FOR REPAIR
201901042201 | 2019-07-14 | LEAD | 2415 | LAMANCHE | N ROCHEBLAVE | WILK | ***************************PICKUP************************* INLET ON ABANDON SERVICE @ VACANT LOT NEXT TO ABOVE ADDRESS /** 1) MN: A325137 SN: 0168731, *TAP: SIZE: B LOC: 5 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: OOOO LOC: ON LAMANCHE 4FT FROM PL N ROCHEBLAVE 4FT OUTSD ****/ | 2019-08-02 | EXCAVATED IN MUD PLOT ++ MADE REPAIR ON 3/4 INCH ABANDONED INLET SERVICE LINE BACKFILLED + DRESSED UP AREA. (NO METER) JOB COMPLETE
201901043401 | 2019-07-15 | LEAD | 700 | N GAYOSO | ST PETER | WOLK | ML- METER LEAK ACCT#128820-519778 METER#A323719 OUTLET SERVICE LEAK UP TO PROPERTY LINE ***CUSTOMER REQUEST WATER TO BE TURNED OFF /** 1) MN: A327412 SN: 0071058, *TAP: SIZE: A LOC: 53 FEET FROM P LINE AT GAYOSO N, *MB: CODE: BDH LOC: ON ST PETER ST 53' FROM LRPL N GAYOSO ****/ | 2019-07-23 | EXAMINED JOB AND FOUND METER NOT SET INSIDE METER BOX AND METER IN OFF POSITION SET 5/8 INCH METER BACK IN SIDE BOX TURNED METER ON AND FOUND CONTRANT EXCAVAVTED IN MUD PLOT AND FOUND LEAK ON GALVENIZED PIPE ON PROPERTY SIDE BACKFILLED AREA LEAK ON PROPERTY SIDE
201901043701 | 2019-07-15 | LEAD | 926 | HARDING DR | DUMAINE | WILK | MI- LEAK IN STREET INLET SERVICE LEAKING AN ASPHALT STREET IN PREVIOUS REPAIRS /** 1) MN: A296257 SN: 0131874, *TAP: SIZE: C LOC: 235 FEET FROM P LINE AT DUMAINE, *MB: CODE: CDN6 LOC: ON HARDING BET ST JOHN/DUMAINE 238FT PL DUMAINE ****/ | 2019-07-24 | MADE 6 X 8 CUT IN CONCRETE BASE STREET WITH AIR GUN AND MADE REPAIR ON 1 SERVICE GOING UNDERNEATH DRAIN BACKFILLED AREA
201901044801 | 2019-07-15 | LEAD | 5316 | DOUGLAS |  | WOLK | INSP L UDUEBOR STATES HE IS UNABLE TO SET METER, WHEEL IS BROKEN. PLEASE REPAIR AND SET 5/8 METER. LOC 308065 ************1ST AM*********** BROKEN HANDWHEEL, UNABLE TO SET METER AS REQUESTED /** 1) MN: A198185 SN: 0141109, *TAP: SIZE: B LOC: 140 FEET FROM P LINE AT EGANIA, *MB: CODE: CDN2 LOC: ON DOUGLAS 134FT FROM PL OF EGANIA 7FT OUTSIDE PL ****/ | 2019-07-16 | EXCAVATED 4 X4 MUD PLOT REPLACE BROKEN 5/8 INCH HANDWHEEL AT ABOBVE LOCATION BACKFILL JOB WITH RIVERSAND AND SET 5/8 INCH WATER METER
201901044901 | 2019-07-15 | LEAD | 3117 | CONTI |  | WOLK | WM--LEAK IN BETWEEN SIDEWALK AND FRONT OF HOUSE EXAMINE OUTLET SERVICE FOR A LEAK CONSTANT REG ON METER /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-07-23 | MADE 4 X 4 SIDEWALK CUT AND MADE REPAIR ON 3/4 INCH OUTLET SERVICE AND REPLACED HAND WHEEL BEHIND METER BOX BACKFILLED AREA
201901046701 | 2019-07-16 | LEAD | 635 | N SCOTT |  | WOLK | ML METERLEAK MTR#E008043 LOC/CUST#222594-515227 CONS REG ON METER. /** 1) MN: D005065 SN: 0057957, *TAP: SIZE: D LOC: 207 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: ADQ3 LOC: ON NO. SCOTT,207' FROM P.L. ORLEANS AVE.,11' OUT- ****/ | 2019-07-23 | EXAMINED PUMPED MANHOLE DOWN FOUND UNION LEAKING MADE REPAIR BY TIGHEN UP UNION INSIDE MANHOLE NO CONSTANT REG
201901047601 | 2019-07-16 | LEAD | 1411 | KENTUCKY | N VILLERE | WILK | INLET SERVICE LEAK. LEAK IN ROADWAY, NON-SURFACE. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 7/15/2019. /** 1) MN: A311653 SN: 0175681, *TAP: SIZE: A LOC: 84 FEET FROM P LINE AT VILLERE N, *MB: CODE: CFL1 LOC: UNDER HEDGE INSIDE WALK-84' P.L. N VILLERE ****/ | 2019-07-23 | EXCAVATED IN ASPHALT STREET + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE COMPACTED BACKFILL + DRESSED UP AREA
201901048401 | 2019-07-16 | LEAD | 826 | N RAMPART | DUMAINE | WOLK | ACCT# 106920-528335 MTR# C035674 INSPECTOR FOUND CONSTANT REGISTRATION ON METER *******1ST AM WED****** (BILLING ISSUE) /** 1) MN: C019743 SN: 0028189, *TAP: SIZE: C LOC: 127 FEET FROM P LINE AT DUMAINE, *MB: CODE: BEK1 LOC: ON N RAMPART 127' FROM PL DUMAINE 1.5' OUTSIDE PL ****/ | 2019-07-25 | EXAMINED METER BOX AND FOUND NO CONSTANT REGISTRATION
201901048701 | 2019-07-16 | LEAD | 1607 | ARTS |  | WILK | INSP L UDUEBOR STATES INLET NEEDS REPAIRS, AREA IS FLOODING. LOC 129088 INLET SERVICE LEAK BAD CURB COCK WATER PASSING IN THE OFF POSITION IN A CONCRETE SIDEWALK /** 1) MN: A261998 SN: 0057300, *TAP: SIZE: A LOC: 53 FEET FROM P LINE AT CLAIBORNE AVE S, *MB: CODE: CDN1 LOC: ON ARTS 50FT FROM PL OF S CLAIBORNE AVE ****/ | 2019-07-25 | EXCAVATED 2 X 2 SIDEWALK CUT REPLACED METER COCK TO STOP LEAK BACKFILLED AND CLEANED THE AREA
201901051201 | 2019-07-16 | LEAD/PLASTIC | 734 | FLORIDA BL | ADA PL | WILK | WM-LEAK ON THE SIDEWALK (CG/07/19) CUSTOMER STATES LEAK IS GETTING WORSE EXAMINE INLET SERVICE IN MUDPLOT NEAR ELECTRIC POLE FOR LEAK CALL GAS COMPANY WILL ON ARRIVAL /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-07-22 | MADE A 5 X 6 MUD CUT EXCAVATED AND MADE REPAIRS ON A 1.50 INLET WATER MAIN CONTROLING LINE LEAD & PLASTIC INLET
201901055001 | 2019-07-17 | LEAD | 310 | CHARTRES | CONTI | WMTLK | *************************PICKUP************************** ********************1ST AM*********************** EXAMINE INLET AND OUTLET SERVICE FOR LEAK CAUSING POOR PRESSURE A-312000 /** 1) MN: E005407 SN: 0138276, *TAP: SIZE: E LOC: 11 FEET FROM P LINE AT BIENVILLE, *MB: CODE: CD LOC: ON CHARTRES, 11' FROM D.P.L. BIENVILLE, 3' OUTSIDE ****/ | 2019-08-15 | EXCAVATED 4 X 6 CONCRETE SLATE SIDEWALK FOUND LEAK ON 2 INCH INLET SERVICE AT WATERMAIN MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL. JOB COMPLETE
201901057601 | 2019-07-17 | LEAD/PLASTIC | 2329 | S ROMAN | JACKSON AV | WOLK | MI- CHANGE LEAD WHIP ACCT#306295-719294 METER#A415493 CHANGE LEAD WHIP HOLE OPENED/EXPOSED /** 1) MN: SN: 0075029, *TAP: SIZE: A LOC: 223 FEET FROM P LINE AT JACKSON AVE, *MB: CODE: BEL LOC: ON SO. ROMAN, 224' FROM U.S.P.L. JACKSON AVE. ****/ | 2019-07-20 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 3/4 SERVICE LEAKING.REPLACED 4 FT. OF 4/4 TUBING FROM CURB TO METER BOX TIED INTO LEAD.
201901062101 | 2019-07-18 | LEAD | 2005 | CLOUET | N JOHNSON | WMBK | MI-MISSING METER COVER METER #A213426 ACCT #168775-433483 REPLACE BROKEN METER BOX CASING /** 1) MN: A304782 SN: 0110697, *TAP: SIZE: A LOC: 37 FEET FROM P LINE AT JOHNSON N, *MB: CODE: BDL LOC: 37' FROM P.L.N.JOHNSON 8' OUTSIDE PL ****/ | 2019-07-26 | ARRIVED AT ABOVE LOCATION TO FIND A UPPER CASING BROKEN REMOVED AND REPLACED TO GRADE
201901064702 | 2019-07-29 | LEAD | 1705 | DESIRE |  | WILK | EXCAVATED AND FOUND NO WATER ON INLET SERVICE COMING FROM WATER MAIN IN STREET /** 1) MN: A236505 SN: 0084875, *TAP: SIZE: A LOC: 42 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BF5 LOC: ON DESIRE, 41.6' FROM S.P.L. NO. DERBIGNY ****/ | 2019-08-05 | EXCAVATE+D IN MUD PLOT + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE UNDER CURB RESTORING WATER BACK TO ABOVE LOCATION ALSO RAISED 5/8 INCH METER BOX BOTTOM TO GRADE BACKFILLED + DRESSED UP AREA ALSO SET 5/8 INCH METER
201901065301 | 2019-07-19 | LEAD | 1324 | ALABO |  | WOLK | INSP L UDUEBOR STATES OUTLET SERVICE IS LEAKING. PLEASE REPAIR METER A440033 LOC 308032 OUTLET SERVICE LEAK IN THE MUD PLOT /** 1) MN: A213032 SN: 0098667, *TAP: SIZE: A LOC: 212 FEET FROM P LINE AT URQUHART, *MB: CODE: BDL LOC: RES ON ALABO 1ST METER - 212' P.L. URQUHART ****/ | 2019-07-26 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 INCH CURB COCK TO MAKE THE REPAIRS
201901065401 | 2019-07-19 | LEAD | 721 | TRICOU |  | WMBK | LOCATIONID#306581-572978 METER#A433196 UPPER METERBOX CASING BROKEN /** 1) MN: A293599 SN: 0119125, *TAP: SIZE: A LOC: 165 FEET FROM P LINE AT ROYAL, *MB: CODE: CDL1 LOC: ON TRICOU 165' FROM PL OF ROYAL ****/ | 2019-07-22 | EXCAVATED 2 X 4 MUD PLOT REPLACE UPPER METER BOX CASING AT ABOVE LOCATION. JOB COMPLETE
201901065701 | 2019-07-19 | LEAD | 925 | INDEPENDENCE |  | WOLK | ML METER LEAK MTR# A273206 ACCT# 114121-427661 OUTLET SERVICE LEAK IN BRICK SIDEWALK, WITH CONSTANT REGISTRATION /** 1) MN: A241447 SN: 0046251, *TAP: SIZE: A LOC: 152 FEET FROM P LINE AT RAMPART N, *MB: CODE: BFLM LOC: BY FENCE AND TREE INSIDE 152' P.L. N RAMPART ****/ | 2019-07-31 | EXCAVATED 2 X 4 BRICK SIDEWAKJ IN TREE ROOTS FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIR ON OUTLET BACKFILL JOB WITH RIVERSAND JOB COMPLETE
201901066301 | 2019-07-19 | LEAD | 1924 | N DERBIGNY |  | WMRE | INSP L UDUEBOR STATES SERVICE IS BURIED. PLEASE RAISE TO GRADE AND SET 5/8 METER. LOC 308070 LOCATE, SET 5/8 METER AS REQUESTED, ALSO RAISE METER TO GRADE /** 1) MN: A251840 SN: 0043024, *TAP: SIZE: B LOC: 114 FEET FROM P LINE AT TOURO, *MB: CODE: BEL1 LOC: ON N DERBIGNY 122' FROM PL TOURO 8' OUTSIDE PL 2' ****/ | 2019-07-25 | EXCAVATED 4 X 2 MUD PLOT THROUGH BRICKS + DEBRIS SET ONRE 5/8 INCH METER WITH METER BOX COMPLETE BACKFILLED AND CLEANED THE AREA ALSO MARKED STREET AND METER BOX COVER WITH BLUE PAINT
201901078101 | 2019-07-22 | LEAD | 1528 | N ROBERTSON | LAHARPE | WILK | MI: LEAK IN STREET INLET SERVICE LEAK IN SIDEWALK BY VACANT LOT /** 1) MN: SN: 0052257, *TAP: SIZE: B LOC: 107 FEET FROM P LINE AT LAHARPE, *MB: CODE: OOO LOC: ON N ROBERTSON 109FT FROM C.P.L. LAHARPE 9FT OUT- ****/ | 2019-08-02 | EXCAVATED 4 X 4 MUD PLOT IN SIDEWALK FOUND LEAK N 3/4 INCH ABANDON SERVICE MADE REPAIR ON INLET SERVICE BACKFILL JOB WITH RIVERSAND JOB COMPLETE
201901078501 | 2019-07-22 | LEAD | 926 | N BROAD | ST PHILIP | WMTBG | MI-METER BOX BELOW GRADE METER#A417279 ACCT#177472-523478 ADJUST METER BOX TO PROPER GRADE /** 1) MN: A224808 SN: 0022842, *TAP: SIZE: A LOC: 166 FEET FROM P LINE AT ST PHILIP, *MB: CODE: C7 LOC: ON N BROAD 162' FROM PL ST PHILIP 3' OUTSIDE PL 12 ****/ | 2019-07-30 | EXCAVTED AND ADJUST METER BOX UP TO GRADE AT ABOVE LOCATION
201901079401 | 2019-07-23 | LEAD | 2317 | NEW ORLEANS |  | WMTLK | LOCATIONID#185432-495688 METER#A436648 LEAK INSIDE METERBOX /** 1) MN: A144673 SN: 0139443, *TAP: SIZE: B LOC: 123 FEET FROM P LINE AT NO. TONTI, *MB: CODE: BD LOC: ON NEW ORLEANS, 123' FROM P.L. NO. TONTI, 6' OUT- ****/ | 2019-08-05 | EXCAVATED 4 X 4 LIMESTONE GUTTER BOTTOM FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201901079801 | 2019-07-23 | LEAD | 5523 | N RAMPART |  | WMTLK | LOCATION ID-115088 MTR-B024397 MTR LEAK/AREA FLOODED /** 1) MN: B033161 SN: 0175910, *TAP: SIZE: B LOC: 87 FEET FROM P LINE AT CAFFIN AVE, *MB: CODE: ADO LOC: ON RAMPART 87FT FROM PL CAFFIN ****/ | 2019-08-01 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201901087201 | 2019-07-24 | LEAD | 1510 | N DORGENOIS |  | WILK | ML-METER LEAK METER# A389575 ACCT# 118243-489237 INLET SERVICE LEAK BAD CURB COCK IN CONCRETE SIDEWALK /** 1) MN: A297473 SN: 0043917, *TAP: SIZE: A LOC: 84 FEET FROM P LINE AT COLUMBUS, *MB: CODE: BFM LOC: INSIDE 84' P.L. COLUMBUS ****/ | 2019-08-02 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201901087501 | 2019-07-24 | LEAD | 1226 | N LOPEZ | DESOTO | WOLK | ML- METER LEAK MTR# A420074 ACCT# 130463-522167 OUTLET SERVICE LEAK IN MUDPLOT NEAR TREE /** 1) MN: A214685 SN: 0060260, *TAP: SIZE: A LOC: 64 FEET FROM P LINE AT DE SOTO, *MB: CODE: ADM2 LOC: ON NO. LOPEZ,71'F ROM P.L. DESOTO ****/ | 2019-08-05 | EZXCAVATED 4 X 4 MUD PLOT IN TREET ROOTS FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIR ON OUTLET BACKFILLED JOB WITH RIVERSAND
201901091101 | 2019-07-25 | LEAD | 3141 | TOULOUSE |  | WMTBG | LOCATIONID#159039-602703 METER#A266086 CAN'T LOCATE METER.LOCATE & RAISE /** 1) MN: A266086 SN: 0000000, *TAP: SIZE: C LOC: 89 FEET FROM P LINE AT LOPEZ S, *MB: CODE: __ LOC: BLDG DEMOLISHED METER TO SERVE A DRINKING FOUNTAIN ****/ | 2019-08-23 | EXCAVATED 4 X 4 MUD PLOT RAIS 5/8 INCH METER BOX UP TO GRADE AT ABOVE LOCATION BACKFILLED JOB WITH RIVERSAND AND COLDMILL
201901091201 | 2019-07-25 | LEAD | 2512 | TRICOU |  | WMTLK | LOCATIONID#181267-554654 METER#A365055 LEAK INSIDE METERBOX /** 1) MN: A267219 SN: 0129024, *TAP: SIZE: B LOC: 148 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: BDN2 LOC: RES ON TRICOU 151FT FROM PL DORGENOIS N 7' OUTSIDE ****/ | 2019-08-01 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201901091701 | 2019-07-25 | LEAD | 2013 | N GALVEZ |  | WMTLK | LOCATIONID#126640-495179 METER#A418167 LEAK INSIDE METERBOX /** 1) MN: A322970 SN: 0054946, *TAP: SIZE: A LOC: 108 FEET FROM P LINE AT PAUGER, *MB: CODE: CD LOC: ON GALVEZ 109'FROM L.S.P.L. PAUGER ****/ | 2019-08-05 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201901092901 | 2019-07-25 | LEAD | 2653 | N TONTI |  | WMRE | INSP L UDUEBOR STATES SERVICE IS BURIED. PLEASE RAISE TO GRADE AND SET 5/8 METER. LOC 308118 LOCATE, RAISE TO GRADE AND SET METER AS REQUESTED, HOUSE UNDER RENOVATION /** 1) MN: 000000 SN: 0081284, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT FRANKLIN AVE, *MB: CODE: BDLM LOC: ON TONTI 134' FROM PL OF FRANKLIN AVE ****/ | 2019-08-06 | EXCAVATED IN GUTTER BOTTOM + LOCATED 5/8 INCH METER BOX ALSO SET 5/8 INCH METER
201901093101 | 2019-07-25 | LEAD | 1422 | ESPLANADE AV |  | WILK | INSP L UDUEBOR STATES SERVICE HAS A BAD CURB COCK. PLEASE REPAIR INLET FOR LOC 142446 BAD CURB COCK IN MUDPLOT NEAR SIDEWALK /** 1) MN: A295115 SN: 0021734, *TAP: SIZE: B LOC: 100 FEET FROM P LINE AT NO. ROBERTSON, *MB: CODE: AFOL LOC: ON ESPLANADE AVE., 98' FROM P.L. NO. ROBERTSON ****/ | 2019-08-02 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201901095801 | 2019-07-25 | LEAD | 128 | S LOPEZ | CLEVELAND AV | WILK | **************************PICKUP*********************** INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A214676 SN: 0005948, *TAP: SIZE: A LOC: 99 FEET FROM P LINE AT CANAL, *MB: CODE: BFL5 LOC: INSIDE OPP FIRST POST ****/ | 2019-08-07 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND. JOB COMPLETE
201901099701 | 2019-07-26 | LEAD | 1461 | N ROBERTSON | COLUMBUS | WILK | PP- POOR PRESSURE MN:A388348 ACCT#106106-731780 ******************J.GILLIAM @ 11:46AM****************** INLET SERVICE LEAK IN CONCRETE SIDEWALK, CUSTOMER OUT OF WATER /** 1) MN: A284498 SN: 0008121, *TAP: SIZE: B LOC: 131 FEET FROM P LINE AT KERLEREC, *MB: CODE: AENO LOC: XX 131' P.L. KERLEREC ****/ | 2019-07-26 | EXCAVATED IN EXISTING SIDEWALK CUT AND MADE REPAIR ON 3/4 INCH INLET SERVICE BACKFILLED AREA JOB COMPLETE
201901102201 | 2019-07-26 | LEAD | 3144 | N PRIEUR | LOUISA | WMTLK | WM- LEAK IN TH STREET EXAMINE INLET/OUTLET SERVICE FOR LEAK UNABLE TO PUMP OUT METER BOX 07/29/19 PER R STANWOOD PER F THARP UPGRD TO A ***B 1ST AM*** (KSW) /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-08-06 | EXSCAVATED IN GUTTER BOTTOM AND MADE REPAIR ON 3/4 INCH INLET SERVICE BACKFILLED AREA
201901104001 | 2019-07-28 | LEAD | 1705 | TUPELO |  | WILK | ML- METER LEAK MTR#A241675 ACCT#172458-422287 INLET SERVICE LEAKING IN TO METER BOX IN MUD PLOT /** 1) MN: A141639 SN: 0127068, *TAP: SIZE: A LOC: 12 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BDLM LOC: MTR ON TUPELO 12FT FROM PL DERBIGNY 7FT OUTSIDE PL ****/ | 2019-08-09 | ARRIVED AT ABOVE LOCATION FOUND METER BOX COCK LEAKING REPAIR + BACKFILLED AREA
201901106401 | 2019-07-29 | LEAD | 2736 | CONTI | N BROAD | WILK | MI- LEAK IN THE STREET CHANGED FROM 2728 CONTI INLET SERVICE LEAK ON ABANDON SERVICE @ VACANT LOT ON THE MAIN /** 1) MN: A279131 SN: 0050027, *TAP: SIZE: A LOC: 204 FEET FROM P LINE AT WHITE N, *MB: CODE: AD21 LOC: OPP SIDE STEPS CURB 277' P.L. N BROAD ****/ | 2019-08-12 | MADE AN 8 X 6 CUT IN ASPHALT STREET + REPLACED 3/4 INCH BEND ADAPTER ON WATER MAIN COMPACTED BACKFILL + DRESSED UP AREA
201901106701 | 2019-07-29 | LEAD | 2220 | ONZAGA |  | WILK | LOCATION: 137689 METER# A 439979 INSP UDUEBOR STATES INLET SERVICE NEED REPAIRS, BAD CURB COCK. PLEASE REPAIR INLET SERVICE LEAK BEHIND CURB COCK /** 1) MN: A328478 SN: 0006833, *TAP: SIZE: B LOC: 166 FEET FROM P LINE AT MIRO S, *MB: CODE: CEMN LOC: ON ONZAGA 166' FROM PL OF MIRO S ****/ | 2019-08-07 | EXCAVATED 4 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL. JOB COMPLETE
201901108401 | 2019-07-29 | LEAD | 2606 | PAUGER | N PRIEUR | WILK | ML- METER LEAK ACCT# 125451-713854 METER# A434974 EXAMINE INLET SERVICE FOR ALEAK WITH CONSTANT REGISTRATION ON THE METER ***HOUSE VACANT*** /** 1) MN: A302060 SN: 0049756, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT PRIEUR NO., *MB: CODE: CDL LOC: ON PAUGER,49' FROM U.S.P.L. NO. PRIEUR ****/ | 2019-08-06 | EXCAVATED IN BRICK SIDEWALK +MADE REPAIR ON 3/4 INCH OUTLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201901112101 | 2019-07-29 | LEAD | 1021 | IBERVILLE | N RAMPART | WILK | WM-LEAK IN THE STREET INLET SERVICE LEAK IN CONCRETE STREET /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-08-01 | MADE AN 8 X 6 CUT IN CONCRETE STREET + MADE REPAIR ON 1 INCH INLET SERVICE LINE COMPACTED BACKFILL + DRESSED UP AREA
201901112201 | 2019-07-29 | LEAD | 3400 | DERBY PL | N SALCEDO | WILK | ML-METER LEAK METER#A131540 ACCT# INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A131540 SN: 0091148, *TAP: SIZE: A LOC: 37 FEET FROM P LINE AT SALCEDO N, *MB: CODE: CDLM LOC: 37' FROM PL N SALCEDO 5' OUTSIDE PL 2' INSIDE CURB ****/ | 2019-08-06 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIR ON OUTLET AND METER BOX UP TO GRADE BACKFILLED JOB WITH RIVERSAND
201901115001 | 2019-07-30 | LEAD | 945 | PICHELOUP PL |  | WMTLK | LOCATIONID#136844-477992 METER#A312421 LEAK INSIDE METERBOX /** 1) MN: A269259 SN: 0067411, *TAP: SIZE: A LOC: 345 FEET FROM P LINE AT DUAMINE, *MB: CODE: BDK LOC: 346FT FROM LSPL DUMAINE ****/ | 2019-08-06 | EXCAVATED 4X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET SERVICE RAISE METER BOX UP TO GARDE BACKFILLED JOB WITH RIVERSAND JOB COMPLETE
201901115202 | 2019-08-21 | LEAD | 1036 | MAZANT |  | WMTLK | EXAMINED JOB AT ABOVE LOCATION AND FOUND TAN COLOR BUICK LA SABE PARK ON METER BOX WITH NO PLATE ON VEHICLE UNABLE TO REPAIR CURB COCK /** 1) MN: A139769 SN: 0069925, *TAP: SIZE: B LOC: 253 FEET FROM P LINE AT RAMPART N, *MB: CODE: ADE LOC: ON MAZANT, 253'F ROM P.L. NO. RAMPART ****/ | 2019-08-21 | EXCAVATED IN CONCRETESIDEWALK + REPLACED 5/8 INCH CURB COCK BACKFILLED + DRESSED UP AREA
201901115301 | 2019-07-30 | LEAD | 1001 | BARTHOLOMEW |  | WMTLK | LOCATIONID#116328-542478 METER#A322845 LEAK INSIDE METERBOX /** 1) MN: A325435 SN: 0042635, *TAP: SIZE: A LOC: 30 FEET FROM P LINE AT RAMPART N, *MB: CODE: CEK LOC: ON BARTHOLOMEW 30FT FROM LSPL RAMPART ****/ | 2019-08-12 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201901115701 | 2019-07-30 | LEAD | 1913 | CAFFIN AV |  | WMTLK | LOCATIONID#151305-424085 METER#A358558 METERBOX OVERFLOWING /** 1) MN: A183064 SN: 0133344, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT PRIEUR N, *MB: CODE: CDL1 LOC: OPP S & W CURB - 110' P.L. N PRIEUR ****/ | 2019-08-13 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND. JOB COMPLETE
201901117001 | 2019-07-30 | LEAD | 1627 | ANDRY |  | WOLK | MI LEAK ON THE SIDEWALK OUTLET SERVICE LEAK IN A BRICK SIDEWALK, WITH CONSTANT REGISTRATION ON THE METER /** 1) MN: B028437 SN: 0144747, *TAP: SIZE: B LOC: 194 FEET FROM P LINE AT CLAIBORNE AVE N, *MB: CODE: BDL LOC: MTR ON ANDRY 194FT FROM PL CLAIBORNE 6FT OUTSD PL ****/ | 2019-08-09 | ARRIVED AT ABOVE LOCATION FOUND 5/8 INCH LEAD LINE LEAKING ON OUTLET + REPAIRED + BACKFILLED JOB
201901118301 | 2019-07-30 | LEAD | 2108 | CONTI |  | WOLK | UNABLE TO INSTALL WHEEL TO SET METER. PLEASE REPAIR AND SET 5/8 METER. LOC 308143 INSTALL HANDWHEEL & SET METER CUSTOMER WAITING ON WATER **BOTH SIDES UNDER RENOVATIONS /** 1) MN: A286538 SN: 0058872, *TAP: SIZE: B LOC: 75 FEET FROM P LINE AT JOHNSON N, *MB: CODE: CFLM LOC: ON CONTI 74FT PL N JOHNSON 8' OUTSIDE 2' INSIDE ****/ | 2019-08-08 | ARRIVED AT ABOVE LOCATION TO FIND A 5/8 INCH A 5/8 INCH HARDWHEEL BROKEN REMOVED AND REPLACED WITH A 5/8 INCH HANDWHEEL TO MAKWE THE REPAIR LEFT ON THE STOP-WASTE
201901118401 | 2019-07-30 | LEAD | 1201 | N RAMPART |  | WMRE | INSP L UDUEBOR STATES SERVICE IS BURIED. PLEASE RAISE TO GRADE AND REMOVE METER A409349 LOC 105261 LOCATE RAISE TO GRADE & REMOVE METER /** 1) MN: A334986 SN: 0007308, *TAP: SIZE: A LOC: 51 FEET FROM P LINE AT RAMPART N, *MB: CODE: ADHN LOC: 10'HPL SIDE CRB BET POLE/END OF GUY WIRE SIDE S ****/ | 2019-08-06 | EXCAVATED IN MUD PLOT + LOCATED 5/8 INCH 5/8 INCH METER BOX RAISED 5/8 INCH BOTTOM TO GRADE + REMOVED 5/8 INCH METER ALSO MADE REPAIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201901119501 | 2019-07-30 | LEAD | 1615-17 | N GALVEZ |  | WMTLK | LOCATION: 308141 METER# A 439942 SET TODAY INSP UDUEBOR STATES OUTLET SERVICE NEED TIE IN, ALSO REPLACE INLET WASHER LEAK. PLEASE REPAIR. EXAMINE INLET & OUTLET TO CLOSE TOGETHER METER SHOP UNABLE TO SET METER, ALSO READY FOR TIE IN. ***HOUSE UNDER RENOVATIONS*** /** AT 1615: 1) MN: A126362 SN: 0040356, *TAP: SIZE: B LOC: 132 FEET FROM P LINE AT LAPEYROUSE, *MB: CODE: CF LOC: ON NO. GALVEZ, 113' FROM P.L. LAPEYROUSE, 4' OUT- ****/ | 2019-08-06 | EXCAVATED IN MUD PLOT + REPLACED 3/4 INCH LEAD OUTLET SERVICE LINE BACKFILLED + DRESSSED UP AREA
201901121001 | 2019-07-31 | LEAD | 2319 | GORDON |  | WOLK | MI CONSTANT ON METER METER#A312654 /** 1) MN: A243208 SN: 0136871, *TAP: SIZE: A LOC: 139 FEET FROM P LINE AT TONTI N, *MB: CODE: CDM2 LOC: MTR ON GORDON 139FT FROM PL TONTI 8FT OUTSIDE PL ****/ | 2019-08-14 | MADE REPAIR ON WHEEL SIDE 5/8 INCH LEAD + PLASTIC BACKFILLED AND CLEAN AREA UP
201901121301 | 2019-07-31 | LEAD | 1614 | INDUSTRY | PARIS AV | WMTLK | METER LEAK ACCT# 136347-492250 METER# A-383057 /** 1) MN: A287527 SN: 0066767, *TAP: SIZE: B LOC: 139 FEET FROM P LINE AT PARIS AVE, *MB: CODE: ADK LOC: 139' P.L. PARIS AVE ****/ | 2019-08-07 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION. JOB COMPLETE
201901121501 | 2019-07-31 | LEAD | 533 | SPAIN |  | WMTLK | LOCATIONID#116231-715456 METER#A319435 LEAK INSIDE METERBOX AROUND CURBCOCK /** 1) MN: A319435 SN: 0046725, *TAP: SIZE: A LOC: 47 FEET FROM P LINE AT CHARTRES, *MB: CODE: AFMK LOC: ON SPAIN 46.5FT FROM PL OF CHARTRES ****/ | 2019-08-09 | EXCAVATED IN MUD PLOT AND MADE REPAIR ON 3/4 INCH INLET SERVICE AND REPALCED 5/8 INCH CURB COCK BACKFILLED AREA
201901125301 | 2019-07-31 | LEAD/PLASTIC | 1881 | HUMANITY | ALLEN | WOLK | ML-METER LEAK LEAKING AGAIN METER#A417224 ACCT#301879-445824 OUTLET SERVICE LEAK IN MUDPLOT CONSTANT REG ON METER ALSO LEFT ONE (1) CONE FOR SAFETY /** 1) MN: A215251 SN: 0103315, *TAP: SIZE: A LOC: 25 FEET FROM P LINE AT HUMANITY, *MB: CODE: AHL LOC: ON ALLEN, 25' FROM P.L. HUMANITY, 5.5' OUTSIDE ****/ | 2019-08-11 | MADE A 2 X 10 MUD CUT EXCAVATED AND RENEWED A 3/4 OUT SERVICE FROM THE METER TO PROPERTY ALSO RAISED THE METER TO GRADE LEAD INLET
201901126201 | 2019-07-31 | LEAD | 1317 | TUPELO | URQUHART | WILK | ML- METER LEAK METER #A194890 ACCT #165111-422538 INLET SERVICE LEAKING INSIDE METER BOX BAD CURB COCK /** 1) MN: A194890 SN: 0105139, *TAP: SIZE: A LOC: 105 FEET FROM P LINE AT URQUHART, *MB: CODE: BDL LOC: ON TUPELO, 105' FROMP.L. URQUHART, 6.5' OUTSIDE ****/ | 2019-08-09 | EXCAVATED 4 X 4 MUD PLOT IN TREE ROOTS FOUND LEAK ON 5/8 INCH INLET SERVICE MDE REPAIR ON INLET AN RAISE METERBOX UP TO GRADE BACKFILLED JOB WITH RIVERSAND
201901127401 | 2019-08-01 | LEAD | 5219 | N ROBERTSON | EGANIA | WOLK | OUTLET SERVICE LEAK /** 1) MN: A284522 SN: 0131912, *TAP: SIZE: B LOC: 123 FEET FROM P LINE AT LIZARDI, *MB: CODE: CDHL LOC: ON N ROBERTSON 122FT FROM PL OF LIZARDI 7FT OUT- ****/ | 2019-07-31 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH OUTLET SERVICE REPAIR ON OUTLET BACKFILL JOB WITH RIVERSAND JOB COMPLETE
201901127601 | 2019-08-01 | LEAD | 1221 | POLAND AV |  | WMTLK | LOCATIONID#150088-431364 METER#A418767 METERBOX OVERFLOWING /** 1) MN: A276001 SN: 0082815, *TAP: SIZE: A LOC: 185 FEET FROM P LINE AT MARAIS, *MB: CODE: ADL2 LOC: 184' P.L. MARAIS ****/ | 2019-08-09 | EXCAVATED 4 X 4 MUD PLOT IN SIDEWALK FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE RPAIR ON OUTLET BACKFILLED JOB WITH RIVERSAND + COLDMILL
201901127701 | 2019-08-01 | LEAD | 1219 | POLAND AV |  | WMTLK | LOCATIONID#157377-730494 METER#A372278 METERBOX OVERFLOWING /** 1) MN: A327238 SN: 0082815, *TAP: SIZE: A LOC: 185 FEET FROM P LINE AT MARAIS, *MB: CODE: ADL2 LOC: ON POLAND AVE., 182.5' FROM P.L. MARAIS, 9'OUTSIDE ****/ | 2019-08-09 | EXCAVATED 4 X 4 MUD PLOT IN SIDEWALK FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPAIR ON OUTLET BACKFILLED JOB WUTH RIVERSAND
201901127901 | 2019-08-01 | LEAD | 1718 | CLOUET |  | WMTLK | LOCATIONID#304706-732999 METER#A415757 LEAK INSIDE METERBOX /** 1) MN: A326932 SN: 0084252, *TAP: SIZE: A LOC: 152 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BEN LOC: 151' P.L. N DERBIGNY ****/ | 2019-08-08 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201901129901 | 2019-08-01 | LEAD | 411 | FRENCHMEN |  | WILK | PP POOR PRESSURE ACCOUNT #107734-728381 METER B020957 EXAMINE INLET SERVICE FOR POOR PRESSURE /** 1) MN: B020957 SN: 0009298, *TAP: SIZE: B LOC: 42 FEET FROM P LINE AT FRENCHMEN, *MB: CODE: BEN5 LOC: ON ESPLANADE AVE ****/ | 2019-08-21 | EXCAVATED IN ASPHALT STREET AT ABOVE LOCATION FOUND NO LEAK ON SERVICE OR METER AT ABOVE LOCATION ALSO FOUND GOOD PRESSURE ON INSIDE FAUCET COMPACTED BACKFILL + DRESSED UP AREA
201901130701 | 2019-08-01 | LEAD | 1336 | ST FERDINAND | N VILLERE | WILK | ****************PICKUP JOB**************** INLET SERVICE LEAK COMING OUT OF OLD PATCH FLOODING CURB GETTING OFF IN DCB /** 1) MN: C023272 SN: 0123894, *TAP: SIZE: C LOC: 54 FEET FROM P LINE AT VILLERE N, *MB: CODE: CDN3 LOC: FRONT BY POST 54FT PL N VILLERE 7' OUTSIDE 1' IN- ****/ | 2019-08-13 | EXCAVATED IN PREVIOUS CUT + MADE REPAIR ON 1 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201901131801 | 2019-08-02 | LEAD | 5252 | CONSTANCE |  | WMTLK | LOCATION ID-104599 MTR BOX OVER FLOWING/GREEN ALGAE /** 1) MN: A345501 SN: 0008667, *TAP: SIZE: A LOC: 76 FEET FROM P LINE AT DUFOSSAT, *MB: CODE: AFLM LOC: ON CONSTANCE 74FT FROM LRPL OF DUFOSSAT ****/ DOTTIE READY 8-7-19 EXP 8-27-19 | 2019-08-16 | ARRIVED AT THE ABOVE LOCATION MADE A 1 X 1 SIDEWALK CUT AROUND THE METER BOX AND MADE REPAIRS ON THE INLET.THEN BACKFILLED AND CLEANED THE AREA.
201901131901 | 2019-08-02 | LEAD | 4714 | N RAMPART |  | WMTLK | LOCATION ID-188854 MTR-A416431 UNDERGROUND LEAK BY MTR /** 1) MN: A262618 SN: 0145956, *TAP: SIZE: B LOC: 139 FEET FROM P LINE AT SISTER, *MB: CODE: AD LOC: 138FT FROM PL SISTER ON RAMPART ** 2) MN: A345321 SN: 0145956, *TAP: SIZE: A LOC: 144 FEET FROM P LINE AT SISTER, *MB: CODE: CD LOC: ON RAMPART 140FT FROM RAMPART 2FT OUTSIDE THERE ARE 2 MORE NOT LISTED. ****/ | 2019-08-09 | EXCAVATED 4 X 6 LIMESTONE DRIVEWAY FOUND LEAK ON ABANDON 3/4 INCH INLET SERVICE MADE REPIR ON INLET BACKFILLED JOB WITH RIVERSNAD AND COLDMILL
201901132101 | 2019-08-02 | LEAD | 2321 | LAPEYROUSE |  | WOLK | LOCATION# 155583 CUSTOMER# 488927 METER# A393542 INSPECTOR DID AN OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION ON METER, CAN'T DETERMINE WHERE LEAK IS COMING FROM.........PLEASE REPAIR /** 1) MN: A311018 SN: 0073477, *TAP: SIZE: A LOC: 132 FEET FROM P LINE AT NO. TONTI, *MB: CODE: CDN2 LOC: ON LAPEYROUSE,133' FROM P.L. NO. TONTI,11.5' OUT- ** 2) MN: A236398 SN: 0163656, *TAP: SIZE: B LOC: 140 FEET FROM P LINE AT TONTI N, *MB: CODE: OOO LOC: ON LAPEYROUSE 141FT FROM PL TONTI 9FT OUTSD PL ****/ | 2019-08-09 | REPLACED 5/8 INCH HANDWHEEL + GUTS IN METER BOX AT ABOVE LOCATION
201901134601 | 2019-08-02 | LEAD/PLASTIC | 6429 | LOUIS XIV |  | WMRE | LOCATION: 308053 M FRAZIER STATES METER BOX SERVICE IS BURIED. PLEASE LOCATE, RAISE AND SET A 3/4 METER. NEW CONSTRUCTION LOCATE, MARK, SET 3/4 METER & RENEW OUTLET. ***NEW CONSTRUCTION*** /** 1) MN: B029789 SN: 0100192, *TAP: SIZE: B LOC: 267 FEET FROM P LINE AT BRAGG, *MB: CODE: ADK LOC: ON LOUIS XIV 267' FROM PL BRAGG 9' OUTSIDE PL ****/ | 2019-08-20 | EXCV 9 X3 CUT FOUND METER IN OFF POSITION CHANGE OUTLET LEAD WHIP REPLACE WITH PLASTIC AND LEFT WHIP BACKFILLED AND DRESS CUT WITH SAND ALSO RAISED METER TO GRADE, JOB CONTINUE TO REPLACE LEAD INLET SERVICE FROM METER TO MAIN
201901136501 | 2019-08-02 | LEAD | 2131 | MUSIC | N GALVEZ | WILK | ML: METER LEAK ACCT#153360-484192 MTR#A429184 INLET SERVICE LEAK INSIDE METER BOX /** 1) MN: A280241 SN: 0142014, *TAP: SIZE: A LOC: 235 FEET FROM P LINE AT GALVEZ N, *MB: CODE: CDM2 LOC: 235' P.L. N GALVEZ 7' OUTSIDE P/L 2' INSIDE CURB ****/ | 2019-08-08 | MADE 4 X 4 SIDEWALK OUT AND REPALCE 5/8 INCH CURB COCK WITH NEW ONE BACKFILLED AREA
201901138101 | 2019-08-02 | LEAD | 1841 | MANDEVILLE | N PRIEUR | WILK | ML- METER LEAK ACCT# 217996-483235 MTR# A417444 INLET SERVICE LEAKING INSIDE METER BOX BAD CURB COCK /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-08-08 | EXCAVATED IN MUD PLOT GUTTER BOTTOM AND REPLACED 5/8 INCH CURB COCK INSIDE METER BOX BACKFILLED AREA
201901138601 | 2019-08-02 | LEAD | 2320 | ALVAR | N TONTI | WOLK | MI: LEAK IN THE SIDEWALK CHECK FOR LEAK @ PROPERTY LINE CONSTANT REG /** 1) MN: A311202 SN: 0093335, *TAP: SIZE: A LOC: 137 FEET FROM P LINE AT TONTI, *MB: CODE: ADK LOC: ON ALVAR 137FT FROM PL OF TONTI 7.5FT OUTSIDE PL ****/ | 2019-08-16 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 OUTLET SERVICE MADE REPAIR ON OUTLET BACKFILED JOB WITH RIVERSAND AND COLDMILL. JOB COMPLETE
201901141201 | 2019-08-03 | LEAD/PLASTIC | 1728 | SONIAT | DANNEEL | WILK | MI:LEAK IN THE STREET INLET SERVICE LEAK IN ASPHALT STREET FROM MUDPLOT /** 1) MN: D004053 SN: 0078021, *TAP: SIZE: D LOC: 35 FEET FROM P LINE AT DANNEEL, *MB: CODE: __ LOC: ON SONIAT, 35' FROM C.P.L. DANNEEL, 7' OUTSIDE, ****/ DOTTIE READY 8-23-19 EXP 9-12-19 | 2019-08-27 | MADE CUT OVER WATER MAIN .REPAIR LEAK ON INLET SERVICE AND CHANGED TAILPIECE.BACKFILLED WITH SAND AND LIMESTONES.(SOC 5FT .X 5 FT .ASPHALT F/D)
201901148201 | 2019-08-05 | LEAD | 722 | PIETY | ROYAL | WOLK | ML-METER LEAK ACCT#131310-541823 METER#A123082 CHECK FOR LEAK AT PROPERTY LINE WITH CONSTANT REGISTRATION HOUSE UNDER RENOVATIONS /** 1) MN: A123082 SN: 0061858, *TAP: SIZE: A LOC: 187 FEET FROM P LINE AT ROYAL, *MB: CODE: BEKN LOC: ON PIETY,187.4' FROM U.S.P.L. ROYAL ****/ | 2019-08-12 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK ON 5/8 INCH OUTLET SERVICE MADE REPIR ON OUTLET SRVICE BACKFILL JOB WITH RIVERSAND AND COLDMILL
201901149201 | 2019-08-05 | LEAD | 829 | OLGA | ORLEANS AV | WOLK | WM-LEAK IN SIDEWALK OUTLET SERVICE LEAK ON SIDEWALK /** 1) MN: A231801 SN: 0040259, *TAP: SIZE: A LOC: 218 FEET FROM P LINE AT ORLEANS AVE, *MB: CODE: CE LOC: 220FT FROM LSPL ORLEANS METER ON OLGA ****/ | 2019-08-14 | EXCAVATED IN CONCRETE SIDEWALK + MADE REPAIR ON 3/4 INCH OUTLET SERVICE LINE BACKFILLED + DRESSED UP AREA
201901154901 | 2019-08-06 | LEAD | 3621 | DANNEEL |  | WMBK | INSP S BIBBINS STATES CASING SHIFTED, OBSTRUCTING METER. PLEASE REPAIR AND CHANGE METER A418215 LOC 199395 BROKEN METER BOX CASING HAS SHIFTED /** 1) MN: A119868 SN: 0158646, *TAP: SIZE: B LOC: 27 FEET FROM P LINE AT AMELIA, *MB: CODE: CD LOC: ON DANNEEL 55FT FROM AMELIA 8FT OUTSIDE ****/ DOTTIE READY 8-9-19 EXP 8-29-19 | 2019-08-09 | ARRIVED ON JOB EXAMINED METER FOUND BROKE METER CASING AND 5/8 INCH METER BOX COCK LEAKING MADE REPAIR AND BACKFILLED JOB COMPLETE
201901155501 | 2019-08-06 | LEAD | 3142 | N RAMPART | LOUISA | WOLK | ML-METER LEAK ACCT #122106-727893 METER #A259120 OUTLET LEAK - BROKEN HANDWHEEL (C) /** 1) MN: A259120 SN: 0040325, *TAP: SIZE: A LOC: 200 FEET FROM P LINE AT LOUISA, *MB: CODE: CFL LOC: 200FT FROM URPL LOUISA ON N RAMPART ST ****/ | 2019-08-13 | MADE 4 X 4 SIDEWALK CUT AND REPLACED HAND WHEEL BEHIND METER BOX BACKFILLED AREA
201901155601 | 2019-08-06 | LEAD | 918 | PIETY | BURGUNDY | WOLK | ML- METER LEAK METER # A395035 ACCT. #: 114252-427235 S/R#12879436 SHOWS WHERE REPAIRS WERE MADE BUT CUST SHOWED RECENT VIDEO WHERE LEAK IS STILL IN PROGRESS. OUTLET LEAK IN THE METER BOX (CONSTANT REG ON THE METER) /** 1) MN: 000000 SN: 0016895, *TAP: SIZE: A LOC: 142 FEET FROM P LINE AT BURGUNDY, *MB: CODE: CELM LOC: 142FT FROM USPL BURGUNDY ON PIETY ****/ | 2019-08-12 | REPLACE BROKEN 5/8 INCH HANDWHEEL AT ABOVE LOCATION
201901155701 | 2019-08-06 | LEAD | 1517-19 | PAUGER | BURGUNDY | WILK | MI- CUT SERVICE BY ENTERGY. NOT SURE IF CUST WITHOUT WATER MN:A115537 ACCT#112974-485550 DAMAGE CLAIM **********CHANGE FROM 1527 PAUGER/BURGUNDY**** CUT INLET SERVICE (IN THE STREET), CUT BY ENTERGY, CUSTOMERS HAS WATER @ STOP/WASTE. *****1ST WEDNESDAY (B) /** AT 1519: 1) MN: A342242 SN: 0044179, *TAP: SIZE: B LOC: 136 FEET FROM P LINE AT DAUPHINE, *MB: CODE: __ LOC: ON PAUGER 137FT FROM PL DAUPHINE ** 2) MN: SN: 0044179, *TAP: SIZE: B LOC: 136 FEET FROM P LINE AT DAUPHINE, *MB: CODE: __ LOC: ON PAUGER 136' FROM P.L. DAUPHINE, 8' OUTSIDE, ****/ | 2019-08-08 | MADE 4 X 4 CUT IN CONCRETE BASE STREET WITH AIR GUN AND MADE REAPIR ON 3/4 INCH INLET SERVICE DAMAGED BY ENTERGY BACKFILLED AREA. JOB COMPLETE
201901157301 | 2019-08-07 | LEAD | 1824 | URSULINES AV |  | WMTLK | LOCATIONID#118996-525232 METER#A399938 LEAK INSIDE METERBOX /** 1) MN: A258010 SN: 0054054, *TAP: SIZE: A LOC: 132 FEET FROM P LINE AT ROMAN N, *MB: CODE: AFKO LOC: INSIDE BY STEPS 132' P.L. N ROMAN ****/ | 2019-08-14 | MADE REPAIR ON 5/8 INCH CURB COCK BACKFILLED AND CLEAN UP AREA
201901158401 | 2019-08-07 | LEAD | 2724-26 | ST CLAUDE AV |  | WILK | LOCATION: 117165 METER# 428383 WAS REMOVED 8/6/19 INSP UDUEBOR STATES INLET SERVICE NEED REPAIRS. BAD BLEEDER VALVE AND CURB COCK. PLEASE REPAIR ONLY. BAD CURB COCK INSIDE METER BOX /** AT 2724: 1) MN: A242638 SN: 0062269, *TAP: SIZE: A LOC: 55 FEET FROM P LINE AT ST FERDINAND, *MB: CODE: AEK LOC: 55FT FROM URPL ST FERDINAND,METER ON ST CLAUDE AVE ****/ | 2019-08-14 | EXCAVATED 2 X 4 CONCRETE SIDEWALK FOUND LEAK 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL
201901159401 | 2019-08-07 | LEAD | 1819 | N BROAD |  | WILK | MI- LEAK BETWEEN THE SIDEWALK AND THE STREET *******FLOODING AREA********* INLET SERVICE LEAK IN ASPHAT STREET /** 1) MN: A308264 SN: 0063476, *TAP: SIZE: A LOC: 159 FEET FROM P LINE AT O REILLY, *MB: CODE: AD LOC: ON N BROAD ST 157' FROM LSPL O'REILLY ST 4' INSID ****/ | 2019-08-20 | EXCAVATED IN ASPHALT STRET + MUD PLOT + REPLACED 3/4 INCH INLET SERVICE LIE FROM WATER TO METER BOX COMPACTED BACKFILL + DRESSED UP AREA
201901159601 | 2019-08-07 | LEAD | 828 | N SALCEDO |  | WOLK | ML-- METER LEAK METER# A398555 ACCT# 117940-521479 OUTLET SERVICE LEAK IN CONCRETE SIDEWALK /** 1) MN: A345088 SN: 0028551, *TAP: SIZE: A LOC: 111 FEET FROM P LINE AT DUMAINE, *MB: CODE: OOOO LOC: 114' P.L. DUMAINE ****/ | 2019-08-19 | REPLACE BROKEN 5/8 INCH HANDWHEEL AT ABOVE LOCATION
201901159701 | 2019-08-07 | LEAD | 3154 | CASTIGLIONE |  | WMTLK | ML-- METER LEAK MTR#A267711 ACCT#144337-492820 EXAMINE INLET AND OUTLET SERVICE FOR LEAK, ALSO REPLACE BROKEN METER BOX CASING /** 1) MN: A267711 SN: 0090743, *TAP: SIZE: B LOC: 223 FEET FROM P LINE AT CRETE, *MB: CODE: CDI3 LOC: ON CASTIGLIONE 12FT FROM DIV. P/L SALTUS 2'OUTSIDE ****/ | 2019-08-21 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201901159901 | 2019-08-07 | LEAD | 2501-2503 | PAINTERS | N DORGENOIS | WMRE | MI LEAK ON THE SIDE WALK LOCATE SERVICE AND REPAIR, UABLE TO DETEERMING WHERE LEAK IN COMING FROM /** AT 2501: 1) MN: A345559 SN: 0076215, *TAP: SIZE: B LOC: 66 FEET FROM P LINE AT PAINTERS, *MB: CODE: BDHM LOC: ON DORGENOIS 66FT FROM PAINTERS ** AT 2503: 2) MN: A345581 SN: 0072615, *TAP: SIZE: B LOC: 24 FEET FROM P LINE AT FRANKLIN, *MB: CODE: HDML LOC: ON N DORGENOIS 24FT FROM D.P.L. FRANKLIN AVE 8FT ****/ | 2019-08-15 | EXCAVATED TO FIND A 5/8 INCH CURB COCK LEAKING REMOVED AND REPLACED WITH A 5/8 ICH CURB COCK TO MAKE THE REPAIR
201901161501 | 2019-08-07 | LEAD | 3030 | ROYAL | MONTEGUT | WILK | WM-LEAK IN SIDEWALK INLET SERVICE LEAK IN CONCRETE SIDEWALK /** 1) MN: A293470 SN: 0021280, *TAP: SIZE: B LOC: 236 FEET FROM P LINE AT MONTEGUT, *MB: CODE: CFL5 LOC: 236FT FROM IRPL MONTEGUT ****/ | 2019-08-13 | MADE 4 X 4 SIDEWALK CUT AND REPLACED 5/8 INCH CURB COCK IN METER BOX BACKFILLED AREA
201901165601 | 2019-08-08 | LEAD | 3605 | ELAINE PL | N JEFFERSON DAVIS PK | WILK | WM - LEAK ON THE SIDEWALK - LEAK ON THE SIDE OF THE PROPERTY - ELAINE PL CHANGED FROM 811 N JEFFERSON DAVIS PK INLET @ THE MAIN IN MUDPLOT /** 1) MN: A312385 SN: 0074409, *TAP: SIZE: A LOC: 78 FEET FROM P LINE AT JEFFERSON DAVIS PKWY., *MB: CODE: CDN2 LOC: ON ELAINE PL., 36' FROM P.L. JEFFERSON DAVIS PKWY ****/ | 2019-08-14 | EXCAVATED IN MU DPLOT + MADE REPAIR ON ABANDONED 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA (NO METER) JOB COMPLETE
201901166401 | 2019-08-08 | LEAD/PLASTIC | 4319 | FRERET |  | WILK | LEAK IN THE STREET ACROSS FROM ABOVE ADDRESS CAUSING A DEPRESSION IN THE STREET **********DUPLICATE OF 4901 FRERET********** /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-08-18 | MADE CUT IN STREET OVER INLET SERVICE.REPAIR LEAK ON SERVICE.BACKFILLED WITH SAND AND LIMESTONES.(SOC 5FT. X 5 FT. ASPHALT)
201901171201 | 2019-08-09 | LEAD/PLASTIC | 5514 | CONSTANCE | OCTAVIA | WOLK | MI: LEAD WHIP NEEDS TO BE REPLACED DUG UP AND EXPOSED MTR#A281977 RENEW OUTLET FROM LEAD TO PLASTIC /** 1) MN: A240114 SN: 0041189, *TAP: SIZE: A LOC: 109 FEET FROM P LINE AT OCTAVIA, *MB: CODE: BD LOC: 109' P.L. OCTAVIA ****/ | 2019-08-16 | ARRIVED AT THE ABOVE LOCATION DUG AROUND THE METER BOX IN THE TREE ROOTS AND RENEWED 3/4 LEAD WITH 3/4 PLASTIC TUBING.THEN BACKFILLED AND CLEANED THE AREA.
201901171501 | 2019-08-09 | LEAD | 2821 | ST ANN |  | WMTLK | ML - METER LEAK ACCOUNT NUMBER - 123081-701215 METER NUMBER - A424230 EXAMINE INLET AND OUTLET SERVICE FOR LEAK METER UNDER WATER, CUSTOMER PARKING ON METER /** 1) MN: A286688 SN: 0053642, *TAP: SIZE: A LOC: 108 FEET FROM P LINE AT DUPRE N, *MB: CODE: ADL LOC: ON ST. ANN,107.5' FROM L.R.P.L. NO. DUPRE ****/ | 2019-08-19 | REPLACE BROKEN 5/8 INCH HANDWHEEL AT ABOVE LOCATION
201901174401 | 2019-08-09 | LEAD | 1801 | NEW ORLEANS |  | WILK | ML METER BOX LEAKING NO ACTIVE ACCT NO METER# INLET SERVICE LEAK IN SIDEWALK BY VACANT LOT 08/20/19 LEAK HAS GOTTEN WORSE FLOODING AREA GETTING ONTO PROPERTY UPGRADED TO PRIORITY -B- (FCP) /** 1) MN: A280370 SN: 0074188, *TAP: SIZE: B LOC: 28 FEET FROM P LINE AT ROMAN N, *MB: CODE: ADK LOC: ON NEW ORLEANS 28FT FROM ROMAN N ****/ | 2019-08-21 | MADE REPAIR ON ABANDONED SERVICE 5/8 INCH METER BOX BACKFILL AND CLEAN UP AREA NO METER
201901175602 | 2019-08-13 | LEAD | 600 | MOSS | TOULOUSE | CYNW | C Y NO WATER ON INLET IN STREET POSSIBLE LINE IS CRIMPED BY CONTRACTORS PR J WHEELER /** 1) MN: E005273 SN: 0078195, *TAP: SIZE: E LOC: 142 FEET FROM P LINE AT TOULOUSE, *MB: CODE: BE LOC: SEWER COVER ON HAGAN 140'PL TOULOUSE 5' OUTSIDE PL ****/ | 2019-08-14 | ARRIVED AT ABOVE LOCATION + FOUND CUSTOMER OUT OF WATER EXCAVATED IN CONCRETE STREET + FOUND INLET CRSHED MADE REPAIR ON 3/4 INLET SERVICE LINE RESTORING WATER TO ABOVE LOCATION .REMOVED TEMPORARY WATER SERVICE COMPACTED BACKFILL + DRESSED UP AREA
201901178501 | 2019-08-10 | LEAD | 3119 | ST PETER |  | WILK | MI LEAK ON SIDEWALK NEAR METERBOX INLET SERVICE LEAK INSIDE METER BOX BAD CURB COCK /** 1) MN: A336743 SN: 0071818, *TAP: SIZE: A LOC: 140 FEET FROM P LINE AT LOPEZ S, *MB: CODE: CDLN LOC: ON ST PETER ST 140' FROM PL S LOPEZ ****/ | 2019-08-21 | EXCAVATED 4 4 LIMESTONE GUTTER BOTTOM FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL ALSO RAISE METER BOX UP TO GRADE
201901180101 | 2019-08-12 | LEAD | 3013 | ST ANN | N GAYOSO | WOLK | ACCT# 118832-706293 METER# A416575 INSPECTOR FOUND CONSTANT REGISTRATION ON METER /** 1) MN: A244606 SN: 0028591, *TAP: SIZE: A LOC: 113 FEET FROM P LINE AT GAYOSO N, *MB: CODE: CFLM LOC: 113' P.L. N GAYOSO ****/ | 2019-08-23 | REPLACED BOTH INLET AND OUTLET WASHERS AT ABOVE NO CONSTANT REGISTRATION
201901183201 | 2019-08-12 | LEAD | 1125 | N BROAD |  | WMTLK | LOCATIONID#212267-521296 METER#D003719 LEAK INSIDE METERBOX /** 1) MN: D003719 SN: 0172709, *TAP: SIZE: D LOC: 162 FEET FROM P LINE AT BELLECHASE, *MB: CODE: CD LOC: ON BROAD 162' FROM BELLECHASE 12' OUTSIDE 3'INSIDE ****/ | 2019-08-27 | EXAMINE JOB AT ABOVE LOCATION FOUND LEAK ON 1 1/2 INLET SERVICE INSIDE OF MANHOLE MADE REPAIR ON INLET
201901183301 | 2019-08-12 | LEAD | 2735 | URSULINES AV |  | WMTLK | LOCATIONID#145636-520938 METER#B023257 LEAK INSIDE METERBOX 08/16/19 CUSTOMER STATES LEAK GETTING WORSE (NLD) 08/19/19 ***CUST STATES LEAK GETTING WORSE FLOODING AREA* (KSW) /** 1) MN: B023257 SN: 0077276, *TAP: SIZE: C LOC: 2 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: CFL7 LOC: ON N WHITE 52FT FROM PL OF URSULINES AVE ****/ | 2019-08-21 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201901183401 | 2019-08-12 | LEAD | 2737 | URSULINES AV |  | WMTLK | LOCATIONID#145637-521152 METER#B031389 LEAK INSIDE METERBOX /** 1) MN: B031389 SN: 0078546, *TAP: SIZE: B LOC: 2 FEET FROM P LINE AT URSULINES AVE, *MB: CODE: CFL7 LOC: ON URSULINES AVE 50FT FROM PL OF N WHITE ****/ | 2019-08-21 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERFVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201901186901 | 2019-08-12 | LEAD | 1418 | SPAIN | N VILLERE | WILK | INLET SERVICE LEAK /** 1) MN: A314833 SN: 0054903, *TAP: SIZE: A LOC: 155 FEET FROM P LINE AT VILLERE N, *MB: CODE: CEL LOC: ON SPAIN,153.5' FROM P.L. NO. VILLERE ****/ | 2019-08-08 | EXCAVATED 4 X 4 LIMESTONE GUTTER BOTTOM FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND AND CODLMILL
201901188201 | 2019-08-12 | LEAD | 1725 | N ROMAN | ALLEN | WILK | MI- LEAK IN STREET INLET SERVICE LEAK IN ASPHALT STREET LEFT ONE (1) CONE FOR SAFETY /** 1) MN: A183595 SN: 0047074, *TAP: SIZE: A LOC: 137 FEET FROM P LINE AT ALLEN, *MB: CODE: CFK LOC: 1ST METER 137FT FROM PL ALLEN ON N ROMAN ****/ | 2019-08-22 | EXCAVATED IN ASPHALT STREET + MADE REPAIR ON ABANDONED 3/4 INCH INLET SERVICE LINE NEAR WATER MAIN COMPACTED BACKFILLED + DRESSED UP AREA
201901189101 | 2019-08-12 | LEAD | 1141 | N VILLERE |  | WOLK | LOCATION: 308230 METER A 439832 SET TODAY INSP UDUEBOR STATES OUTLET SERVICE NEED TIE IN. HOUSE UNDER RENOVATIONS AND VACANT. CUSTOMER READY FOR OUTLET TIE IN HOUSE UNDER RENOVATION /** 1) MN: A229677 SN: 0036843, *TAP: SIZE: A LOC: 55 FEET FROM P LINE AT GOV. NICHOLLS, *MB: CODE: BDON LOC: ON NO. VILLERE,55.8' FROM U.S.P.L. GOV. NICHOLLS ****/ | 2019-08-13 | EXCAVATED 2 X 4 CONCRETE SIDEWALK RENEW 5/8 INCH OUTLET SERVICE FROM METER BOX TO PROPERTY TIE INTO 3/4 INCH PLASTIC LINE BACJKFILL JOB WITH RIVERSAND AND COLDMILL. JOB COMPLETE
201901189501 | 2019-08-12 | LEAD | 1372 | ANNETTE | N VILLERE | WILK | *********PICKUP JOB********* INLET SERVICE LEAK IN ASPHALT STREET GETTING OFF IN DCB /** 1) MN: 000000 SN: 0045532, *TAP: SIZE: A LOC: 92 FEET FROM P LINE AT VILLERE N, *MB: CODE: AE25 LOC: METER ON ANNETTE 92 FT FROM PL N VILLERE ****/ | 2019-08-28 | EXCAVATED IN ASPHALT STREET + MADE REPAIR ON 3/4 INCH INLET SERVICE LINE COMPACTED BACKFILLED + DRESSED UP AREA NO METER JOB COMPLETE
201901189601 | 2019-08-12 | LEAD | 3019 | BANKS | S SALCEDO | WILK | ML- METER LEAK ACCT# 107653-531132 MTR# A275262 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A336785 SN: 0018168, *TAP: SIZE: A LOC: 134 FEET FROM P LINE AT SALCEDO S, *MB: CODE: ADK4 LOC: ON BANKS 133FT FROM PL OF SALCEDO S ****/ | 2019-08-21 | MADE REPAIR ON 5/8 INCH WHEEL BACKFILL CLEAN UP AREA
201901190201 | 2019-08-12 | LEAD | 1025 | ALVAR | ST CLAUDE AV | WILK | ML-METER LEAK METER#A260965 ACCT#110514-424559 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A260965 SN: 0060928, *TAP: SIZE: B LOC: 185 FEET FROM P LINE AT RAMPART N, *MB: CODE: CDL3 LOC: ON ALVAR 185.5' FROM LSPL N RAMPART ****/ | 2019-08-22 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201901192001 | 2019-08-13 | LEAD | 1603 | GENTILLY BL | PONCE DE LEON | WMTLK | WATER METER LEAK. LEAK IS IN THE GRASS BETWEEN THE SIDEWALK AND THE ROADWAY, LOCATED ON PONCE DE LEON. ECHOLOGICS REPORTED AND MARKED THE LEAK ON 8/9/2019. /** 1) MN: 000000 SN: 0064704, *TAP: SIZE: A LOC: 28 FEET FROM P LINE AT GENTILLY BLVD, *MB: CODE: CDHO LOC: 29FT FROM PL GENTILLY METER ON PONCE DE LEON ****/ | 2019-08-26 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201901192801 | 2019-08-13 | LEAD/PLASTIC | 2513 | ROBERT | MAGNOLIA | WILK | MI- LEAK IN STREET *** DOTTIE C-8/18/19,R-8/22/19,EXP. 9/11/19***** CHANGED FROM 2500BLK ROBERT EXAMINE INLET SERVICE FOR LEAK IN ASPHALT STREET GETTING OFF IN DCB /** 1) MN: A313494 SN: 0017780, *TAP: SIZE: A LOC: 99 FEET FROM P LINE AT MAGNOLIA, *MB: CODE: ADL3 LOC: ON ROBERT 99FT FROM PL OF MAGNOLIA ****/ DOTTIE READY 8-23-19 EXP 9-12-19 | 2019-08-27 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 3/4 SERVICE LEAKING .REPLACED 18 FT. OF 3/4 TUBING.(SOC 4FT. X 12 FT. CONCRETE BASE)
201901193001 | 2019-08-13 | LEAD | 4020 | DELGADO DR |  | WILK | ML-- METER LEAK MTR# B042748 ACCT # 137459-475281 INLET SERVICE LEAK IN THE MUD PLOT @ THE CURB /** 1) MN: B018572 SN: 0068056, *TAP: SIZE: B LOC: 110 FEET FROM P LINE AT DELGADO DR, *MB: CODE: BDK2 LOC: ON DELGADO 112' FROM PL OF DELGADO DR ****/ | 2019-08-27 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201901196601 | 2019-08-14 | LEAD | 1004 | DAUPHINE |  | WOLK | LOCATIONID#118762-529575 METER#A293189 LEAK INSIDE METERBOX /** 1) MN: A293189 SN: 0029177, *TAP: SIZE: A LOC: 52 FEET FROM P LINE AT ST PHILIP, *MB: CODE: CE LOC: 52FT. FRM LRPL ST PHILIP METER ON DAUPHINE ****/ | 2019-08-23 | REPLACE BOTH INLET AND OUTLET WASHERS AT ABOVE LOCATION
201901196701 | 2019-08-14 | LEAD | 2435 | URSULINES AV | ROCHEBLAVE | WOLK | ACCT# 124315-52440 MTR# A390769 INSPECTOR FOUND CONS ON METER, NO VISIBLE S&W VALVE. /** 1) MN: A309315 SN: 0044622, *TAP: SIZE: A LOC: 54 FEET FROM P LINE AT ROCHEBLAVE N, *MB: CODE: BDN1 LOC: 2FT LS APPROACH OUTSIDE 54' P.L. N ROCHEBLAVE ****/ | 2019-08-26 | EXAMINE JOB AT ABOVE LOCATION FOUND NO CONSTANT REG ON METER. JOB COMPLETE
201901199001 | 2019-08-14 | LEAD/PLASTIC | 3600 | FRERET |  | WILK | WTER LEAK IN STREET /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-08-18 | MADE CUT OVER INLET SERVICE.REPAIR 3/4 LEAD SERVICE.BACKFILLED CUT WITH SAND AND LIME STONES.(SOC 6FT. X 6 FT .ASPHALT.
201901199601 | 2019-08-14 | LEAD | 2612 | PALMYRA | BROAD PL | WMTLK | WM- LEAK AT THE CURB EXAMINE INLET & OUTLET SERVICE FOR A LEAK INSIDE METER BOX IN THE MUD PLOT /** 1) MN: A197701 SN: 0038941, *TAP: SIZE: A LOC: 94 FEET FROM P LINE AT DORGENOIS S, *MB: CODE: BGL LOC: INSIDE S AND W ****/ | 2019-08-26 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAKON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILLED JOB WITH RIVERSAND
201901200701 | 2019-08-14 | LEAD | 2753 | IBERVILLE | N WHITE | WOLK | CONS ON METER & METER LEAK ACCT# 113216-534062 METER# A-409522 /** 1) MN: A262879 SN: 0046204, *TAP: SIZE: B LOC: 70 FEET FROM P LINE AT WHITE N, *MB: CODE: AF LOC: ON IBERVILLE 70' FROM PL N WHITE 12' OUTSIDE PL 2' ** 2) MN: SN: 0046204, *TAP: SIZE: A LOC: 55 FEET FROM P LINE AT WHITE N, *MB: CODE: FL1 LOC: 68' P.L. N WHITE ****/ | 2019-08-26 | REPLACE BROKEN 5/8 INCH HANDWHEEL AT ABOVE LOCATION
201901202301 | 2019-08-14 | LEAD | 928 | ST ANN |  | WILK | WM-LEAK ON THE SIDEWALK INLET SERVICE LEAK IN ASPHALT STREET /** 1) MN: B018539 SN: 0029592, *TAP: SIZE: B LOC: 129 FEET FROM P LINE AT BURGUNDY, *MB: CODE: BEK2 LOC: 129' P.L. BURGUNDY ****/ | 2019-08-23 | MADE 2 X 6 CUT IN DOUBLE LAYER SIDEWALK WITH SLATE AND REPLACED 3/4 INCH CURB COCK BACKFILLED AREA
201901212001 | 2019-08-16 | LEAD | 2732 | WISTERIA |  | WMTLK | LOCATIONID#144717-478955 METER#A374885 LEAK INSIDE METERBOX /** 1) MN: A338859 SN: 0085766, *TAP: SIZE: A LOC: 223 FEET FROM P LINE AT LOTUS, *MB: CODE: CDL LOC: 223' P.L. LOTUS ****/ | 2019-08-22 | EXAMINE JOB FOUND LEAK ON METER BOX COCK REPLACED METER COCK WITH A 5/8 METER BOX COCK WITHOUT FITTING. FOUND LEAD ON INET AND OUTLET. JOB COMPLETED
201901215801 | 2019-08-16 | LEAD | 1928 | CONTI |  | WMRE | INSP M FRAZIER STATES SERVICE IS BURIED. PLEASE RAISE TO GRADE AND SET 5/8 METER. LOC 308094 LOCATE, RAISE TO GRADE AND SET METER AS REQUESTED ***HOUSE UNDER RENOVATIONS*** /** 1) MN: 000000 SN: 0051443, *TAP: SIZE: A LOC: 221 FEET FROM P LINE AT ROMAN N, *MB: CODE: ADK1 LOC: ON CONTI, 220.6' FROM P.L. NO. ROMAN ****/ | 2019-08-28 | EXCAVATED IN MUD PLOT AT ABOVE BOTTOM + LOCATED 5/8 INCH METER BOX RAISED METER BOX BOTTOM TO GRADE + SET 5/8 INCH METER BACKFILLED BACKFILLED + DRESSED UP AREA
201901215901 | 2019-08-16 | LEAD | 1924 | CONTI |  | WMRE | INSP M FRAZIER STATES SERVICE IS BURIED. PLEASE RAISE TO GRADE AND SET 5/8 METER. LOC 308093 LOCATE, RAISE TO GRADE & SET METER AS REQUESTED ***HOUSE UNDER RENOVATIONS*** /** 1) MN: 000000 SN: 0064737, *TAP: SIZE: A LOC: 202 FEET FROM P LINE AT ROMAN N, *MB: CODE: CDK6 LOC: RS OF ALLEY ON CONTI 203 FT FROM PL N ROMAN ****/ | 2019-08-28 | EXCAVATEDIN MUD PLOT AT ABOVE LOCATION + LOCATED 5/8 INCH METER BOX RAISED METER BOX BOTTOM TO GRADE + SET 5/8 INCH METER BACKFILLED + DRESSED UP AREA
201901218101 | 2019-08-16 | LEAD | 1518 | N BROAD | LAHARPE | WILK | ML-METER LEAK INSIDE BOX BUT NOT FLOWING OVER METER WAS SET TODAY ACCT#182160-494423 INLET SERVICE LEAK IN SIDEWALK COMING FROM BAD BLEEDER VALVE /** 1) MN: A144430 SN: 0055105, *TAP: SIZE: A LOC: 110 FEET FROM P LINE AT COLUMBUS, *MB: CODE: BDK6 LOC: ON N BROAD 112FT FROM PL COLUMBUS 8' OUTSIDE PL 2' ****/ | 2019-08-27 | EXCAVATED 2 X 4 CONCRETE DRIVEWAY FOUND LEAK ON 5/8 INCH INLET SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND AND COLDMILL ALSO REPLACE BAD 5/8 INCH WATER METER
201901221001 | 2019-08-17 | LEAD | 2629 | URSULINES AV | N DORGENOIS | WMTLK | LOCATION ID# 111136 MTR# A401092 LEAK AROUND & INSIDE METER /** 1) MN: SN: 0013590, *TAP: SIZE: B LOC: 227 FEET FROM P LINE AT DORGENOIS N, *MB: CODE: CFL LOC: IN GARDEN 227' P.L. N DORGENOIS ****/ | 2019-08-27 | EXCAVATED 4 X 4 MUD PLOT FOUND LEAK ON 5/8 INCH SERVICE MADE REPAIR ON INLET BACKFILL JOB WITH RIVERSAND
201901224301 | 2019-08-19 | LEAD | 4435 | BACCICH |  | WMTLK | LOCATIONID#169072-479210 METER#B038907 LEAK INSIDE METERBOX /** 1) MN: B031882 SN: 0111033, *TAP: SIZE: B LOC: 276 FEET FROM P LINE AT GENTILLY BLVD, *MB: CODE: ADK LOC: ON BACCICH, 278' FROM P.L. GENTILLY BLVD., 11'OUT- ****/ | 2019-08-20 | EXCAVATED DOWN ON INLET SERVICE. FOUND LEAD AND CURB COCK WAS LEAKING. MADE REPAIRS BY REPLACING WASHERS CURB COCK ALSO METER BECAUSE IT WAS CHOKED. BACKFILLED LOCATION HAS POOR PRESSURE AT FAUCET. ALSO CUSTOMER HAVE OLD GALVANIZE PIPES. CUSTOMER WAS NOT HOME. PROBLEM IS ON CUSTOMER. OLD METER INFO: B038907 FACT: 14121554 MAKE: HERSEY READ: 2538
201901230501 | 2019-08-19 | LEAD | 5114 | MONTEGUT | DREUX AV | WILK | ML- METER LEAK METER #A236499 ACCT # 169128-468906 INLET SERVICE LEAK IN MUDPLOT /** 1) MN: A236499 SN: 0111694, *TAP: SIZE: A LOC: 445 FEET FROM P LINE AT DREUX AVE, *MB: CODE: ADM LOC: 445FT PL DREUX AV 6' OUTSIDE 6' INSIDE CURB ****/ | 2019-08-28 | EXCAVATED DOWN ON INLET SERVICE IN TREE ROOTS BY HAND. FOUND LEAD AND CURB COCK WAS LEAKING. MADE REPAIRS BY REPLACING COCK, EASHERS. BACKFILLED.
201901232501 | 2019-08-20 | LEAD | 309 | N BROAD |  | WOLK | LOCATION# 120324 CUSTOMER# 519647 METER# A418777 INSPECTOR DID AN OUTSIDE INSPECTION FOUND CONSTANT REGISTRATION ON METER, CAN'T DETERMINE WHERE LEAK IS COMING FROM..............PLEASE REPAIR /** 1) MN: A328464 SN: 0055338, *TAP: SIZE: C LOC: 113 FEET FROM P LINE AT BIENVILLE, *MB: CODE: ADK3 LOC: 113FT FROM PL BIENVILLE BY POLE ****/ | 2019-08-27 | EXAMINE JOB AT ABOVE LOCATION FOUND NO CONSTANT REGISTRATION ONMETER
201901234201 | 2019-08-28 | LEAD/PLASTIC | 833 | ELEONORE | ELEONORE | WOLK | ML- METER LEAK ACCT#148092-564700 MTR# A433648 CONS. FOUND ON METER, PERFORMED S&W TEST CONS. CONTINUED. /** 1) MN: A272789 SN: 0008776, *TAP: SIZE: A LOC: 75 FEET FROM P LINE AT ELEONORE, *MB: CODE: AEH2 LOC: 76FT FROM PL ELEONORE 2ND METER SIDE ST ****/ DOTTIE READY 8-23-19 EXP 9-12-19 | 2019-08-27 | MADE CUT IN SIDEWALK OVER INLET AND OUTLET SERVICE .MADE REPAIR ON BOTH METER BOXES.BACKFILLED WITH SAND AND LIMESTONES.COULDN'T REMOVE ALL LEAD FROM OUTLET HOME OWNER SAID DON'T GO IN HER GARDEN.(SOC4FT. X 8 FT .S/W) JOB COMPLETE
201901235101 | 2019-08-20 | LEAD | 1204 | NAPOLEON AV | COLISEUM | WOLK | ML-METER LEAK ACCT#104028-560974 METER#A394777 OUTLET SERVICE LEAKING FROM HANDWHEEL FLOODING GUTTER BOTTOM WITH SOME WATER GETTING OFF IN THE DCB. METER ON COLISEUM /** 1) MN: A140962 SN: 0007297, *TAP: SIZE: A LOC: 91 FEET FROM P LINE AT NAPOLEON AVE, *MB: CODE: ADHL LOC: BY GATE CURB SIDE ST ON COLISEUM 91FT FROM USPL OF ****/ DOTTIE READY 8-23-19 EXP 9-12-19 | 2019-08-25 | EXAMINE WATER LEAK AT ABOVE LOCATION FOUND 5/8 CURB COCK AND 5/8 HANDWHEEL BAD .REPLACED 5/8 METER BOX COMPLET TIED INTO LEAD ON INLET AND OUTLET.
201901236201 | 2019-08-20 | LEAD | 2300 | A P TUREAUD AV | N TONTI | WMBK | LOCATION ID# 218237-723018 MTR# A407044 NEED A METERBOX CASING AND COVER /** 1) MN: A319964 SN: 0068234, *TAP: SIZE: B LOC: 39 FEET FROM P LINE AT A.P.TUREAUD AVE, *MB: CODE: ADHK LOC: ON N TONTI 38FT FROM PL A P TUREAUD AVE ****/ | 2019-08-22 | EXCAVATED IN MUD PLOT AND REPLACED METER BOX CASING AND TOP BACKFILLED AREA.
201901253101 | 2019-08-22 | LEAD | 925 | DECATUR |  | WILK | MI LEAK INSIDE NSIDE METER BOX *****************DAMAGE CLAIM***************** **********************1ST AM********************* CUT INLET SERVICE BY BEEP ME PLUMBING IN BRICK SIDEWALK /** 1) MN: A112933 SN: 0004009, *TAP: SIZE: B LOC: 113 FEET FROM P LINE AT ST PHILIP, *MB: CODE: BFM7 LOC: ON DECATUR,113' FROM S.P.L. ST. PHILIP ****/ | 2019-08-23 | EXAMINE JOB AT ABOVE LOCATION FOUND LEAK ON INLET SERVICE MADE REPAIRS ON INLET, HOLE WAS ALREADY EXPOSED BY (BEEP ME PLUMBING) JOB COMPLETE
201901261101 | 2019-08-24 | LEAD | 1710 | N ROMAN |  | WILK | WATER INLET SERVICE /** NO WATER METER/TAP INFO FOUND IN AUTO LOOKUP. ****/ | 2019-08-22 | EXCAVATED IN GUTTER BOTTOM + AMDE REAPIR ON 3/4 INCH INLET SERVICE LINE BACKFILLED + DRESSED UP AREA NO METER
201901261601 | 2019-08-24 | LEAD | 5901 | PAULINE DR | PRENTISS AV | WMTLK | ML- METER LEAK METER# A435046 ACCT# 175476-470737 EXAMINE INLET/OUTLET SERVICE FOR LEAK UNABLE TO PUMP DOWN /** 1) MN: A223557 SN: 0119914, *TAP: SIZE: B LOC: 508 FEET FROM P LINE AT MADRID, *MB: CODE: CDLM LOC: 508FT FROM PL MADRID 8' OUTSIDE ****/ | 2019-08-28 | EXCAVATED DOWN ON INLET SERVICE FROM METER TO CURB. FOUND LEAD AND CURB COCK WAS LEAKING. MADE REPAIRS BY RELACING COCK, WASHERS. ALSO LEAK IN STREET THAT IN FRONT OF SERVICE 5831 IS COMING IN TO FRESH EXCAVATED HOLE. THERE NO MORE LEAKS AT LOCATION. BACKFILLED.
201902229601 | 2019-01-02 | LEAD | 2408 | PAUGER |  | WMRE | LOCATION: 306646 INSP UDEBOR STATES METER SERVICE IS BURIED, AREA FLOODED. PLEASE LOCATE AND SET 5/8 METER. LOCATE & SET METER, ALSO RAISE TO GRADE. ***HOUSE UNDER RENOVATION*** /** 1) MN: SN: 0040543, *TAP: SIZE: A LOC: 81 FEET FROM P LINE AT DERBIGNY N, *MB: CODE: BEL1 LOC: ON PAUGER,81' FROM U.S.P.L. NO. DERBIGNY ****/ | 2019-01-11 | EXCAVATED 8 X 6 MUD PLOT FOUND ABANDONED INLET SERVICE LINE TIED INTO SET 5/8 INCH METER COMPLETE WITH METER BACKFILLED AND CLEANED THE AREA
201902232401 | 2019-01-02 | LEAD | 1306 | ALABO |  | WMRE | LOCATION: 305638 INSP UDEBOR STATES METER SERVICE IS BURIED. PLEASE LOCATE AND SET A 5/8 METER. LOCATE & RAISE TO GRADE. ***HOUSE UNDER RENOVATIONS*** /** 1) MN: A265617 SN: 0089208, *TAP: SIZE: A LOC: 58 FEET FROM P LINE AT URQUHART, *MB: CODE: BD LOC: RES ON ALABO 58FT FROM PL URQUHART ****/ | 2019-01-09 | EXCAVATED AND RELOCATED METER BOX INTO SIDEWALK SET A 5/8 INCH WATER METER BACKFILLED JOB WITH RIVER SAND COLDMILL